## Solar_Inverters
Grid Support Solar Inverter List (Full Data)
Data has not changed since October 12, 2026
This list contains an extensive amount of equipment information. If you require any assistance, please reach out to us at SolarEquipment@energy.ca.gov or 916-654-4120.
Inverter List Notes
This row is intentionally left blank.
(1) Any text in curly brackets at the end of the Model Number is not part of the Manufacturer's Model Number. Part of the text in curly brackets indicates the specified voltage option for that model number, if provided; models with multiple voltage options will have multiple row entries, with one for each eligible option.
(2) Hybrid inverters are capable of taking DC power input from both a solar system and an energy storage system. These models are listed on both the solar and battery inverter lists to reflect the dual functionality. Refer to the manufacturer's documentation for more information on the exact functionality and limitations.
(3) RPP: UL 1741 SA13 tested with reactive power priority enabled (when operating at apparent power capacity, inverter will reduce active power as needed to ensure curve-required reactive power is provided)
(4) A Y* notes the inverter has not been certified according to CSIP, but instead NRTL reported inverter was connected to a gateway during compatibility testing.
(5) The listed Firmware Version is the version used during the inverter's UL 1741 Supplement SA (SA8-SA13) testing and certified on the listed Certificate Date; multiple firmware versions may be listed for a single certificate date if all are required to comply with Supplement SA. Multiple certificate dates with different firmware versions may be listed if new firmware versions were certified under Supplement SA and reported by the manufacturer. Additional firmware versions may be certified but not reported. Check with NRTL for the most current information.
(6) Inverter CSIP conformance information refers to the entity responsible for the documentation provided to the manufacturer. If the inverter is certified to CSIP, then the information refers to the certifying entity and the certificate date. Otherwise, the information refers to the NRTL that issued the compatibility report and the date of the report.
(7) The 'Monitor Key Data Scheduling Attestation' is no longer required by California Investor Owned Utilities and the CEC no longer collects this information.
(8) The anti-island detection method information is from a manufacturer self-attestation.
Blue colored text indicates that the model number occurs multiple times on the list under different manufacturer names.
Manufacturer Name | Model Number1 | Hybrid Inverter2 | UL 1741 Supplement SB Certification | UL 1741 Supplement SA Testing | UL 1741 SA13 Volt-Var | UL 1741 SA Freq-Watt Volt-Watt | UL 1741 SA Disable Permit Service Limit Active Power | Common Smart Inverter Profile Conformance | Monitor Key Data Scheduling | Description | Maximum Continuous Output Power at Unity Power Factor | Nominal Voltage | Weighted Efficiency | UL 1741 (3rd Ed.) Supplement SB Certification |  | UL 1741 Supplement SA Certification (SA8-SA13)5 |  |  | UL 1741 SA13 Volt-Var | UL 1741 SA Freq-Watt Volt-Watt | UL 1741 SA Disable Permit Service Limit Active Power | Inverter CSIP Conformance6 |  | Monitor Key Data Scheduling Attestation7 | Notes | Built-In Meter | Microinverter | Night Tare Loss | Power Rating, Continuous, 40 deg C | Night Tare Loss, 40 deg C | Voltage Minimum | Voltage Nominal | Voltage Maximum | Power Level | Power Level | Power Level | Power Level | Power Level | Power Level | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Grid Support Listing Date | Last Update | Group 1 Anti-Island8 | Group 2a Anti-Island8 | Group 2b Anti-Island8 | Group 2c Anti-Island8 | Group 3 Anti-Island8 | Group 4 Anti-Island8 | Group 5 Anti-Island8 | Group 6 Anti-Island8 | Others8
|  | PV and Battery | 3rd Edition | SA8-SA13 | RPP3 | SA14-SA15 | SA17-SA18 | CSIP4 | Attestation7 |  | (kW) | (Vac) | (%) | Certifying Entity | Certificate Date [mo/day/yr] | Certifying Entity | Certificate Date [mo/day/yr] | Firmware Version(s) Tested | Listing Date (mo/day/yr) | Certificate Date [mo/day/yr] | Listing Date (mo/day/yr) | Issuing Entity | Document Date (mo/day/yr) | Listing Date |  |  |  | (W) | (kW) | (W) | (Vdc) | (Vdc) | (Vdc) | 10% (kW) | 20% (kW) | 30% (kW) | 50% (kW) | 75% (kW) | 100% (kW) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%) |  |  | G1AI | G2aAI | G2bAI | G2cAI | G3AI | G4AI | G5AI | G6AI | OAI
ABB | PVI-3.0-OUTD-S-US-A {208V} | N | N | Y | Y | N | N | N | N | 3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-A {240V} | N | N | Y | Y | N | N | N | N | 3 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-A {277V} | N | N | Y | Y | N | N | N | N | 3 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-A {208V} | N | N | Y | Y | N | N | N | N | 3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-A {240V} | N | N | Y | Y | N | N | N | N | 3 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-A {277V} | N | N | Y | Y | N | N | N | N | 3 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-M-A {208V} | N | N | Y | Y | N | N | N | N | 3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-M-A {240V} | N | N | Y | Y | N | N | N | N | 3 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-M-A {277V} | N | N | Y | Y | N | N | N | N | 3 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.3-TL-PLUS-US-SB-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 95.5 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.3-TL-PLUS-US-SB-RA-Q {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2020-08-21 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | N | N | 0.9 |  |  | 200 | 340 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 95.5 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | 2020-08-21
ABB | UNO-DM-3.3-TL-PLUS-US-SE-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 95.5 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.3-TL-PLUS-US-SZM-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 95.5 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.3-TL-PLUS-US-SZ-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 95.5 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.3-TL-PLUS-US-SB-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3.3 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 355 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 95.9 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 96.6 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5 | 96.3 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.3-TL-PLUS-US-SB-RA-Q {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.3 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3.3 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2020-08-21 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | N | N | 0.9 |  |  | 200 | 355 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 95.9 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 96.6 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5 | 96.3 | 2020-08-21
ABB | UNO-DM-3.3-TL-PLUS-US-SE-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 3.3 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 355 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 95.9 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 96.6 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5 | 96.3 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.3-TL-PLUS-US-SZM-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 3.3 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 355 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 95.9 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 96.6 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5 | 96.3 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.3-TL-PLUS-US-SZ-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 3.3 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 355 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 95.9 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 96.6 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5 | 96.3 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.8-TL-PLUS-US-SB-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3.3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 95.3 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 96.4 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96 | 95.8 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.8-TL-PLUS-US-SB-RA-Q {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3.3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2020-08-21 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | N | N | 0.9 |  |  | 200 | 340 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 95.3 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 96.4 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96 | 95.8 | 2020-08-21
ABB | UNO-DM-3.8-TL-PLUS-US-SE-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 3.3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 95.3 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 96.4 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96 | 95.8 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.8-TL-PLUS-US-SZM-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 3.3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 95.3 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 96.4 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96 | 95.8 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.8-TL-PLUS-US-SZ-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 3.3 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 95.3 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 96.4 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96 | 95.8 | 2017-07-01 | 2020-08-21
ABB | PVI-3.6-OUTD-S-US-A {208V} | N | N | Y | Y | N | N | N | N | 3.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-A {240V} | N | N | Y | Y | N | N | N | N | 3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-A {277V} | N | N | Y | Y | N | N | N | N | 3.6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-A {208V} | N | N | Y | Y | N | N | N | N | 3.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-A {240V} | N | N | Y | Y | N | N | N | N | 3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-A {277V} | N | N | Y | Y | N | N | N | N | 3.6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-M-A {208V} | N | N | Y | Y | N | N | N | N | 3.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-M-A {240V} | N | N | Y | Y | N | N | N | N | 3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.6 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-M-A {277V} | N | N | Y | Y | N | N | N | N | 3.6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.6 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-A {208V} | N | N | Y | Y | N | N | N | N | 3.3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-A {240V} | N | N | Y | Y | N | N | N | N | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-A {277V} | N | N | Y | Y | N | N | N | N | 3.8 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-A {208V} | N | N | Y | Y | N | N | N | N | 3.3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-A {240V} | N | N | Y | Y | N | N | N | N | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-A {277V} | N | N | Y | Y | N | N | N | N | 3.8 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-M-A {208V} | N | N | Y | Y | N | N | N | N | 3.3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.8 | 208 | 95.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [3/9/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-M-A {240V} | N | N | Y | Y | N | N | N | N | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [3/9/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-M-A {277V} | N | N | Y | Y | N | N | N | N | 3.8 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.8-TL-PLUS-US-SB-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.8-TL-PLUS-US-SB-RA-Q {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2020-08-21 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | N | N | 1 |  |  | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | 2020-08-21
ABB | UNO-DM-3.8-TL-PLUS-US-SE-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.8-TL-PLUS-US-SZM-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Interactive Utility Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-3.8-TL-PLUS-US-SZ-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | 2017-07-01 | 2020-08-21
ABB | PVI-4.2-OUTD-S-US-A {208V} | N | N | Y | Y | N | N | N | N | 4.2 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-A {240V} | N | N | Y | Y | N | N | N | N | 4.2 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-A {277V} | N | N | Y | Y | N | N | N | N | 4.2 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-A {208V} | N | N | Y | Y | N | N | N | N | 4.2 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-A {240V} | N | N | Y | Y | N | N | N | N | 4.2 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-A {277V} | N | N | Y | Y | N | N | N | N | 4.2 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-M-A {208V} | N | N | Y | Y | N | N | N | N | 4.2 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.1 |  |  | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-M-A {240V} | N | N | Y | Y | N | N | N | N | 4.2 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 4.2 | 240 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-M-A {277V} | N | N | Y | Y | N | N | N | N | 4.2 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 4.2 | 277 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.2 |  |  | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 2017-07-01 | 2018-10-15
ABB | UNO-DM-4.6-TL-PLUS-US-SB-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 95.2 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 96.4 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8 | 95.8 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-4.6-TL-PLUS-US-SB-RA-Q {208V} | N | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2020-08-21 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | N | N | 0.9 |  |  | 200 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 95.2 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 96.4 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8 | 95.8 | 2020-08-21
ABB | UNO-DM-4.6-TL-PLUS-US-SE-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 95.2 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 96.4 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8 | 95.8 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-4.6-TL-PLUS-US-SZM-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 95.2 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 96.4 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8 | 95.8 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-4.6-TL-PLUS-US-SZ-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 0.9 |  |  | 200 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 95.2 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 96.4 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8 | 95.8 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-4.6-TL-PLUS-US-SB-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-4.6-TL-PLUS-US-SB-RA-Q {240V} | N | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2020-08-21 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | N | N | 1 |  |  | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | 2020-08-21
ABB | UNO-DM-4.6-TL-PLUS-US-SE-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-4.6-TL-PLUS-US-SZM-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-4.6-TL-PLUS-US-SZ-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-5.0-TL-PLUS-US-SB-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 4.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 240 | 340 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-5.0-TL-PLUS-US-SB-RA-QU {208V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 4.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2020-08-21 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | N | N | 1 |  |  | 240 | 340 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | 2020-08-21
ABB | UNO-DM-5.0-TL-PLUS-US-SE-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 4.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 240 | 340 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-5.0-TL-PLUS-US-SZM-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 4.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 240 | 340 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-5.0-TL-PLUS-US-SZ-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 4.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 240 | 340 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-5.0-TL-PLUS-US-SZ-RA-U {208V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 4.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2020-08-21 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 240 | 340 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | 2020-08-21
ABB | PVI-5000-OUTD-US-A {208V} | N | N | Y | Y | N | N | N | N | 5 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 5 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-A {240V} | N | N | Y | Y | N | N | N | N | 5 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-A {277V} | N | N | Y | Y | N | N | N | N | 5 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-A {208V} | N | N | Y | Y | N | N | N | N | 5 kW, 208 Vac Grid Support Utility Interactive Inverter | 5 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-A {240V} | N | N | Y | Y | N | N | N | N | 5 kW, 240 Vac Grid Support Utility Interactive Inverter | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-A {277V} | N | N | Y | Y | N | N | N | N | 5 kW, 277 Vac Grid Support Utility Interactive Inverter | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-M-A {208V} | N | N | Y | Y | N | N | N | N | 5 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 5 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-M-A {240V} | N | N | Y | Y | N | N | N | N | 5 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-M-A {277V} | N | N | Y | Y | N | N | N | N | 5 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | 2017-07-01 | 2018-10-15
ABB | UNO-DM-5.0-TL-PLUS-US-SB-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.2 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8 | 96.5 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-5.0-TL-PLUS-US-SB-RA-QU {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2020-08-21 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | N | N | 1 |  |  | 200 | 355 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.2 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8 | 96.5 | 2020-08-21
ABB | UNO-DM-5.0-TL-PLUS-US-SE-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.2 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8 | 96.5 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-5.0-TL-PLUS-US-SZM-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.2 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8 | 96.5 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-5.0-TL-PLUS-US-SZ-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2018-10-15 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.2 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8 | 96.5 | 2017-07-01 | 2020-08-21
ABB | UNO-DM-5.0-TL-PLUS-US-SZ-RA-U {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and Rapid Shutdown power supply | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/10/2020] | [1913B] | 2020-08-21 | [06/10/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1 |  |  | 200 | 355 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.2 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8 | 96.5 | 2020-08-21
ABB | PVI-6000-OUTD-US-A {208V} | N | N | Y | Y | N | N | N | N | 6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-A {240V} | N | N | Y | Y | N | N | N | N | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-A {277V} | N | N | Y | Y | N | N | N | N | 6 kW, 277 Vac Grid Support Utility Interactive Inverter | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-A {208V} | N | N | Y | Y | N | N | N | N | 6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-A {240V} | N | N | Y | Y | N | N | N | N | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-A {277V} | N | N | Y | Y | N | N | N | N | 6 kW, 277 Vac Grid Support Utility Interactive Inverter | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-M-A {208V} | N | N | Y | Y | N | N | N | N | 6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 6 | 208 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-M-A {240V} | N | N | Y | Y | N | N | N | N | 6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-M-A {277V} | N | N | Y | Y | N | N | N | N | 6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | 2017-07-01 | 2018-10-15
ABB | UNO-DM-6.0-TL-PLUS-US-SB-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU | 6 | 208 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2018-10-15 | [06/09/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1.3 |  |  | 240 | 340 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8 | 96.8 | 2017-11-01 | 2020-08-21
ABB | UNO-DM-6.0-TL-PLUS-US-SB-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU | 6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2018-10-15 | [06/09/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1.3 |  |  | 200 | 355 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 96.6 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 97.3 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4 | 97.2 | 2017-11-01 | 2020-08-21
ABB | UNO-DM-6.0-TL-PLUS-US-SB-RA-QU {208V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 6 | 208 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2020-08-21 | [06/09/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | N | N | 1.3 |  |  | 240 | 340 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8 | 96.8 | 2020-08-21
ABB | UNO-DM-6.0-TL-PLUS-US-SB-RA-QU {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2020-08-21 | [06/09/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | N | N | 1.3 |  |  | 200 | 355 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 96.6 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 97.3 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4 | 97.2 | 2020-08-21
ABB | UNO-DM-6.0-TL-PLUS-US-SC-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, cellular, RSD PSU | 6 | 208 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2018-10-15 | [06/09/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1.3 |  |  | 240 | 340 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8 | 96.8 | 2017-11-01 | 2020-08-21
ABB | UNO-DM-6.0-TL-PLUS-US-SC-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, cellular, RSD PSU | 6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2018-10-15 | [06/09/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1.3 |  |  | 200 | 355 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 96.6 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 97.3 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4 | 97.2 | 2017-11-01 | 2020-08-21
ABB | UNO-DM-6.0-TL-PLUS-US-SE-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, Ethernet card, RSD PSU | 6 | 208 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2018-10-15 | [06/09/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1.3 |  |  | 240 | 340 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8 | 96.8 | 2017-11-01 | 2020-08-21
ABB | UNO-DM-6.0-TL-PLUS-US-SE-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, Ethernet card, RSD PSU | 6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2018-10-15 | [06/09/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1.3 |  |  | 200 | 355 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 96.6 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 97.3 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4 | 97.2 | 2017-11-01 | 2020-08-21
ABB | UNO-DM-6.0-TL-PLUS-US-S-XRA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU | 6 | 208 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2018-10-15 | [06/09/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1.3 |  |  | 240 | 340 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8 | 96.8 | 2017-11-01 | 2020-08-21
ABB | UNO-DM-6.0-TL-PLUS-US-S-XRA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU | 6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2018-10-15 | [06/09/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1.3 |  |  | 200 | 355 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 96.6 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 97.3 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4 | 97.2 | 2017-11-01 | 2020-08-21
ABB | UNO-DM-6.0-TL-PLUS-US-SZM-RA {208V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, Zigbee, Revenue Grade Meter, RSD PSU | 6 | 208 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2018-10-15 | [06/09/2020] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1.3 |  |  | 240 | 340 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8 | 96.8 | 2017-11-01 | 2020-08-21
ABB | UNO-DM-6.0-TL-PLUS-US-SZM-RA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, Zigbee, Revenue Grade Meter, RSD PSU | 6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/09/202] | [1913D] | 2018-10-15 | [06/09/202] | 2020-08-21 | PCTEST | 2020-01-16 | 2020-08-21 |  | Y | N | 1.3 |  |  | 200 | 355 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 96.6 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 97.3 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4 | 97.2 | 2017-11-01 | 2020-08-21
ABB | UNO-7.6-TL-OUTD-S-US-A {208V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 208 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | [2/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.3 |  |  | 200 | 340 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 96.3 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7 | 96.8 | 2017-07-01 | 2019-02-15
ABB | UNO-7.6-TL-OUTD-S-US-A {240V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | [2/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.4 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 97.5 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2019-02-15
ABB | UNO-7.6-TL-OUTD-S-US-A {277V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 277 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | [2/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.5 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 96.3 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 2017-07-01 | 2019-02-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-A {208V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 208 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | [2/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.3 |  |  | 200 | 340 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 96.3 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7 | 96.8 | 2017-07-01 | 2019-02-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-A {240V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | [2/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.4 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 97.5 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2019-02-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-A {277V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 277 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | [2/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.5 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 96.3 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 2017-07-01 | 2019-02-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A {208V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 208 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | [2/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.3 |  |  | 200 | 340 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 96.3 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7 | 96.8 | 2017-07-01 | 2019-02-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A {240V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | [2/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.4 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 97.5 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2019-02-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A {277V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 277 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | [2/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.5 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 96.3 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 2017-07-01 | 2019-02-15
ABB | UNO-8.6-TL-OUTD-S-US-A {240V} | N | N | Y | Y | Y | N | N | N | 8.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.4 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 96.3 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2019-02-15
ABB | UNO-8.6-TL-OUTD-S-US-A {277V} | N | N | Y | Y | Y | N | N | N | 8.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 277 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.5 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97.2 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6 | 97.5 | 2017-07-01 | 2019-02-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-A {240V} | N | N | Y | Y | Y | N | N | N | 8.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.4 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 96.3 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2019-02-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-A {277V} | N | N | Y | Y | Y | N | N | N | 8.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 277 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.5 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97.2 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6 | 97.5 | 2017-07-01 | 2019-02-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-M-A {240V} | N | N | Y | Y | Y | N | N | N | 8.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.4 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 96.3 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | 2017-07-01 | 2019-02-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-M-A {277V} | N | N | Y | Y | Y | N | N | N | 8.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 277 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.5 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97.2 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6 | 97.5 | 2017-07-01 | 2019-02-15
ABB | TRIO-50.0-TL-OUTD-US-480 {480V} | N | N | Y | Y | N | N | N | N | 50 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector | 50 | 480 | 98 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [1/27/2017] | [A.0.9.A, B.1.E.1, C.1.8.8] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1 |  |  | 520 | 720 | 800 | 5 | 10 | 15 | 25 | 37.5 | 50 | 96.3426 | 97.3941 | 97.7305 | 97.8494 | 97.8642 | 97.7358 | 97.8 | 96.859 | 98.0033 | 98.3351 | 98.526 | 98.5515 | 98.4933 | 98.4222 | 95.9226 | 97.5683 | 98.0341 | 98.3179 | 98.3432 | 98.3043 | 98.1633 | 2017-07-01 | 2018-10-15
ABB | TRIO-60.0-TL-OUTD-US-480 {480V} | N | N | Y | Y | N | N | N | N | 60 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector | 60 | 480 | 98 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [1/27/2017] | [A.0.9.A, B.1.E.1, C.1.8.8] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.8 |  |  | 570 | 720 | 800 | 6 | 12 | 18 | 30 | 45 | 60 | 96.7 | 97.7 | 97.9 | 98 | 98 | 97.8 | 97.9 | 97.2 | 98.1 | 98.4 | 98.5 | 98.5 | 98.4 | 98.4 | 96.4 | 97.8 | 98.1 | 98.3 | 98.3 | 98.2 | 98.2 | 2017-07-01 | 2018-10-15
ABB | TRIO-TM-60.0-US-480 {480V} | N | N | Y | Y | Y | N | N | N | 60 kVA, 480 Vac Grid Support Utility Interactive Inverter with arc detector | 60 | 480 | 98 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [04/12/2018] | [A.0.2.7, B.0.2.9, C.0.5.1] | 2018-10-15 | [04/12/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.6 |  |  | 570 | 720 | 800 | 6 | 12 | 18 | 30 | 45 | 60 | 96.7 | 97.6 | 97.8 | 97.9 | 97.8 | 97.6 | 97.8 | 97.3 | 98.3 | 98.5 | 98.6 | 98.6 | 98.4 | 98.5 | 96.7 | 98 | 98.3 | 98.4 | 98.4 | 98.3 | 98.3 | 2018-06-01 | 2018-10-15
ABB | PVS-60-TL-R-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kVA 480Vac transformerless Grid Support Utility Inverter with arc detection. | 60.033 | 480 | 98 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/15/2020] | [1945E] | 2020-09-01 | [06/15/2020] | 2020-09-01 | UL | 2020-07-29 | 2020-09-01 |  | Y | N | 0.9 |  |  | 570 | 720 | 800 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.761 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 98.4835 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517 | 98.2671 | 2020-09-01
ABB | PVS-60-TL-SC-R-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kVA 480Vac transformerless Grid Support Utility Inverter with arc detection. | 60.033 | 480 | 98 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/15/2020] | [1945E] | 2020-09-01 | [06/15/2020] | 2020-09-01 | UL | 2020-07-29 | 2020-09-01 |  | Y | N | 0.9 |  |  | 570 | 720 | 800 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.761 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 98.4835 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517 | 98.2671 | 2020-09-01
ABB | PVS-60-TL-SC-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kW, 480 V transformerless Grid Support Uitlity Interactive Inverter | 60.033 | 480 | 98 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/15/2020] | [1945E] | 2019-06-03 | [06/15/2020] | 2020-09-01 | UL | 2020-07-29 | 2020-09-01 |  | Y | N | 0.9 |  |  | 570 | 720 | 800 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.761 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 98.4835 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517 | 98.2671 | 2019-06-03 | 2020-09-01
ABB | PVS-60-TL-S-R-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kVA 480Vac transformerless Grid Support Utility Inverter with arc detection. | 60.033 | 480 | 98 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/15/2020] | [1945E] | 2020-09-01 | [06/15/2020] | 2020-09-01 | UL | 2020-07-29 | 2020-09-01 |  | Y | N | 0.9 |  |  | 570 | 720 | 800 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.761 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 98.4835 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517 | 98.2671 | 2020-09-01
ABB | PVS-60-TL-S-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kW, 480 V transformerless Grid Support Uitlity Interactive Inverter | 60.033 | 480 | 98 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/15/2020] | [1945E] | 2019-06-03 | [06/15/2020] | 2020-09-01 | UL | 2020-07-29 | 2020-09-01 |  | Y | N | 0.9 |  |  | 570 | 720 | 800 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.761 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 98.4835 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517 | 98.2671 | 2019-06-03 | 2020-09-01
ABB | PVS-60-TL-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kW, 480 V transformerless Grid Support Uitlity Interactive Inverter | 60.033 | 480 | 98 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/15/2020] | [1945E] | 2019-06-03 | [06/15/2020] | 2020-09-01 | UL | 2020-07-29 | 2020-09-01 |  | Y | N | 0.9 |  |  | 570 | 720 | 800 | 6.0033 | 12.0066 | 18.0098 | 30.0164 | 45.0246 | 60.0328 | 96.5178 | 97.5972 | 97.8433 | 97.8474 | 97.8285 | 97.6431 | 97.761 | 97.1899 | 98.2527 | 98.4975 | 98.5891 | 98.5631 | 98.4288 | 98.4835 | 96.4868 | 97.9037 | 98.2417 | 98.3996 | 98.3905 | 98.2517 | 98.2671 | 2019-06-03 | 2020-09-01
ABB | PVS-166-TL-POWER-MODULE-1-US {800V} | N | N | Y | Y | Y | Y | Y* | Y | 166 kW, 800 V transformerless Grid Support Utility Interactive inverter | 165.954 | 800 | 98.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [07/13/2020] | [1923D] | 2019-12-23 | [07/13/2020] | 2020-09-01 | UL | 2020-07-29 | 2020-09-01 |  | Y | N | 12 |  |  | 850 | 1100 | 1200 | 16.595 | 33.191 | 49.786 | 82.977 | 124.466 | 165.954 | 96.77 | 98.03 | 98.27 | 98.39 | 98.32 | 98.15 | 98.25 | 96.7 | 98.08 | 98.39 | 98.53 | 98.48 | 98.34 | 98.38 | 95.77 | 97.71 | 98.11 | 98.23 | 98.33 | 98.25 | 98.15 | 2019-12-23 | 2020-09-01
ABB | PVS-166-TL-POWER-MODULE-2-US {800V} | N | N | Y | Y | Y | Y | Y* | Y | 166 kW, 800 V transformerless Grid Support Utility Interactive inverter | 165.954 | 800 | 98.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [07/13/2020] | [1923D] | 2019-12-23 | [07/13/2020] | 2020-09-01 | UL | 2020-07-29 | 2020-09-01 |  | Y | N | 12 |  |  | 850 | 1100 | 1200 | 16.595 | 33.191 | 49.786 | 82.977 | 124.466 | 165.954 | 96.77 | 98.03 | 98.27 | 98.39 | 98.32 | 98.15 | 98.25 | 96.7 | 98.08 | 98.39 | 98.53 | 98.48 | 98.34 | 98.38 | 95.77 | 97.71 | 98.11 | 98.23 | 98.33 | 98.25 | 98.15 | 2019-12-23 | 2020-09-01
ABB | PVS-175-TL-POWER-MODULE-1-US {800V} | N | N | Y | Y | Y | Y | Y* | Y | 175 kW, 800 V transformerless Grid Support Utility Interactive inverter | 179.574 | 800 | 98.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [07/13/2020] | [1923D] | 2019-12-23 | [07/13/2020] | 2020-09-01 | UL | 2020-07-29 | 2020-09-01 |  | Y | N | 12 |  |  | 850 | 1100 | 1200 | 17.957 | 35.915 | 53.872 | 89.787 | 134.681 | 179.574 | 95.65 | 97.31 | 97.7 | 97.83 | 97.59 | 97.24 | 97.54 | 95.6 | 97.4 | 97.8 | 97.94 | 97.76 | 97.52 | 97.69 | 94.83 | 97.05 | 97.53 | 97.62 | 97.61 | 97.36 | 97.45 | 2019-12-23 | 2020-09-01
ABB | PVS-175-TL-POWER-MODULE-2-US {800V} | N | N | Y | Y | Y | Y | Y* | Y | 175 kW, 800 V transformerless Grid Support Utility Interactive inverter | 179.574 | 800 | 98.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [07/13/2020] | [1923D] | 2019-12-23 | [07/13/2020] | 2020-09-01 | UL | 2020-07-29 | 2020-09-01 |  | Y | N | 12 |  |  | 850 | 1100 | 1200 | 17.957 | 35.915 | 53.872 | 89.787 | 134.681 | 179.574 | 95.65 | 97.31 | 97.7 | 97.83 | 97.59 | 97.24 | 97.54 | 95.6 | 97.4 | 97.8 | 97.94 | 97.76 | 97.52 | 97.69 | 94.83 | 97.05 | 97.53 | 97.62 | 97.61 | 97.36 | 97.45 | 2019-12-23 | 2020-09-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF4.6K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 4.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.55 |  |  | 170 | 360 | 480 | 0.46004 | 0.92008 | 1.3801 | 2.3002 | 3.4503 | 4.6004 | 90.0323 | 93.5475 | 95.1945 | 96.1078 | 97.0873 | 97.6576 | 96.2238 | 92.0536 | 95.4444 | 96.6155 | 97.193 | 97.6015 | 97.9183 | 97.0835 | 91.3957 | 94.457 | 95.607 | 96.4039 | 97.3965 | 97.7534 | 96.6042 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF5K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 5 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.998 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.54 |  |  | 185 | 360 | 480 | 0.49977 | 0.99954 | 1.4993 | 2.4988 | 3.7483 | 4.9977 | 90.4784 | 93.2137 | 95.14 | 96.0694 | 96.9926 | 97.6424 | 96.1594 | 92.4052 | 95.3595 | 96.3498 | 97.3339 | 97.7012 | 97.8953 | 97.1427 | 92.1092 | 94.4574 | 96.025 | 96.9389 | 97.2818 | 97.7372 | 96.7336 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF6K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.995 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.55 |  |  | 220 | 360 | 480 | 0.59949 | 1.199 | 1.7985 | 2.9974 | 4.4962 | 5.9949 | 89.6111 | 93.1275 | 95.0844 | 95.9139 | 96.7975 | 97.5628 | 95.9737 | 91.5635 | 95.2459 | 96.3148 | 97.026 | 97.4503 | 97.6847 | 96.891 | 90.447 | 94.2504 | 95.2582 | 96.0739 | 97.3601 | 97.5238 | 96.4139 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF7K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 7 kW, 240 Vac Grid Support Utility Interactive Inverter | 6.996 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.55 |  |  | 170 | 360 | 480 | 0.69965 | 1.3993 | 2.0989 | 3.4982 | 5.2474 | 6.9965 | 90.3929 | 93.17 | 95.0405 | 95.8786 | 97.0631 | 97.8025 | 96.1472 | 91.7958 | 94.7364 | 95.9576 | 97.3508 | 97.62 | 98.0209 | 97.0069 | 90.9421 | 94.2244 | 95.3311 | 97.2654 | 97.577 | 97.9083 | 96.8256 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF7.6K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.599 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.55 |  |  | 185 | 360 | 480 | 0.75993 | 1.5199 | 2.2798 | 3.7996 | 5.6995 | 7.5993 | 90.5816 | 93.924 | 95.0812 | 95.9376 | 96.8505 | 97.3432 | 96.074 | 92.2385 | 94.5571 | 95.506 | 96.3515 | 97.2995 | 97.7191 | 96.5666 | 91.2608 | 94.6559 | 95.4007 | 96.3723 | 97.146 | 97.5532 | 96.4345 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF8K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 8 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.999 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.64 |  |  | 195 | 360 | 480 | 0.79986 | 1.5997 | 2.3996 | 3.9993 | 5.9989 | 7.9986 | 91.8222 | 93.64 | 95.1025 | 96.117 | 97.2117 | 97.5628 | 96.3521 | 92.4234 | 95.301 | 96.372 | 97.1563 | 97.482 | 97.9602 | 96.9929 | 91.3948 | 94.4946 | 95.4063 | 96.7014 | 97.5172 | 97.7524 | 96.7083 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF8.6K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 8.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 8.596 | 240 | 97 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.58 |  |  | 210 | 360 | 480 | 0.85956 | 1.7191 | 2.5787 | 4.2978 | 6.4467 | 8.5956 | 92.3963 | 94.4909 | 95.2393 | 96.215 | 97.3575 | 97.7814 | 96.5428 | 93.4917 | 95.4239 | 96.5341 | 97.3485 | 97.6449 | 97.9515 | 97.1875 | 93.2217 | 95.1588 | 95.5559 | 96.7104 | 97.5554 | 97.9038 | 96.8622 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF9.6K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.592 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.65 |  |  | 235 | 360 | 480 | 0.9592 | 1.9184 | 2.8776 | 4.796 | 7.194 | 9.592 | 90.0006 | 93.7166 | 95.2164 | 96.0942 | 97.1032 | 97.8688 | 96.2497 | 91.9548 | 95.489 | 96.5298 | 97.3018 | 97.623 | 97.9692 | 97.1082 | 91.4432 | 94.7028 | 95.6808 | 96.6654 | 97.5238 | 97.776 | 96.7507 | 2022-12-01
AIMS Power Inc. | PIHY4600 {240V} | Y | N | Y | Y | Y | Y | Y* | N | 4.6 kW, 240 Vac, Grid Support Utility Interactive Inverter | 4.6004 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [11/17/2022] | [1.11] | 2023-02-13 | [11/17/2022] | 2023-02-13 | Intertek | 2022-06-20 | No Information Submitted |  | N | N | 0.55 |  |  | 170 | 360 | 480 | 0.46004 | 0.92008 | 1.3801 | 2.3002 | 3.4503 | 4.6004 | 90.0323 | 93.5475 | 95.1945 | 96.1078 | 97.0873 | 97.6576 | 96.2238 | 92.0536 | 95.4444 | 96.6155 | 97.193 | 97.6015 | 97.9183 | 97.0835 | 91.3957 | 94.457 | 95.607 | 96.4039 | 97.3965 | 97.7534 | 96.6042 | 2023-02-13
AIMS Power Inc. | PIHY9600 {240V} | Y | N | Y | Y | Y | Y | Y* | N | 9.6 kW, 240 Vac, Grid Support Utility Interactive Inverter | 9.592 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [11/17/2022] | [1.11] | 2023-02-13 | [11/17/2022] | 2023-02-13 | Intertek | 2022-06-20 | No Information Submitted |  | N | N | 0.65 |  |  | 235 | 360 | 480 | 0.9592 | 1.9184 | 2.8776 | 4.796 | 7.194 | 9.592 | 90.0006 | 93.7166 | 95.2164 | 96.0942 | 97.1032 | 97.8688 | 96.2497 | 91.9548 | 95.489 | 96.5298 | 97.3018 | 97.623 | 97.9692 | 97.1082 | 91.4432 | 94.7028 | 95.6808 | 96.6654 | 97.5238 | 97.776 | 96.7507 | 2023-02-13
Alpha ESS Co., Ltd. | SMILE-SP7.6-INV {240V} | Y | Y | N | N | N | N | Y | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.644 | 240 | 97 | CSA Group | [5/5/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-07-09 | 2024-09-23 |  | N | N | 9.44 |  |  | 230 | 400 | 480 | 0.764 | 1.529 | 2.293 | 3.822 | 5.733 | 7.644 | 94.86 | 96.15 | 96.53 | 96.68 | 96.44 | 96.2 | 96.41 | 96.22 | 97.36 | 97.65 | 97.68 | 97.53 | 97.26 | 97.5 | 95.62 | 97.01 | 97.4 | 97.59 | 97.45 | 97.2 | 97.36 | 2024-05-01 | 2024-09-23
Alpha ESS Co., Ltd. | SMILE-SP9.6-INV {240V} | Y | Y | N | N | N | N | Y | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 9.628 | 240 | 97 | CSA Group | [5/5/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-07-09 | 2024-09-23 |  | N | N | 9.4 |  |  | 300 | 400 | 480 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7607 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 97.378 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369 | 97.2329 | 2024-05-01 | 2024-09-23
Altenergy Power System Inc. | YC600 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 548 W, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 0.55 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [02/10/2018] | [V5] | 2018-10-15 | [01/25/2019] | 2020-04-13 | CSA Group | 2020-02-21 | 2020-04-13 |  | N | Y | 0.02 |  |  | 24 | 36 | 45 | 0.0548 | 0.1096 | 0.1644 | 0.274 | 0.411 | 0.548 | 94.4 | 95.9 | 96 | 96.4 | 96.3 | 96.1 | 96.2 | 94.1 | 95.8 | 96.2 | 96.5 | 96.7 | 96.6 | 96.4 | 93.7 | 95.7 | 95.8 | 96.4 | 96.7 | 96.7 | 96.4 | 2018-03-01 | 2020-04-13
Altenergy Power System Inc. | DS3-S {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 640 VA, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 0.656 | 240 | 96.5 | CSA Group | [3/16/2023] | CSA Group | [12/3/2021] | [V3] | 2022-01-11 | [12/3/2021] | 2022-02-22 | CSA Group | 2021-12-15 | 2022-02-22 |  | N | Y | 0.0309 |  |  | 36 | 39 | 43 | 0.065576 | 0.13115 | 0.19673 | 0.32788 | 0.49182 | 0.65576 | 93.181 | 95.6973 | 96.3996 | 97.1172 | 97.3735 | 97.3721 | 96.9512 | 91.3188 | 95.4251 | 96.1626 | 96.921 | 97.2096 | 97.2115 | 96.6986 | 88.8902 | 94.6788 | 95.3854 | 96.6674 | 97.0063 | 97.058 | 96.3022 | 2022-01-11 | 2023-04-21
Altenergy Power System Inc. | DS3-L {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 768 VA, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 0.78 | 240 | 97 | CSA Group | [3/16/2023] | CSA Group | [12/3/2021] | [V3] | 2022-01-11 | [12/3/2021] | 2022-02-22 | CSA Group | 2021-12-15 | 2022-02-22 |  | N | Y | 0.0298 |  |  | 36 | 39 | 43 | 0.078012 | 0.15602 | 0.23404 | 0.39006 | 0.58509 | 0.78012 | 93.9415 | 96.1616 | 96.4671 | 97.324 | 97.3934 | 97.2869 | 97.0627 | 92.635 | 95.8543 | 96.2083 | 97.1732 | 97.1851 | 97.1197 | 96.8136 | 90.7535 | 95.265 | 95.608 | 96.9238 | 97.026 | 96.9688 | 96.4926 | 2022-01-11 | 2023-04-21
Altenergy Power System Inc. | DS3 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 880 VA, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 0.896 | 240 | 97 | CSA Group | [3/16/2023] | CSA Group | [12/3/2021] | [V3] | 2022-01-11 | [12/3/2021] | 2022-02-22 | CSA Group | 2021-12-15 | 2022-02-22 |  | N | Y | 0.0307 |  |  | 36 | 39 | 43 | 0.08959 | 0.17918 | 0.26877 | 0.44795 | 0.67192 | 0.8959 | 94.3657 | 96.2996 | 96.7019 | 97.3487 | 97.3711 | 97.1574 | 97.1016 | 93.4249 | 96.0554 | 96.2969 | 97.187 | 97.1895 | 96.9841 | 96.8643 | 91.7219 | 95.3753 | 95.781 | 96.9412 | 97.0431 | 96.8177 | 96.5628 | 2022-01-11 | 2023-04-21
Altenergy Power System Inc. | DS3-LV {120V} | N | Y | N | N | N | N | Y* | Y | 900 VA, 120 Vac, Grid Support Utility Interactive Microinverter | 0.915 | 120 | 95 | CSA Group | [7/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-07-09 | 2024-10-11 |  | N | Y | 0.03 |  |  | 28 | 36 | 45 | 0.091 | 0.183 | 0.274 | 0.457 | 0.686 | 0.915 | 93.85 | 95.45 | 95.81 | 95.77 | 95.12 | 94.2 | 95.26 | 91.96 | 94.63 | 95.44 | 95.49 | 94.9 | 93.95 | 94.91 | 90.23 | 91.35 | 95.08 | 95.16 | 94.92 | 94.02 | 94.58 | 2024-10-11
Altenergy Power System Inc. | EZ1-LV {120V} | N | Y | N | N | N | N | Y* | Y | 900 VA, 120 Vac, Grid Support Utility Interactive Microinverter | 0.915 | 120 | 95 | CSA Group | [7/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-07-09 | 2024-10-11 |  | N | Y | 0.03 |  |  | 28 | 36 | 45 | 0.091 | 0.183 | 0.274 | 0.457 | 0.686 | 0.915 | 93.85 | 95.45 | 95.81 | 95.77 | 95.12 | 94.2 | 95.26 | 91.96 | 94.63 | 95.44 | 95.49 | 94.9 | 93.95 | 94.91 | 90.23 | 91.35 | 95.08 | 95.16 | 94.92 | 94.02 | 94.58 | 2024-10-11
Altenergy Power System Inc. | DS3-H {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 1050 VA, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 1.068 | 240 | 97 | CSA Group | [3/16/2023] | CSA Group | [12/3/2021] | [V3] | 2022-01-11 | [12/3/2021] | 2022-02-22 | CSA Group | 2021-12-15 | 2022-02-22 |  | N | Y | 0.0302 |  |  | 36 | 39 | 43 | 0.10678 | 0.21356 | 0.32034 | 0.5339 | 0.80085 | 1.0678 | 95.1794 | 96.5032 | 97.0713 | 97.3703 | 97.247 | 96.8666 | 97.1129 | 94.6754 | 96.5032 | 96.8828 | 97.2184 | 97.0584 | 96.686 | 96.9292 | 93.3921 | 95.4955 | 96.6088 | 97.0261 | 96.932 | 96.553 | 96.6806 | 2022-01-11 | 2023-04-21
Altenergy Power System Inc. | QS1 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 1.2 kW, 208 Vac Grid Support Utility Interactive Microinverter | 1.2183 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [02/07/2021] | [V5] | 2021-03-11 | [02/07/2021] | 2021-03-11 | CSA Group | 2021-02-05 | 2021-03-11 |  | N | Y | 0.046 |  |  | 27 | 37.5 | 48 | 0.12183 | 0.24366 | 0.36549 | 0.60914 | 0.91372 | 1.2183 | 95.4629 | 96.4508 | 96.5764 | 96.5697 | 96.1392 | 95.4927 | 96.2383 | 95.1509 | 96.3907 | 96.7164 | 96.7168 | 96.3775 | 95.9339 | 96.4189 | 94.854 | 96.1629 | 96.0576 | 96.5787 | 96.3787 | 95.9939 | 96.2912 | 2021-03-11
Altenergy Power System Inc. | QS1 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 1.225 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/28/2019] | [V5] | 2019-03-01 | [01/28/2019] | 2020-04-21 | CSA Group | 2020-03-18 | 2020-04-21 |  | N | Y | 0.09 |  |  | 27 | 37.5 | 48 | 0.12252 | 0.24503 | 0.36755 | 0.61258 | 0.91887 | 1.2252 | 93.497 | 96.0302 | 96.2918 | 96.5164 | 96.1897 | 95.6368 | 96.1272 | 93.4891 | 96.0102 | 96.472 | 96.7093 | 96.5407 | 96.1255 | 96.3985 | 92.8188 | 95.8573 | 96.4916 | 96.6522 | 96.6297 | 96.2942 | 96.41 | 2019-03-01 | 2020-04-21
Altenergy Power System Inc. | QS1200 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 1.225 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/28/2019] | [V5] | 2019-03-01 | [01/28/2019] | 2020-04-21 | CSA Group | 2020-03-18 | 2020-04-21 |  | N | Y | 0.09 |  |  | 27 | 37.5 | 48 | 0.12252 | 0.24503 | 0.36755 | 0.61258 | 0.91887 | 1.2252 | 93.497 | 96.0302 | 96.2918 | 96.5164 | 96.1897 | 95.6368 | 96.1272 | 93.4891 | 96.0102 | 96.472 | 96.7093 | 96.5407 | 96.1255 | 96.3985 | 92.8188 | 95.8573 | 96.4916 | 96.6522 | 96.6297 | 96.2942 | 96.41 | 2019-03-01 | 2020-04-21
Altenergy Power System Inc. | QS1A {240V} | N | N | Y | Y | Y | N | N | N | 1.5 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.516 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [07/02/2021] | [V7] | 2021-08-23 | [07/02/2021] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.038 |  |  | 30 | 41 | 52 | 0.152 | 0.303 | 0.455 | 0.758 | 1.137 | 1.516 | 95.51 | 96.54 | 96.63 | 96.65 | 96.14 | 95.39 | 96.26 | 95.29 | 96.49 | 96.46 | 96.74 | 96.36 | 95.82 | 96.39 | 94.75 | 96.22 | 96.1 | 96.61 | 96.35 | 95.99 | 96.28 | 2021-08-23
Altenergy Power System Inc. | QT2 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 1728 VA, 208 Vac Grid Support Utility Interactive Inverter | 1.733 | 208 | 96 | CSA Group | [3/30/2023] | CSA Group | [3/30/2023] | [V3] | 2022-10-03 | [3/30/2023] | 2022-10-21 | CSA Group | 2022-09-14 | 2022-10-21 |  | N | Y | 0.087 |  |  | 34 | 38 | 42 | 0.17335 | 0.34669 | 0.52004 | 0.86673 | 1.3001 | 1.7335 | 91.7047 | 94.9566 | 95.8278 | 96.4736 | 96.2718 | 95.6544 | 95.9816 | 91.1033 | 94.6328 | 95.5262 | 96.2977 | 96.0945 | 95.5277 | 95.7679 | 90.7908 | 94.3068 | 95.2091 | 96.1291 | 96.0151 | 95.4601 | 95.6202 | 2022-10-03 | 2023-05-11
Altenergy Power System Inc. | QT2-208 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 1728 VA, 208 Vac Grid Support Utility Interactive Inverter | 1.733 | 208 | 96 | CSA Group | [3/30/2023] | CSA Group | [3/30/2023] | [V3] | 2022-10-03 | [3/30/2023] | 2022-10-21 | CSA Group | 2022-09-14 | 2022-10-21 |  | N | Y | 0.087 |  |  | 34 | 38 | 42 | 0.17335 | 0.34669 | 0.52004 | 0.86673 | 1.3001 | 1.7335 | 91.7047 | 94.9566 | 95.8278 | 96.4736 | 96.2718 | 95.6544 | 95.9816 | 91.1033 | 94.6328 | 95.5262 | 96.2977 | 96.0945 | 95.5277 | 95.7679 | 90.7908 | 94.3068 | 95.2091 | 96.1291 | 96.0151 | 95.4601 | 95.6202 | 2022-10-03 | 2023-05-11
Altenergy Power System Inc. | QT2 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 1800 VA, 480 Vac Grid Support Utility Interactive Inverter | 1.821 | 480 | 95.5 | CSA Group | [3/30/2023] | CSA Group | [3/30/2023] | [V3] | 2022-10-03 | [3/30/2023] | 2022-10-21 | CSA Group | 2022-09-14 | 2022-10-21 |  | N | Y | 0.2248 |  |  | 34 | 38 | 42 | 0.18209 | 0.36418 | 0.54628 | 0.91046 | 1.3657 | 1.8209 | 91.7619 | 95.0301 | 95.8934 | 95.8613 | 96.5617 | 96.4818 | 96.0618 | 91.0471 | 94.4013 | 95.2407 | 94.6659 | 95.9417 | 95.9714 | 95.3184 | 90.5428 | 93.7744 | 94.5888 | 95.1333 | 95.1599 | 95.6227 | 94.855 | 2022-10-03 | 2023-05-11
Altenergy Power System Inc. | QT2-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 1800 VA, 480 Vac Grid Support Utility Interactive Inverter | 1.821 | 480 | 95.5 | CSA Group | [3/30/2023] | CSA Group | [3/30/2023] | [V3] | 2022-10-03 | [3/30/2023] | 2022-10-21 | CSA Group | 2022-09-14 | 2022-10-21 |  | N | Y | 0.2248 |  |  | 34 | 38 | 42 | 0.18209 | 0.36418 | 0.54628 | 0.91046 | 1.3657 | 1.8209 | 91.7619 | 95.0301 | 95.8934 | 95.8613 | 96.5617 | 96.4818 | 96.0618 | 91.0471 | 94.4013 | 95.2407 | 94.6659 | 95.9417 | 95.9714 | 95.3184 | 90.5428 | 93.7744 | 94.5888 | 95.1333 | 95.1599 | 95.6227 | 94.855 | 2022-10-03 | 2023-05-11
Altenergy Power System Inc. | QS2 {208V} | N | Y | N | N | N | N | Y* |  | 1920 VA, 208 Vac, Grid Support Utility Interactive Microinverter | 1.9226 | 208 | 95.5 | CSA Group | [9/4/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-08-19 |  |  | N | Y | 0.003 |  |  | 30 | 38 | 45 | 0.19226 | 0.38453 | 0.57679 | 0.96132 | 1.442 | 1.9226 | 92.8349 | 95.4023 | 95.9593 | 96.1007 | 95.6838 | 94.8766 | 95.636 | 91.6254 | 94.4081 | 94.7503 | 95.8276 | 95.4129 | 94.6642 | 95.1813 | 90.4979 | 93.5436 | 94.0868 | 95.6285 | 95.4257 | 94.5398 | 94.9721 | 2025-11-03
Altenergy Power System Inc. | QS2 {240V} | N | Y | N | N | N | N | Y* |  | 1920 VA, 240 Vac, Grid Support Utility Interactive Microinverter | 1.9239 | 240 | 95.5 | CSA Group | [9/4/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-08-19 |  |  | N | Y | 0.004 |  |  | 30 | 38 | 45 | 0.19239 | 0.38478 | 0.57717 | 0.96195 | 1.4429 | 1.9239 | 92.4766 | 95.5292 | 96.1933 | 96.4307 | 96.0832 | 95.3708 | 95.9618 | 91.2929 | 94.4941 | 94.8829 | 96.1353 | 95.7768 | 95.1599 | 95.4705 | 90.1448 | 93.6274 | 94.2495 | 95.9298 | 95.8089 | 95.0408 | 95.2731 | 2025-11-03
Amensolar Ess Co., Ltd | N3H-X5.0-US {240V} | Y | Y | N | N | N | N | N | N | 5 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 5.09 | 240 | 97 | SGS | [2/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2023-06-12
Amensolar Ess Co., Ltd | N3H-X5US {240V} | Y | Y | N | N | N | N | N | N | 5.0 kW, 240Vac Grid Support Utility Interactive Hybrid Inverter | 5.09 | 240 | 97 | SGS | [10/12/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.509 | 1.018 | 1.527 | 2.545 | 3.817 | 5.09 | 94.57 | 95.73 | 96.2 | 96.92 | 97.19 | 96.59 | 96.81 | 95.31 | 96.27 | 96.69 | 97.41 | 97.78 | 97.08 | 97.36 | 95.11 | 95.97 | 96.72 | 97.19 | 97.64 | 96.85 | 97.21 | 2025-04-01
Amensolar Ess Co., Ltd | N3H-X6.0-US {240V} | Y | Y | N | N | N | N | N | N | 6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 6.117 | 240 | 97 | SGS | [2/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2023-06-12
Amensolar Ess Co., Ltd | N3H-X7.6-US {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 7.765 | 240 | 97 | SGS | [2/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2023-06-12
Amensolar Ess Co., Ltd | N3H-X8.0-US {240V} | Y | Y | N | N | N | N | N | N | 8 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 8.084 | 240 | 97 | SGS | [2/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.808 | 1.617 | 2.425 | 4.042 | 6.063 | 8.084 | 93.98 | 95.42 | 96.35 | 97.36 | 97.92 | 96.85 | 97.27 | 93.95 | 95.64 | 96.59 | 97.27 | 97.93 | 97.01 | 97.31 | 94.07 | 95.49 | 96.43 | 97.32 | 97.69 | 96.99 | 97.17 | 2023-06-12
Amensolar Ess Co., Ltd | N3H-X8US {240V} | Y | Y | N | N | N | N | N | N | 8.0 kW, 240Vac Grid Support Utility Interactive Hybrid Inverter | 8.084 | 240 | 97.5 | SGS | [10/12/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.808 | 1.617 | 2.425 | 4.042 | 6.063 | 8.084 | 93.98 | 95.42 | 96.35 | 97.36 | 97.92 | 96.85 | 97.27 | 93.95 | 95.64 | 96.59 | 97.27 | 97.93 | 97.01 | 97.31 | 94.07 | 95.49 | 96.43 | 97.32 | 97.69 | 96.99 | 97.17 | 2025-04-01
Amensolar Ess Co., Ltd | N3H-X10.0-US {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 10.177 | 240 | 97 | SGS | [2/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2023-06-12
Amensolar Ess Co., Ltd | N3H-X10US {240V} | Y | Y | N | N | N | N | N | N | 10.0 kW, 240Vac Grid Support Utility Interactive Hybrid Inverter | 10.177 | 240 | 97 | SGS | [10/12/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.018 | 2.035 | 3.053 | 5.088 | 7.632 | 10.177 | 94.69 | 95.94 | 96.4 | 96.8 | 97.34 | 96.75 | 96.91 | 95.39 | 96.33 | 96.85 | 97.45 | 97.97 | 97.37 | 97.51 | 94.93 | 95.96 | 96.65 | 97.01 | 97.56 | 97.03 | 97.12 | 2025-04-01
Amensolar Ess Co., Ltd | N3H-X12US {240V} | Y | Y | N | N | N | N | N | N | 12.0 kW, 240Vac Grid Support Utility Interactive Hybrid Inverter | 12.214 | 240 | 96 | SGS | [11/11/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 13.202 |  |  | 200 | 360 | 430 | 1.221 | 2.443 | 3.664 | 6.107 | 9.16 | 12.214 | 93.59 | 95.32 | 95.52 | 95.8 | 95.49 | 95.61 | 95.48 | 94.26 | 96.13 | 96.66 | 96.87 | 96.62 | 96.29 | 96.54 | 94 | 96.18 | 96.74 | 96.88 | 96.68 | 96.36 | 96.58 | 2025-04-01
Amensolar Ess Co., Ltd | N3H-X16US {240V} | Y | Y | N | N | N | N | N | N | 16.0 kW, 240Vac Grid Support Utility Interactive Hybrid Inverter | 16.199 | 240 | 96 | SGS | [11/11/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 16.199 |  |  | 220 | 360 | 430 | 1.62 | 3.24 | 4.86 | 8.099 | 12.149 | 16.199 | 93.66 | 95.36 | 95.8 | 95.93 | 95.51 | 96.18 | 95.59 | 94.19 | 96.06 | 96.55 | 96.88 | 96.64 | 96.35 | 96.53 | 94.09 | 96 | 96.54 | 96.95 | 96.69 | 96.25 | 96.57 | 2025-04-01
Anker Innovations Limited | MI80S {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 640 VA, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 0.656 | 240 | 96.5 | CSA Group | [4/7/2024] | CSA Group | [4/7/2024] | [V3] | 2024-05-21 | [4/9/2024] | 2024-05-21 | CSA Group | 2024-04-12 | 2024-05-21 |  | N | Y | 0.0309 |  |  | 36 | 39 | 43 | 0.065576 | 0.13115 | 0.19673 | 0.32788 | 0.49182 | 0.65576 | 93.181 | 95.6973 | 96.3996 | 97.1172 | 97.3735 | 97.3721 | 96.9512 | 91.3188 | 95.4251 | 96.1626 | 96.921 | 97.2096 | 97.2115 | 96.6986 | 88.8902 | 94.6788 | 95.3854 | 96.6674 | 97.0063 | 97.058 | 96.3022 | 2024-05-21
Anker Innovations Limited | MI80L {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 768 VA, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 0.78 | 240 | 97 | CSA Group | [4/7/2024] | CSA Group | [4/7/2024] | [V3] | 2024-05-21 | [4/9/2024] | 2024-05-21 | CSA Group | 2024-04-12 | 2024-05-21 |  | N | Y | 0.0298 |  |  | 36 | 39 | 43 | 0.078012 | 0.15602 | 0.23404 | 0.39006 | 0.58509 | 0.78012 | 93.9415 | 96.1616 | 96.4671 | 97.324 | 97.3934 | 97.2869 | 97.0627 | 92.635 | 95.8543 | 96.2083 | 97.1732 | 97.1851 | 97.1197 | 96.8136 | 90.7535 | 95.265 | 95.608 | 96.9238 | 97.026 | 96.9688 | 96.4926 | 2024-05-21
Anker Innovations Limited | MI80 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 880 VA, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 0.896 | 240 | 97 | CSA Group | [4/7/2024] | CSA Group | [4/7/2024] | [V3] | 2024-05-21 | [4/9/2024] | 2024-05-21 | CSA Group | 2024-04-12 | 2024-05-21 |  | N | Y | 0.0307 |  |  | 36 | 39 | 43 | 0.08959 | 0.17918 | 0.26877 | 0.44795 | 0.67192 | 0.8959 | 94.3657 | 96.2996 | 96.7019 | 97.3487 | 97.3711 | 97.1574 | 97.1016 | 93.4249 | 96.0554 | 96.2969 | 97.187 | 97.1895 | 96.9841 | 96.8643 | 91.7219 | 95.3753 | 95.781 | 96.9412 | 97.0431 | 96.8177 | 96.5628 | 2024-05-21
Anker Innovations Limited | MI80H {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 1050 VA, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 1.068 | 240 | 97 | CSA Group | [4/7/2024] | CSA Group | [4/7/2024] | [V3] | 2024-05-21 | [4/9/2024] | 2024-05-21 | CSA Group | 2024-04-12 | 2024-05-21 |  | N | Y | 0.0302 |  |  | 36 | 39 | 43 | 0.10678 | 0.21356 | 0.32034 | 0.5339 | 0.80085 | 1.0678 | 95.1794 | 96.5032 | 97.0713 | 97.3703 | 97.247 | 96.8666 | 97.1129 | 94.6754 | 96.5032 | 96.8828 | 97.2184 | 97.0584 | 96.686 | 96.9292 | 93.3921 | 95.4955 | 96.6088 | 97.0261 | 96.932 | 96.553 | 96.6806 | 2024-05-21
Anker Innovations Limited | A17E1 {240V} | Y | Y | N | N | N | N | Y* |  | 7.68 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.687 | 240 | 96 | SGS | [9/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-09-23 |  |  | N | N | 8.23 |  |  | 350 | 400 | 450 | 0.769 | 1.537 | 2.306 | 3.844 | 5.765 | 7.687 | 91.34 | 94.38 | 95.35 | 95.94 | 96.03 | 95.48 | 95.63 | 94.04 | 96.12 | 96.69 | 96.97 | 96.93 | 96.28 | 96.72 | 93.21 | 95.57 | 96.28 | 96.63 | 96.58 | 96.02 | 96.34 | 2025-12-01
Apparent Inc. | SG424U CA, 120VAC, 60Hz {120V} | N | N | Y | Y | Y | Y | Y* | Y | 250 W, 120 Vac Grid Support Utility Interactive Microinverter | 0.25 | 120 | 91.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [08/24/2018] | [R313] | 2019-04-02 | [08/24/2018] | 2022-08-22 | TUV Rheinland | 2022-03-17 | 2021-01-11 |  | N | Y | 0.45 |  |  | 31.2 | 36.4 | 48.9 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 85.4 | 91.1 | 91.5 | 92.1 | 91.8 | 90.6 | 91.5 | 87 | 90.8 | 91.5 | 92.4 | 92.2 | 91.2 | 91.8 | 86.1 | 90.9 | 92 | 92.2 | 92.4 | 92 | 92 | 2019-04-02 | 2022-08-22
Apparent Inc. | SG424-PLUS-120VAC-60HZ-CA {120V} | N | Y | N | N | N | N | N | N | 325 W, 120 Vac Grid Support Utility Interactive Microinverter | 0.326 | 120 | 91.5 | TUV | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.528 |  |  | 36 | 44 | 52 | 0.033 | 0.065 | 0.098 | 0.163 | 0.244 | 0.326 | 85.21 | 90.2 | 91.5 | 91.95 | 91.55 | 90.53 | 91.25 | 85.37 | 90.66 | 91.37 | 92.09 | 91.86 | 91.05 | 91.49 | 84.92 | 90.49 | 91.67 | 92.02 | 91.96 | 91.32 | 91.55 | 2025-02-03
Aptos Solar Technology LLC | MAC-400 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 382 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.38254 | 240 | 96.5 | CSA Group | [3/17/2023] | CSA Group | [06/07/2020] | [V01.01.00] | 2022-08-22 | [06/07/2020] | 2022-08-22 | CSA Group | 2022-06-08 | 2022-08-22 |  | N | Y | 0.105 |  |  | 34 | 42 | 48 | 0.038254 | 0.076508 | 0.11476 | 0.19127 | 0.28691 | 0.38254 | 95.2284 | 96.2184 | 96.2572 | 96.5457 | 96.7835 | 96.1938 | 96.5505 | 95.6795 | 96.127 | 96.4072 | 96.3431 | 96.7759 | 96.5316 | 96.5522 | 96.0364 | 95.9735 | 96.4085 | 96.2046 | 96.6989 | 96.6089 | 96.4929 | 2022-08-22 | 2023-05-01
Aptos Solar Technology LLC | MAC-400R {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 382W, 240 Vac Grid Support Utility Interactive Microinverter | 0.38254 | 240 | 96.5 | CSA Group | [3/17/2023] | CSA Group | [08/12/2021] | [V01.01.00] | 2021-09-21 | [08/12/2021] | 2021-09-21 | CSA Group | 2021-08-13 | 2021-09-21 |  | N | Y | 0.105 |  |  | 34 | 42 | 48 | 0.038254 | 0.076508 | 0.11476 | 0.19127 | 0.28691 | 0.38254 | 95.2284 | 96.2184 | 96.2572 | 96.5457 | 96.7835 | 96.1938 | 96.5505 | 95.6795 | 96.127 | 96.4072 | 96.3431 | 96.7759 | 96.5316 | 96.5522 | 96.0364 | 95.9735 | 96.4085 | 96.2046 | 96.6989 | 96.6089 | 96.4929 | 2021-09-21 | 2023-05-01
Aptos Solar Technology LLC | MAC-400 {208V} | N | Y | N | N | N | N | Y* | Y | 382 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.38726 | 208 | 96.5 | CSA Group | [3/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-27 | 2023-11-01 |  | N | Y | 0.09 |  |  | 38 | 42 | 48 | 0.03873 | 0.07745 | 0.11618 | 0.19363 | 0.29045 | 0.38726 | 94.6456 | 96.0225 | 96.3244 | 96.4166 | 96.4735 | 95.9551 | 96.3221 | 94.6265 | 95.7556 | 96.3916 | 96.4249 | 96.447 | 96.0618 | 96.3091 | 94.8633 | 95.8439 | 96.3819 | 96.3279 | 96.5471 | 96.2922 | 96.366 | 2023-11-01
Aptos Solar Technology LLC | MAC-400R {208V} | N | Y | N | N | N | N | Y* | Y | 382 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.38726 | 208 | 96.5 | CSA Group | [3/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-27 | 2023-11-01 |  | N | Y | 0.09 |  |  | 38 | 42 | 48 | 0.03873 | 0.07745 | 0.11618 | 0.19363 | 0.29045 | 0.38726 | 94.6456 | 96.0225 | 96.3244 | 96.4166 | 96.4735 | 95.9551 | 96.3221 | 94.6265 | 95.7556 | 96.3916 | 96.4249 | 96.447 | 96.0618 | 96.3091 | 94.8633 | 95.8439 | 96.3819 | 96.3279 | 96.5471 | 96.2922 | 96.366 | 2023-11-01
Aptos Solar Technology LLC | MAC-800 {208V} | N | Y | N | N | N | N | Y* | Y | 766 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.767 | 208 | 96.5 | CSA Group | [3/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-06-08 | No Information Submitted |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.07671 | 0.15342 | 0.23013 | 0.38355 | 0.57533 | 0.7671 | 94.7583 | 96.0685 | 96.3783 | 96.4713 | 96.5088 | 96.0574 | 96.3707 | 94.8184 | 95.8015 | 96.4279 | 96.4518 | 96.4948 | 96.1343 | 96.358 | 94.3079 | 95.7956 | 96.3964 | 96.4624 | 96.4815 | 96.0999 | 96.327 | 2023-05-01
Aptos Solar Technology LLC | MAC-800 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 766 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.767 | 240 | 96.5 | CSA Group | [3/17/2023] | CSA Group | [06/07/2020] | [V01.01.00] | 2022-08-22 | [06/07/2020] | 2022-08-22 | CSA Group | 2022-06-08 | 2022-08-22 |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.076709 | 0.15342 | 0.23013 | 0.38354 | 0.57532 | 0.76709 | 95.467 | 96.1734 | 96.2274 | 96.4901 | 96.6946 | 96.1498 | 96.4932 | 95.7932 | 96.0559 | 96.3844 | 96.3319 | 96.7007 | 96.4903 | 96.5062 | 95.7028 | 95.9016 | 96.4122 | 96.1946 | 96.7005 | 96.575 | 96.4735 | 2022-08-22 | 2023-05-01
Aptos Solar Technology LLC | MAC-800R {208V} | N | Y | N | N | N | N | Y* | Y | 766 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.767 | 208 | 96.5 | CSA Group | [3/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-13 | No Information Submitted |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.07671 | 0.15342 | 0.23013 | 0.38355 | 0.57533 | 0.7671 | 94.7583 | 96.0685 | 96.3783 | 96.4713 | 96.5088 | 96.0574 | 96.3707 | 94.8184 | 95.8015 | 96.4279 | 96.4518 | 96.4948 | 96.1343 | 96.358 | 94.3079 | 95.7956 | 96.3964 | 96.4624 | 96.4815 | 96.0999 | 96.327 | 2023-05-01
Aptos Solar Technology LLC | MAC-800R {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 766W, 240 Vac Grid Support Utility Interactive Microinverter | 0.767 | 240 | 96.5 | CSA Group | [3/17/2023] | CSA Group | [08/12/2021] | [V01.01.00] | 2021-09-21 | [08/12/2021] | 2021-09-21 | CSA Group | 2021-08-13 | 2021-09-21 |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.076709 | 0.15342 | 0.23013 | 0.38354 | 0.57532 | 0.76709 | 95.467 | 96.1734 | 96.2274 | 96.4901 | 96.6946 | 96.1498 | 96.4932 | 95.7932 | 96.0559 | 96.3844 | 96.3319 | 96.7007 | 96.4903 | 96.5062 | 95.7028 | 95.9016 | 96.4122 | 96.1946 | 96.7005 | 96.575 | 96.4735 | 2021-09-21 | 2023-05-01
Base Power, Inc | MIN 3000TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 3.095 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.095 | 240 | 97 | Intertek | [7/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 1.593 |  |  | 125 | 380 | 480 | 0.30951 | 0.61902 | 0.92853 | 1.5475 | 2.3213 | 3.0951 | 92.5494 | 94.742 | 95.5187 | 96.466 | 96.3778 | 96.1735 | 96.0481 | 94.9531 | 96.9774 | 97.284 | 97.7821 | 97.7609 | 97.4493 | 97.5411 | 93.2489 | 95.9992 | 96.7283 | 97.2156 | 97.3487 | 97.3889 | 97.0169 | 2025-09-22
Base Power, Inc | MIN 3800TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 3.888 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.888 | 240 | 97 | Intertek | [7/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 1.593 |  |  | 160 | 380 | 480 | 0.38882 | 0.77764 | 1.1665 | 1.9441 | 2.9162 | 3.8882 | 92.9226 | 95.0495 | 95.9079 | 96.5875 | 96.7318 | 96.456 | 96.3523 | 95.8681 | 97.43 | 97.8567 | 98.062 | 98.0583 | 97.9727 | 97.9116 | 93.4977 | 96.4887 | 97.1935 | 97.6687 | 97.7381 | 97.6144 | 97.4199 | 2025-09-22
Base Power, Inc | MIN 5000TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 4.943 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 4.943 | 240 | 97.5 | Intertek | [7/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 1.593 |  |  | 210 | 380 | 480 | 0.49432 | 0.98864 | 1.483 | 2.4716 | 3.7074 | 4.9432 | 94.2674 | 96.0279 | 96.6177 | 96.9688 | 96.7976 | 96.4626 | 96.6555 | 95.8274 | 97.6476 | 97.9929 | 98.1977 | 98.0262 | 97.7757 | 97.9388 | 95.1548 | 97.2155 | 97.7005 | 97.9802 | 97.817 | 97.6089 | 97.6903 | 2025-09-22
Base Power, Inc | MIN 6000TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 5.918 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 5.918 | 240 | 97 | Intertek | [7/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 1.593 |  |  | 170 | 380 | 480 | 0.59178 | 1.1836 | 1.7753 | 2.9589 | 4.4383 | 5.9177 | 93.4931 | 95.0713 | 96.0091 | 96.5068 | 96.5375 | 96.277 | 96.2595 | 96.2836 | 97.6235 | 97.995 | 98.0323 | 97.7405 | 97.6407 | 97.7632 | 95.2829 | 97.0935 | 97.4899 | 97.8279 | 97.6998 | 97.4333 | 97.5612 | 2025-09-22
Base Power, Inc | MIN 7600TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 7.524 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 7.524 | 240 | 97.5 | Intertek | [7/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 1.593 |  |  | 212 | 380 | 480 | 0.75242 | 1.5048 | 2.2573 | 3.7621 | 5.6431 | 7.5242 | 94.8321 | 96.2443 | 96.9372 | 97.1359 | 97.0549 | 96.4681 | 96.899 | 96.1031 | 97.82 | 98.0103 | 98.1875 | 98.0302 | 97.4081 | 97.9421 | 95.2191 | 97.2034 | 97.6838 | 97.8749 | 97.7927 | 97.3782 | 97.6437 | 2025-09-22
Base Power, Inc | MIN 8200TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 8.2 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 8.251 | 240 | 97.5 | Intertek | [6/25/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.82514 | 1.6503 | 2.4754 | 4.1257 | 6.1886 | 8.2514 | 93.9258 | 96.1247 | 96.8143 | 97.2666 | 97.2617 | 97.0721 | 97.0092 | 95.5722 | 97.4863 | 97.9916 | 98.2391 | 98.1842 | 98.0166 | 98.0249 | 93.7743 | 96.6734 | 97.4868 | 97.9609 | 97.966 | 97.9229 | 97.673 | 2025-09-22
Base Power, Inc | MIN 9000TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 9 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 9.063 | 240 | 97.5 | Intertek | [6/25/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.90625 | 1.8125 | 2.7188 | 4.5312 | 6.7969 | 9.0625 | 94.2384 | 96.2702 | 96.908 | 97.3235 | 97.2 | 97.0403 | 97.018 | 95.9482 | 97.6026 | 98.0707 | 98.2515 | 98.1428 | 97.9914 | 98.0346 | 94.3716 | 96.8985 | 97.6347 | 98.0229 | 98.0409 | 97.9412 | 97.7795 | 2025-09-22
Base Power, Inc | MIN 10000TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 10.082 | 240 | 97.5 | Intertek | [6/25/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.0082 | 2.0164 | 3.0246 | 5.041 | 7.5615 | 10.082 | 95.1276 | 96.4976 | 97.0675 | 97.3296 | 97.1985 | 96.9229 | 97.0787 | 96.3253 | 97.7618 | 98.1384 | 98.2919 | 98.1462 | 97.9316 | 98.0731 | 95.0134 | 97.1984 | 97.7803 | 98.0517 | 98.0092 | 97.8719 | 97.8234 | 2025-09-22
Base Power, Inc | MIN 11400TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 11.52 | 240 | 98 | Intertek | [6/25/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.152 | 2.304 | 3.456 | 5.76 | 8.64 | 11.52 | 95.3626 | 96.9572 | 97.4775 | 97.685 | 97.5433 | 97.3539 | 97.4392 | 96.5819 | 98.0275 | 98.3999 | 98.5274 | 98.4351 | 98.2539 | 98.3467 | 95.457 | 97.1914 | 97.7448 | 97.9708 | 97.8318 | 97.6582 | 97.7149 | 2025-09-22
Canadian Solar Inc. | CSI-25KTL-GS-FL {480V} | N | N | Y | Y | Y | N | N | N | 25 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter | 25 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [01/31/2018] | [1D] | 2018-11-01 | [01/31/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 14 |  |  | 580 | 650 | 780 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 97.1 | 97.4 | 97.6 | 97.9 | 98 | 97.8 | 97.9 | 97.1 | 97.3 | 97.6 | 97.8 | 98.3 | 97.6 | 98 | 97.2 | 97.4 | 97.7 | 97.8 | 98 | 97.5 | 97.9 | 2018-02-15 | 2019-11-15
Canadian Solar Inc. | CSI-30KTL-GS-FL {480V} | N | N | Y | Y | Y | N | N | N | 30 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter | 30 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [01/31/2018] | [1D] | 2018-11-01 | [01/31/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 580 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.1 | 97.9 | 97.9 | 98.3 | 97.5 | 97.9 | 97.8 | 97.4 | 98.1 | 98.1 | 98.4 | 98.1 | 97.9 | 98.1 | 97.1 | 97.9 | 98 | 98.3 | 98 | 97.8 | 98 | 2018-02-15 | 2019-11-15
Canadian Solar Inc. | CSI-36KTL-CT {480V} | N | N | Y | Y | N | N | N | N | 36 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000 Vdc | 36 | 480 | 98 | No Information Submitted | No Information Submitted | CSA Group | [8/2/2017] | [V0.60] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 0 |  |  | 540 | 730 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 98.4 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2 | 98.3 | 2017-10-01 | 2018-11-01
Canadian Solar Inc. | CSI-36KTL-GS-FL {480V} | N | N | Y | Y | Y | N | N | N | 36 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter | 36 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [01/31/2018] | [1D] | 2018-11-01 | [01/31/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 580 | 650 | 780 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3 | 98.2 | 98.1 | 98.4 | 97.6 | 98.1 | 97.9 | 97.7 | 98.3 | 98.3 | 98.4 | 98.3 | 98.1 | 98.3 | 97.4 | 98.1 | 98.2 | 98.3 | 98.2 | 98.1 | 98.2 | 2018-02-15 | 2019-11-15
Canadian Solar Inc. | CSI-40KTL-GS {480V} | N | N | Y | Y | Y | N | N | N | 40 kW, 480 Vac, 3-phase Utility Interactive Inverter, with external fan | 40 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/31/2018] | [1D] | 2018-11-01 | [01/31/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 97.7 | 98.1 | 97.8 | 98.3 | 98.4 | 98.6 | 98.5 | 98.3 | 98.5 | 97.6 | 98.1 | 98.2 | 98.4 | 98.3 | 98 | 98.3 | 2018-02-15 | 2019-11-15
Canadian Solar Inc. | CSI-40KTL-GS-FL {480V} | N | N | Y | Y | Y | N | N | N | 40 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter | 40 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/31/2018] | [1D] | 2018-11-01 | [01/31/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 98 | 98.1 | 97.9 | 98.3 | 98.4 | 98.7 | 98.6 | 98.3 | 98.5 | 97.6 | 98.2 | 98.2 | 98.4 | 98.3 | 98.2 | 98.3 | 2018-02-15 | 2019-11-15
Canadian Solar Inc. | CSI-50KTL-CT {480V} | N | N | Y | Y | N | N | N | N | 50 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc | 50 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [7/6/2017] | [V5.00] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 0.88 |  |  | 480 | 730 | 850 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6089 | 96.843 | 97.4816 | 97.8549 | 97.8327 | 97.6904 | 97.6497 | 98.0184 | 98.6275 | 98.7749 | 98.8023 | 98.7196 | 98.6108 | 98.7055 | 97.7339 | 98.4586 | 98.6223 | 98.6594 | 98.5869 | 98.4698 | 98.56 | 2017-10-01 | 2018-11-01
Canadian Solar Inc. | CSI-50KTL-GS {480V} | N | N | Y | Y | Y | N | N | N | 50 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 50 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/08/2018] | [19/01] | 2018-11-01 | [01/08/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.7 | 98.4 | 98.5 | 98.6 | 98.5 | 98.4 | 98.4 | 97.8 | 98.5 | 98.6 | 98.7 | 98.5 | 98.4 | 98.5 | 97.9 | 98.6 | 98.7 | 98.8 | 98.6 | 98.5 | 98.6 | 2018-02-01 | 2019-11-15
Canadian Solar Inc. | CSI-50KTL-GS-FL {480V} | N | N | Y | Y | Y | N | N | N | 50 kW, 480 Vac, Fanless, 3-phase Grid Support Utility Interactive Inverter, | 50 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/08/2018] | [19/01] | 2018-11-01 | [01/08/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5 | 98.5 | 98.4 | 98.6 | 98.3 | 98.5 | 98.4 | 97.8 | 98.6 | 98.5 | 98.7 | 98.4 | 98.5 | 98.5 | 98 | 98.7 | 98.8 | 98.8 | 98.6 | 98.5 | 98.6 | 2018-02-01 | 2019-11-15
Canadian Solar Inc. | CSI-60KTL-CT {480V} | N | N | Y | Y | N | N | N | N | 60 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc | 60 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [7/6/2017] | [V5.00] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 0.88 |  |  | 540 | 730 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5104 | 97.4761 | 97.8852 | 98.0525 | 97.9434 | 97.7271 | 97.8678 | 98.2227 | 98.7116 | 98.7911 | 98.779 | 98.6548 | 98.4981 | 98.6749 | 98.0008 | 98.5506 | 98.6633 | 98.6588 | 98.5228 | 98.3541 | 98.5403 | 2017-10-01 | 2018-11-01
Canadian Solar Inc. | CSI-60KTL-GS {480V} | N | N | Y | Y | Y | N | N | N | 60 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 60 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/08/2018] | [19/01] | 2018-11-01 | [01/08/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 720 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7 | 98.3 | 98.4 | 98.6 | 98.4 | 98.2 | 98.4 | 97.8 | 98.5 | 98.5 | 98.6 | 98.5 | 98.3 | 98.5 | 97.9 | 98.5 | 98.6 | 98.7 | 98.6 | 98.5 | 98.6 | 2018-02-01 | 2019-11-15
Canadian Solar Inc. | CSI-66KTL-GS {480V} | N | N | Y | Y | Y | N | N | N | 66 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. | 66 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/08/2018] | [19/01] | 2018-11-01 | [01/08/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 720 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.6 | 98.4 | 98.5 | 98.6 | 98.4 | 98.3 | 98.4 | 97.7 | 98.5 | 98.6 | 98.7 | 98.5 | 98.4 | 98.5 | 97.8 | 98.7 | 98.7 | 98.8 | 98.6 | 98.5 | 98.6 | 2018-02-01 | 2019-11-15
CE+T America Inc. | 30C {480V} | Y | N | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac Grid Support Utility Interactive Battery Charge controller | 29.99 | 480 | 95 | No Information Submitted | No Information Submitted | UL | [10/31/2018];[10/31/2018];[10/31/2018];[10/31/2018];[03/22/2019] | [3.2.42];[3.2.60];[3.2.90];[3.2.91];[3.2.106] | 2018-10-15 | [03/22/2019] | 2022-01-03 | Intertek | 2021-10-27 | 2022-01-03 | Formerly Ideal Power Inc. 30C {480V}, or CE+T Energy Solution Inc. 30C {480V}. | N | N | 56.8 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.7 | 94.3 | 94.8 | 95.2 | 95.1 | 94.8 | 94.9 | 92.2 | 94.2 | 94.6 | 95.3 | 95.4 | 95.5 | 95.1 | 89.6 | 92.8 | 93.3 | 94.8 | 95.2 | 95.4 | 94.6 | 2018-02-01 | 2022-01-03
CE+T America Inc. | 30C3 {480V} | Y | N | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac Grid Support Utility Interactive Battery Charge controller with additional Photovoltaic input | 29.99 | 480 | 95 | No Information Submitted | No Information Submitted | UL | [10/31/2018];[10/31/2018];[10/31/2018];[10/31/2018];[03/22/2019] | [3.2.42];[3.2.60];[3.2.90];[3.2.91];[3.2.106] | 2018-10-15 | [03/22/2019] | 2022-01-03 | Intertek | 2021-10-27 | 2022-01-03 | Formerly Ideal Power Inc. 30C3 {480V}, or CE+T Energy Solution Inc. 30C3 {480V}. | N | N | 56.8 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.7 | 94.3 | 94.8 | 95.2 | 95.1 | 94.8 | 94.9 | 92.2 | 94.2 | 94.6 | 95.3 | 95.4 | 95.5 | 95.1 | 89.6 | 92.8 | 93.3 | 94.8 | 95.2 | 95.4 | 94.6 | 2018-02-01 | 2022-01-03
CESC New Energy Technology Co., Ltd. | Mars 9600 HVSP {240V} | Y | N | Y | Y | Y | Y | Y* |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.592 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [6/19/2024] | [1.11] | 2025-11-03 | [6/19/2024] | 2025-11-03 | Intertek | 2024-07-08 |  |  | N | N | 0.65 |  |  | 235 | 360 | 480 | 0.9592 | 1.9184 | 2.8776 | 4.796 | 7.194 | 9.592 | 90.0006 | 93.7166 | 95.2164 | 96.0942 | 97.1032 | 97.8688 | 96.2497 | 91.9548 | 95.489 | 96.5298 | 97.3018 | 97.623 | 97.9692 | 97.1082 | 91.4432 | 94.7028 | 95.6808 | 96.6654 | 97.5238 | 97.776 | 96.7507 | 2025-10-28
Cherry Solution Co., Ltd. | CMI-600S-SA {240V} | N | Y | N | N | N | N | N | Y | 604 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.604 | 240 | 96.5 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.7 |  |  | 35 | 42 | 50 | 0.06 | 0.121 | 0.181 | 0.302 | 0.453 | 0.604 | 96.8 | 96.07 | 95.62 | 96.9 | 97.98 | 95.98 | 97.23 | 95.95 | 96.01 | 95.54 | 96.33 | 97.4 | 96.06 | 96.76 | 95.07 | 96.11 | 95.91 | 95.78 | 96.16 | 95.71 | 95.98 | 2024-08-01
Cherry Solution Co., Ltd. | CMI-600S-WA {240V} | N | Y | N | N | N | N | N | Y | 604 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.604 | 240 | 96.5 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.7 |  |  | 35 | 42 | 50 | 0.06 | 0.121 | 0.181 | 0.302 | 0.453 | 0.604 | 96.8 | 96.07 | 95.62 | 96.9 | 97.98 | 95.98 | 97.23 | 95.95 | 96.01 | 95.54 | 96.33 | 97.4 | 96.06 | 96.76 | 95.07 | 96.11 | 95.91 | 95.78 | 96.16 | 95.71 | 95.98 | 2024-08-01
Cherry Solution Co., Ltd. | CMI-600S-SA {208V} | N | Y | N | N | N | N | N | Y | 608 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.608 | 208 | 96.5 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.2 |  |  | 35 | 42 | 50 | 0.061 | 0.122 | 0.183 | 0.304 | 0.456 | 0.608 | 94.8 | 95.91 | 95.87 | 96.9 | 96.69 | 96.57 | 96.51 | 96.36 | 96.48 | 95.77 | 95.91 | 96.48 | 96.7 | 96.28 | 96.68 | 95.53 | 96.41 | 96.89 | 96.3 | 96.15 | 96.41 | 2024-08-01
Cherry Solution Co., Ltd. | CMI-600S-WA {208V} | N | Y | N | N | N | N | N | Y | 608 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.608 | 208 | 96.5 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.2 |  |  | 35 | 42 | 50 | 0.061 | 0.122 | 0.183 | 0.304 | 0.456 | 0.608 | 94.8 | 95.91 | 95.87 | 96.9 | 96.69 | 96.57 | 96.51 | 96.36 | 96.48 | 95.77 | 95.91 | 96.48 | 96.7 | 96.28 | 96.68 | 95.53 | 96.41 | 96.89 | 96.3 | 96.15 | 96.41 | 2024-08-01
Cherry Solution Co., Ltd. | CMI-800S-SA {208V} | N | Y | N | N | N | N | N | Y | 800 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.8 | 208 | 96 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.23 |  |  | 35 | 42 | 50 | 0.08 | 0.16 | 0.24 | 0.4 | 0.6 | 0.8 | 95.35 | 96.03 | 95.77 | 96.9 | 95.96 | 95.54 | 96.09 | 96.12 | 95.49 | 95.53 | 95.62 | 96.08 | 95.85 | 95.88 | 94.46 | 95.18 | 95.82 | 95.98 | 96.4 | 96.07 | 96.09 | 2024-08-01
Cherry Solution Co., Ltd. | CMI-800S-SA {240V} | N | Y | N | N | N | N | N | Y | 800 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.8 | 240 | 96.5 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.23 |  |  | 35 | 42 | 50 | 0.08 | 0.16 | 0.24 | 0.4 | 0.6 | 0.8 | 96.37 | 97.08 | 96.2 | 96.9 | 96.04 | 93.75 | 96.19 | 95.91 | 96.65 | 97.06 | 98.06 | 96.36 | 94.08 | 96.69 | 95.47 | 95.57 | 97.11 | 97.26 | 97.07 | 95.63 | 96.9 | 2024-08-01
Cherry Solution Co., Ltd. | CMI-800S-WA {208V} | N | Y | N | N | N | N | N | Y | 800 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.8 | 208 | 96 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.23 |  |  | 35 | 42 | 50 | 0.08 | 0.16 | 0.24 | 0.4 | 0.6 | 0.8 | 95.35 | 96.03 | 95.77 | 96.9 | 95.96 | 95.54 | 96.09 | 96.12 | 95.49 | 95.53 | 95.62 | 96.08 | 95.85 | 95.88 | 94.46 | 95.18 | 95.82 | 95.98 | 96.4 | 96.07 | 96.09 | 2024-08-01
Cherry Solution Co., Ltd. | CMI-800S-WA {240V} | N | Y | N | N | N | N | N | Y | 800 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.8 | 240 | 96.5 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.23 |  |  | 35 | 42 | 50 | 0.08 | 0.16 | 0.24 | 0.4 | 0.6 | 0.8 | 96.37 | 97.08 | 96.2 | 96.9 | 96.04 | 93.75 | 96.19 | 95.91 | 96.65 | 97.06 | 98.06 | 96.36 | 94.08 | 96.69 | 95.47 | 95.57 | 97.11 | 97.26 | 97.07 | 95.63 | 96.9 | 2024-08-01
Cherry Solution Co., Ltd. | CMI-1000S-SA {208V} | N | Y | N | N | N | N | N | Y | 994 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.994 | 208 | 96.5 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.11 |  |  | 35 | 42 | 50 | 0.099 | 0.199 | 0.298 | 0.497 | 0.745 | 0.994 | 94.84 | 95.16 | 96.36 | 96.9 | 96.23 | 96.33 | 96.28 | 95.41 | 96.39 | 96.61 | 96.91 | 97.2 | 95.62 | 96.88 | 95.87 | 95.1 | 96.51 | 96.66 | 96.56 | 97.13 | 96.5 | 2024-08-01
Cherry Solution Co., Ltd. | CMI-1000S-WA {208V} | N | Y | N | N | N | N | N | Y | 994 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.994 | 208 | 96.5 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.11 |  |  | 35 | 42 | 50 | 0.099 | 0.199 | 0.298 | 0.497 | 0.745 | 0.994 | 94.84 | 95.16 | 96.36 | 96.9 | 96.23 | 96.33 | 96.28 | 95.41 | 96.39 | 96.61 | 96.91 | 97.2 | 95.62 | 96.88 | 95.87 | 95.1 | 96.51 | 96.66 | 96.56 | 97.13 | 96.5 | 2024-08-01
Cherry Solution Co., Ltd. | CMI-1000S-SA {240V} | N | Y | N | N | N | N | N | Y | 1062 W, 240 Vac Grid Support Utility Interactive Microinverter | 1.062 | 240 | 96.5 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.13 |  |  | 35 | 42 | 50 | 0.106 | 0.212 | 0.319 | 0.531 | 0.797 | 1.062 | 96.2 | 96.43 | 96.23 | 95.91 | 96.91 | 96.23 | 96.53 | 95.78 | 96.63 | 96.63 | 96.31 | 96.59 | 96.21 | 96.48 | 95.09 | 96.59 | 96.64 | 96.09 | 97.25 | 96.23 | 96.76 | 2024-08-01
Cherry Solution Co., Ltd. | CMI-1000S-WA {240V} | N | Y | N | N | N | N | N | Y | 1062 W, 240 Vac Grid Support Utility Interactive Microinverter | 1.062 | 240 | 96.5 | CSA Group | [2/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | Y | 0.13 |  |  | 35 | 42 | 50 | 0.106 | 0.212 | 0.319 | 0.531 | 0.797 | 1.062 | 96.2 | 96.43 | 96.23 | 95.91 | 96.91 | 96.23 | 96.53 | 95.78 | 96.63 | 96.63 | 96.31 | 96.59 | 96.21 | 96.48 | 95.09 | 96.59 | 96.64 | 96.09 | 97.25 | 96.23 | 96.76 | 2024-08-01
Chilicon Power, LLC | CP-250E-60/72-208/240-MC4 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 277 W, 208 Vac Grid Support Utility Interactive Inverter | 0.277 | 208 | 95.5 | No Information Submitted | No Information Submitted | Intertek | [01/08/2020] | [3542] | 2018-10-15 | [02/19/2019] | 2020-02-11 | Intertek | 2020-01-07 | 2020-02-11 |  | N | Y | 0.02 |  |  | 28 | 30 | 32 | 0.03 | 0.06 | 0.08 | 0.14 | 0.21 | 0.28 | 92 | 95.1 | 95.9 | 96 | 95.6 | 94.9 | 95.5 | 91.2 | 94.8 | 95.7 | 96 | 95.6 | 95.1 | 95.5 | 90.6 | 94.5 | 95.6 | 96 | 95.7 | 95.2 | 95.4 | 2017-12-15 | 2020-02-11
Chilicon Power, LLC | CP-250E-60/72-208/240-MC4 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 289 W, 240 Vac Grid Support Utility Interactive Inverter | 0.289 | 240 | 96 | No Information Submitted | No Information Submitted | Intertek | [01/08/2020] | [3542] | 2018-10-15 | [02/19/2019] | 2020-02-11 | Intertek | 2020-01-07 | 2020-02-11 |  | N | Y | 0.06 |  |  | 28 | 30 | 32 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.3 | 95.4 | 96.1 | 96.2 | 95.9 | 95.2 | 95.8 | 91.6 | 95.2 | 96 | 96.3 | 96 | 95.4 | 95.8 | 91 | 95.1 | 95.9 | 96.3 | 96.1 | 95.6 | 95.8 | 2017-12-15 | 2020-02-11
Chilicon Power, LLC | CP-720-60/72/96-208/240-MC4 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 720 W, 240 Vac, Grid Support Utility Interactive Twin Microinverter (2 PV modules per inverter) | 0.721 | 240 | 96 | No Information Submitted | No Information Submitted | Intertek | [01/13/2020] | [3541] | 2019-02-01 | [02/15/2019] | 2020-02-11 | Intertek | 2020-01-07 | 2020-02-11 |  | N | Y | 0.1 |  |  | 60 | 65 | 70 | 0.072122 | 0.14424 | 0.21637 | 0.36061 | 0.54091 | 0.72122 | 93.1325 | 95.8508 | 96.485 | 96.6636 | 96.3127 | 95.4342 | 96.2128 | 92.5062 | 95.5354 | 96.3479 | 96.6951 | 96.2594 | 95.3978 | 96.1321 | 91.7173 | 95.2191 | 96.1457 | 96.6114 | 96.0277 | 95.1854 | 95.9094 | 2019-02-01 | 2020-02-11
Chilicon Power, LLC | CP-720-60/72/96-208/240-MC4 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 720 W, 208 Vac, Grid Support Utility Interactive Twin Microinverter (2 PV modules per inverter) | 0.725 | 208 | 95.5 | No Information Submitted | No Information Submitted | Intertek | [01/13/2020] | [3541] | 2019-02-01 | [02/15/2019] | 2020-02-11 | Intertek | 2020-01-07 | 2020-02-11 |  | N | Y | 0.1 |  |  | 60 | 65 | 70 | 0.072543 | 0.14509 | 0.21763 | 0.36272 | 0.54407 | 0.72543 | 93.0721 | 95.576 | 96.2371 | 96.3244 | 95.6753 | 94.8437 | 95.7284 | 93.0023 | 95.3597 | 96.086 | 96.3359 | 95.7304 | 94.9137 | 95.7317 | 92.3998 | 94.8703 | 95.8744 | 96.2342 | 95.6885 | 94.6211 | 95.5996 | 2019-02-01 | 2020-02-11
Chint Power Systems America | CPS ECH7.6KTL/US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 208Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 7.57 | 208 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 50 |  |  | 200 | 370 | 480 | 0.757 | 1.514 | 2.271 | 3.785 | 5.678 | 7.57 | 94.56 | 94.85 | 96.24 | 96.53 | 96.92 | 96.17 | 96.52 | 92.85 | 95.08 | 95.82 | 96.68 | 96.91 | 96.86 | 96.48 | 93.76 | 94.98 | 96.55 | 96.49 | 96.81 | 96.51 | 96.48 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH7.6KTL/US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 7.57 | 240 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 60 |  |  | 200 | 370 | 480 | 0.757 | 1.514 | 2.271 | 3.785 | 5.678 | 7.57 | 93.67 | 94.44 | 96.1 | 96.58 | 96.58 | 96.81 | 96.31 | 93.37 | 94.93 | 95.94 | 95.94 | 96.8 | 96.8 | 96.28 | 93.76 | 94.98 | 96.55 | 96.49 | 96.81 | 96.51 | 96.48 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH9.6KTL/US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 208Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 9.54 | 240 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 50 |  |  | 200 | 370 | 480 | 0.954 | 1.908 | 2.862 | 4.77 | 7.155 | 9.54 | 93.67 | 95.3 | 96.29 | 96.41 | 96.85 | 96.66 | 96.48 | 93.34 | 95.58 | 96.24 | 96.71 | 96.82 | 96.74 | 96.52 | 92.37 | 95.32 | 96.76 | 96.57 | 96.78 | 96.43 | 96.46 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH9.6KTL/US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 9.55 | 208 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 60 |  |  | 200 | 370 | 480 | 0.955 | 1.91 | 2.865 | 4.775 | 7.163 | 9.55 | 93.14 | 95.32 | 96.26 | 96.52 | 96.97 | 96.69 | 96.54 | 93.15 | 95.37 | 96.33 | 96.71 | 96.8 | 96.81 | 96.51 | 92.61 | 95.52 | 96.23 | 96.73 | 96.82 | 96.68 | 96.49 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH11.4KTL/US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 11.35 | 208 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 80 |  |  | 200 | 370 | 480 | 1.135 | 2.27 | 3.405 | 5.675 | 8.513 | 11.35 | 93.09 | 95.58 | 96.61 | 96.68 | 96.67 | 96.62 | 96.47 | 93.52 | 95.77 | 96.55 | 96.75 | 96.78 | 96.71 | 96.56 | 92.98 | 95.7 | 96.48 | 96.74 | 96.74 | 96.62 | 96.5 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH11.4KTL/US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 11.36 | 240 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 30 |  |  | 200 | 370 | 480 | 1.136 | 2.272 | 3.408 | 5.68 | 8.52 | 11.36 | 93.84 | 95.64 | 96.4 | 96.47 | 96.77 | 96.49 | 96.48 | 93.84 | 95.83 | 96.45 | 96.76 | 96.77 | 96.64 | 96.56 | 93.44 | 95.75 | 96.44 | 96.69 | 96.67 | 96.45 | 96.46 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH12KTL/US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12 kW, 208Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 11.99 | 240 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 60 |  |  | 200 | 370 | 480 | 1.199 | 2.398 | 3.597 | 5.995 | 8.993 | 11.99 | 93.6 | 95.71 | 96.47 | 96.56 | 96.65 | 96.59 | 96.44 | 93.91 | 95.96 | 96.56 | 96.86 | 96.73 | 96.56 | 96.58 | 93.45 | 95.87 | 96.45 | 96.67 | 96.61 | 96.65 | 96.44 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH12KTL/US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12 kW, 240Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 12 | 208 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 80 |  |  | 200 | 370 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.26 | 95.84 | 96.34 | 96.57 | 96.65 | 96.51 | 96.45 | 94.27 | 95.87 | 96.58 | 96.86 | 96.86 | 96.73 | 96.67 | 93.7 | 95.9 | 96.43 | 96.75 | 96.81 | 96.61 | 96.57 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS SCA20KTL-DO-R/US-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 20 kVA, 1000 Vdc, 480 Vac, 3-phase, non-isolated Grid Support Utility Interactive Inverter | 20 | 480 | 98 | Intertek | [5/16/2022] | Intertek | [11/28/2019] | [00.02.00] | 2020-01-13 | [11/28/2019] | 2020-08-03 | Intertek | 2020-03-19 | 2020-08-03 |  | N | N | 3 |  |  | 560 | 735 | 850 | 2.0112 | 4.0224 | 6.0336 | 10.056 | 15.0839 | 20.1119 | 96.9815 | 97.6652 | 97.8012 | 97.8313 | 97.6023 | 97.256 | 97.6353 | 97.9016 | 98.3305 | 98.4819 | 98.4139 | 98.2956 | 98.149 | 98.3215 | 97.5397 | 98.2151 | 98.3121 | 98.2684 | 98.1987 | 97.9889 | 98.1909 | 2020-01-13 | 2022-06-13
Chint Power Systems America | CPS SCA25KTL-DO/US-208 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 25 kVA, 1000 Vdc, 208 Vac, 3-phase, non-isolated Grid Support Utility Interactive Inverter | 25 | 208 | 96.5 | CSA Group | [9/28/2022] | CSA Group | [9/28/2022] | [V01.04.00] | 2020-10-12 | [9/28/2022] | 2020-10-12 | Intertek | 2020-08-28 | 2020-10-12 |  | N | N | 2.9 |  |  | 480 | 575 | 850 | 2.5432 | 5.0864 | 7.6296 | 12.716 | 19.074 | 25.432 | 95.687 | 96.8055 | 97.0311 | 97.0424 | 96.7769 | 96.4735 | 96.8058 | 95.3071 | 96.2843 | 96.7871 | 96.7814 | 96.4829 | 96.1186 | 96.5069 | 93.5943 | 95.6171 | 96.1229 | 96.3357 | 96.1514 | 95.85 | 96.0426 | 2020-10-12 | 2023-02-01
Chint Power Systems America | CPS SCA25KTL-DO-R/US-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 25 kVA, 1000 Vdc, 480 Vac, 3 phase, non-isolated Grid Support Utility Interactive Inverter | 25 | 480 | 98 | Intertek | [5/16/2022] | Intertek | [11/28/2019] | [00.02.00] | 2020-01-13 | [11/28/2019] | 2020-08-03 | Intertek | 2020-03-19 | 2020-08-03 |  | N | N | 3 |  |  | 560 | 735 | 850 | 2.5259 | 5.0517 | 7.5776 | 12.6294 | 18.944 | 25.2587 | 96.9119 | 97.6982 | 97.8295 | 97.8399 | 97.5971 | 97.2868 | 97.6381 | 97.8973 | 98.3256 | 98.4773 | 98.4082 | 98.2817 | 98.0946 | 98.3092 | 97.5003 | 98.1562 | 98.3137 | 98.2793 | 98.1854 | 97.9963 | 98.1822 | 2020-01-13 | 2022-06-13
Chint Power Systems America | CPS SCA36KTL-DO/US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 36 kVA, 480 Vac, 1000 Vdc, 3-phase, non-isolated Grid Support Utility Interactive Inverter | 36 | 480 | 98 | No Information Submitted | No Information Submitted | CSA Group | [12/10/2020] | [V0.90] | 2018-10-15 | [12/10/2020] | 2021-01-21 | CSA Group | 2020-12-07 | 2021-01-21 |  | Y | N | 0 |  |  | 540 | 730 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 98.4 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2 | 98.3 | 2017-09-01 | 2021-01-21
Chint Power Systems America | CPS SCA36KTL-DO/US-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 36 kVA, 1000 Vdc, 480 Vac, 3-phase, non-isolated Grid Support Utility Interactive Inverter | 36 | 480 | 97.5 | CSA Group | [9/28/2022] | CSA Group | [9/28/2022] | [V01.18.00] | 2023-02-01 | [9/28/2022] | 2023-02-01 | Intertek | 2022-10-26 | 2023-02-01 |  | N | N | 2.9 |  |  | 400 | 625 | 850 | 3.6292 | 7.2583 | 10.8875 | 18.1458 | 27.2188 | 36.2917 | 93.7839 | 95.508 | 96.459 | 96.7736 | 97.1214 | 96.9894 | 96.7481 | 94.9739 | 96.4987 | 96.7245 | 97.8252 | 97.8261 | 97.7151 | 97.5077 | 95.5762 | 97.0793 | 97.3029 | 97.8896 | 98.181 | 98.0773 | 97.85 | 2023-02-01 | 2023-02-21
Chint Power Systems America | CPS SCA50KTL-DO/US-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 50 kVA , 1000 Vdc, 480 Vac, 3-phase, non-isolated Grid Support Utility Interactive Inverter | 50 | 480 | 98.5 | CSA Group | [9/28/2022] | CSA Group | [9/28/2022] | [V01.12.00] | 2018-10-15 | [9/28/2022] | 2020-08-03 | Intertek | 2020-03-19 | 2020-08-03 |  | N | N | 0.88 |  |  | 480 | 730 | 850 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6 | 96.8 | 97.5 | 97.9 | 97.8 | 97.7 | 97.6 | 98 | 98.6 | 98.8 | 98.8 | 98.7 | 98.6 | 98.7 | 97.7 | 98.5 | 98.6 | 98.7 | 98.6 | 98.5 | 98.6 | 2017-08-01 | 2023-02-01
Chint Power Systems America | SCA50K-T-US-208 {208V} | N | Y | Y | Y | Y | Y | Y* |  | 50 kVA, 208 Vac, Grid Support Utility Interactive Inverter, 1000 Vdc, 3 Phase Non-isolated | 50 | 208 | 96.5 | CSA Group | [9/2/2025] | CSA Group | [9/2/2025] | [01.01.00] | 2025-10-13 | [9/2/2025] | 2025-10-13 | CSA Group | 2025-08-26 |  |  | N | N | 20 |  |  | 200 | 380 | 700 | 5.0118 | 10.0236 | 15.0354 | 25.059 | 37.5885 | 50.118 | 95.7529 | 96.5043 | 96.6671 | 96.5557 | 96.2057 | 95.5743 | 96.2998 | 96.7071 | 97.3014 | 97.3414 | 97.2243 | 96.7529 | 96.3486 | 96.9279 | 95.4614 | 96.3829 | 96.7971 | 96.7471 | 96.27 | 95.8986 | 96.3882 | 2025-10-13 | 2026-04-21
Chint Power Systems America | CPS SCA60KTL-DO/US-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 60 kVA , 1000 Vdc, 480 Vac, 3-phase, non-isolated Grid Support Utility Interactive Inverter | 60 | 480 | 98.5 | CSA Group | [9/28/2022] | CSA Group | [9/28/2022] | [V01.12.00] | 2018-10-15 | [9/28/2022] | 2020-08-03 | Intertek | 2020-03-19 | 2020-08-03 |  | N | N | 0.88 |  |  | 540 | 730 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5 | 97.5 | 97.9 | 98.1 | 97.9 | 97.7 | 97.9 | 98.2 | 98.7 | 98.8 | 98.8 | 98.7 | 98.5 | 98.7 | 98 | 98.6 | 98.7 | 98.7 | 98.5 | 98.4 | 98.5 | 2017-08-01 | 2023-02-01
Chint Power Systems America | CPS SCH100KTL-AIO/US-600 {600V} | N | Y | Y | Y | Y | Y | Y* | Y | 100 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter | 100 | 600 | 98.5 | CSA Group | [2/28/2022] | CSA Group | [09/26/2019] | [V4.00] | 2019-11-01 | [09/26/2019] | 2020-08-03 | Intertek | 2020-03-19 | 2020-08-03 |  | N | N | 0.33 |  |  | 870 | 1000 | 1300 | 10.056 | 20.112 | 30.168 | 50.28 | 75.42 | 100.56 | 98.51 | 99 | 99.01 | 99.09 | 98.94 | 98.78 | 98.96 | 98.03 | 98.44 | 98.61 | 98.6 | 98.48 | 98.29 | 98.49 | 97.25 | 97.82 | 98.17 | 98.19 | 98.14 | 97.93 | 98.09 | 2019-11-01 | 2022-06-13
Chint Power Systems America | CPS SCH100KTL-DO/US-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 100 kVA , 1500 Vdc, 480 Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter | 100 | 480 | 98 | CSA Group | [2/28/2022] | CSA Group | [06/01/2021] | [V1.09.00] | 2021-10-01 | [06/01/2021] | 2021-10-01 | CSA Group | 2021-08-11 | 2021-10-01 |  | N | N | 1.6 |  |  | 760 | 1000 | 1300 | 10.0204 | 20.0407 | 30.0611 | 50.1018 | 75.1528 | 100.2037 | 98.5414 | 98.92 | 98.8914 | 98.7529 | 98.4471 | 98.1229 | 98.5759 | 98.0314 | 98.5014 | 98.5529 | 98.4186 | 98.13 | 97.7786 | 98.2384 | 97.2429 | 97.88 | 98.0871 | 98.0186 | 97.7443 | 97.3586 | 97.8105 | 2021-10-01 | 2022-06-13
Chint Power Systems America | CPS SCH100KTL-DO/US-600 {600V} | N | Y | Y | Y | Y | Y | Y* | Y | 100 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter | 100 | 600 | 98.5 | CSA Group | [2/28/2022] | CSA Group | [06/08/2018];[06/17/2020] | [V2.00];[V4.00] | 2018-10-15 | [06/08/2018];[06/17/2020] | 2020-08-03 | Intertek | 2020-03-19 | 2020-08-03 |  | N | N | 4.5 |  |  | 870 | 1000 | 1300 | 10 | 20 | 30 | 50 | 75 | 100 | 98.5519 | 98.9972 | 99.062 | 99.0008 | 98.8738 | 98.7452 | 98.9099 | 97.9026 | 98.4849 | 98.5322 | 98.5674 | 98.447 | 98.2811 | 98.4543 | 97.098 | 97.901 | 98.071 | 98.1053 | 98.08 | 97.9054 | 98.0273 | 2018-08-01 | 2022-06-13
Chint Power Systems America | SCA100K-T-US-480 {480V} | N | Y | Y | Y | Y | Y | Y* |  | 100 kVA, 480 Vac, Grid Support Utility Interactive Inverter, 1000 Vdc, 3 Phase Non-isolate | 100 | 480 | 98 | CSA Group | [9/2/2025] | CSA Group | [9/2/2025] | [01.01.00] | 2025-10-13 | [9/2/2025] | 2025-10-13 | CSA Group | 2025-08-26 |  |  | N | N | 21.54 |  |  | 340 | 720 | 850 | 10.016 | 20.032 | 30.048 | 50.08 | 75.12 | 100.16 | 95.6943 | 97.0214 | 97.21 | 97.3843 | 97.3214 | 97.1057 | 97.2304 | 97.44 | 98.45 | 98.5686 | 98.5829 | 98.4557 | 98.2943 | 98.447 | 97.1571 | 98.18 | 98.3943 | 98.4271 | 98.3143 | 98.1843 | 98.2881 | 2025-10-13
Chint Power Systems America | CPS SCH125KTL-AIO/US-600 {600V} | N | Y | Y | Y | Y | Y | Y* | Y | 125 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter | 125 | 600 | 98.5 | CSA Group | [2/28/2022] | CSA Group | [09/26/2019] | [V4.00] | 2019-11-01 | [09/26/2019] | 2020-08-03 | Intertek | 2020-03-19 | 2020-08-03 |  | N | N | 0.33 |  |  | 870 | 1000 | 1300 | 12.555 | 25.109 | 37.664 | 62.773 | 94.16 | 125.546 | 98.79 | 99.03 | 99.05 | 99.01 | 98.81 | 98.58 | 98.88 | 98.2 | 98.51 | 98.6 | 98.54 | 98.33 | 98.01 | 98.39 | 97.56 | 98.01 | 98.15 | 98.17 | 97.96 | 97.63 | 98 | 2019-11-01 | 2022-06-13
Chint Power Systems America | CPS SCH125KTL-DO/US-600 {600V} | N | Y | Y | Y | Y | Y | Y* | Y | 125 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter | 125 | 600 | 98.5 | CSA Group | [2/28/2022] | CSA Group | [06/08/2018];[06/17/2020] | [V2.00];[V4.00] | 2018-10-15 | [06/08/2018];[06/17/2020] | 2020-08-03 | Intertek | 2020-03-19 | 2020-08-03 |  | N | N | 4.9 |  |  | 870 | 1000 | 1300 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 98.7077 | 99.0329 | 99.0691 | 98.9523 | 98.7899 | 98.5613 | 98.8549 | 98.1008 | 98.563 | 98.5841 | 98.5384 | 98.352 | 98.0513 | 98.4045 | 97.4171 | 98.0383 | 98.14 | 98.1411 | 97.9782 | 97.6992 | 97.9985 | 2018-08-01 | 2022-06-13
Chint Power Systems America | SCH200K-T-US-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 200 kVA, 480 Vac, Grid Support Utility Interactive Inverter | 200 | 480 | 98 | CSA Group | [3/11/2025] | CSA Group | [3/11/2025] | [V3.00] | 2025-04-21 | [3/11/2025] | 2025-04-21 | CSA Group | 2025-03-11 | 2025-04-21 |  | N | N | 10 |  |  | 900 | 1000 | 1300 | 20.16 | 40.32 | 60.48 | 100.8 | 151.2 | 201.6 | 97.8214 | 98.36 | 98.4414 | 98.3171 | 98.0771 | 97.86 | 98.1643 | 97.6221 | 98.255 | 98.401 | 98.2066 | 97.923 | 97.6892 | 98.0328 | 96.6113 | 97.6662 | 97.8805 | 97.8837 | 97.633 | 97.3955 | 97.6643 | 2025-04-21 | 2025-07-21
Chint Power Systems America | SCH250K-T-US-600 {600V} | N | Y | Y | Y | Y | Y | Y* | Y | 250 kW, 600 Vac Grid Support Utility Interactive Inverter | 250 | 600 | 98.5 | CSA Group | [12/3/2024] | CSA Group | [12/3/2024] | [2.0] | 2025-01-13 | [12/3/2024] | 2025-01-13 | CSA Group | 2024-12-02 | 2025-01-13 |  | N | N | 15 |  |  | 900 | 1100 | 1300 | 25.03 | 50.06 | 75.09 | 125.15 | 187.725 | 250.3 | 97.4986 | 98.5514 | 98.7043 | 98.6057 | 98.49 | 98.5114 | 98.5045 | 97.8971 | 98.1643 | 98.6357 | 98.4114 | 98.3886 | 98.2486 | 98.3852 | 97.5629 | 98.0286 | 98.3014 | 98.3529 | 98.1786 | 97.9014 | 98.1839 | 2025-01-13 | 2025-02-03
Chint Power Systems America | CPS SCH275KTL-DO/US-800 {800V} | N | Y | Y | Y | Y | Y | Y* | Y | 275kVA Grid Support Utility Interactive Inverter, 1500Vdc, 800Vac 3 Phase Non-isolated | 275 | 800 | 98.5 | TUV Rheinland | [5/31/2022] | TUV Rheinland | [5/31/2022] | [01.00] | 2022-02-01 | [1/13/2022] | 2022-09-12 | TUV Rheinland | 2022-06-14 | 2022-09-12 |  | N | N | 6.5 |  |  | 900 | 1190 | 1300 | 27.5 | 55 | 82.5 | 137.5 | 206.25 | 275 | 97.0743 | 97.7914 | 98.0243 | 98.19 | 98.0943 | 97.89 | 98.0398 | 98.3714 | 98.8114 | 98.89 | 98.9171 | 98.81 | 98.67 | 98.8176 | 98.0929 | 98.6957 | 98.7829 | 98.8371 | 98.73 | 98.59 | 98.7246 | 2022-02-01 | 2022-09-12
Chint Power Systems America | CPS SCH320KTL-DO/US-800 {800V} | N | Y | Y | Y | Y | Y | Y* | Y | 320kVA Grid Support Utility Interactive Inverter, 1500Vdc, 800Vac 3 Phase Non-isolated | 320 | 800 | 98.5 | CSA Group | [5/6/2024] | CSA Group | [5/6/2024] | 1.01.00 | 2024-05-06 | [5/6/2024] | 2024-07-01 | CSA Group | 2024-05-27 | 2024-07-01 |  | N | N | 15 |  |  | 880 | 1190 | 1300 | 32.042 | 64.084 | 96.126 | 160.21 | 240.315 | 320.42 | 97.33 | 98.05 | 98.28 | 98.38 | 98.28 | 97.9 | 98.23 | 98.27 | 98.81 | 98.88 | 98.77 | 98.66 | 98.32 | 98.68 | 98.01 | 98.65 | 98.75 | 98.78 | 98.69 | 98.38 | 98.67 | 2023-11-01 | 2024-07-01
Chint Power Systems America | CPS SCH350KTL-DO/US-800 {800V} | N | Y | Y | Y | Y | Y | Y* | Y | 350kVA Grid Support Utility Interactive Inverter, 1500Vdc, 800Vac 3 Phase Non-isolated | 350 | 800 | 98.5 | CSA Group | [5/6/2024] | CSA Group | [5/6/2024] | 1.01.00 | 2024-05-06 | [5/6/2024] | 2024-07-01 | CSA Group | 2024-05-27 | 2024-07-01 |  | N | N | 15 |  |  | 880 | 1190 | 1300 | 35.043 | 70.086 | 105.13 | 175.216 | 262.824 | 350.432 | 97.46 | 98.13 | 98.31 | 98.34 | 98.3 | 98.05 | 98.25 | 98.3 | 98.72 | 98.8 | 98.8 | 98.71 | 98.53 | 98.71 | 98.15 | 98.64 | 98.7 | 98.66 | 98.66 | 98.34 | 98.63 | 2023-11-01 | 2024-07-01
CSI Solar Co., Ltd. | CSI-25K-T480GL03-U {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 25 kW, 480 Vac Grid Support Utility Interactive Inverter | 24.8876 | 480 | 98.5 | CSA Group | [9/26/2023] | CSA Group | [9/26/2023] | [A2] | 2024-01-11 | [9/26/2023] | 2024-01-11 | CSA Group | 2023-09-14 | 2024-01-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 2.4888 | 4.9775 | 7.4663 | 12.4438 | 18.6657 | 24.8876 | 98.3085 | 98.5231 | 98.5821 | 98.598 | 98.4828 | 98.3112 | 98.5053 | 98.2835 | 98.5436 | 98.6114 | 98.5806 | 98.5088 | 98.4295 | 98.525 | 98.3192 | 98.4885 | 98.5276 | 98.5312 | 98.4377 | 98.377 | 98.4629 | 2024-01-11
CSI Solar Co., Ltd. | CSI-25K-T480GL01-UB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 25 kW, 480 Vac, Long Separate Wiring Box, Three-Phase Grid Support Utility Interactive Inverter | 24.958 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/06/2020] | [1D] | 2020-11-23 | [03/06/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 347 | 470 | 800 | 2.4958 | 4.9916 | 7.4874 | 12.479 | 18.7185 | 24.9581 | 97.8538 | 98.3868 | 98.42 | 98.5665 | 98.4105 | 98.354 | 98.4181 | 98.0001 | 98.4275 | 98.4174 | 98.6659 | 98.423 | 98.3476 | 98.4529 | 97.893 | 98.4187 | 98.493 | 98.685 | 98.4659 | 98.373 | 98.4852 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-25KTL-GS-FLB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 25 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box | 25 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [03/29/2019] | [1D] | 2019-05-01 | [03/29/2019] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 14 |  |  | 580 | 650 | 770 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 97.143 | 97.3103 | 97.5582 | 97.902 | 98.1863 | 97.7856 | 97.9456 | 97.1369 | 97.2947 | 97.4013 | 97.8837 | 98.2954 | 97.7509 | 97.978 | 97.2361 | 97.396 | 97.5435 | 97.6922 | 98.0012 | 97.4855 | 97.7947 | 2019-05-01 | 2021-12-01
CSI Solar Co., Ltd. | CSI-30K-T208GL03-U {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 30 kW, 208 Vac Grid Support Utility Interactive Inverter | 29.878 | 208 | 97 | CSA Group | [9/26/2023] | CSA Group | [9/26/2023] | [A2] | 2024-01-11 | [9/26/2023] | 2024-01-11 | CSA Group | 2023-09-14 | 2024-01-11 |  | N | N | 1.394 |  |  | 340 | 580 | 680 | 2.988 | 5.976 | 8.963 | 14.939 | 22.408 | 29.878 | 96.25 | 97.44 | 97.69 | 97.55 | 96.93 | 96.47 | 97.13 | 96.06 | 97.23 | 97.54 | 97.46 | 96.84 | 96.41 | 97.02 | 96.09 | 97.08 | 97.42 | 97.36 | 96.81 | 96.36 | 96.96 | 2024-01-11
CSI Solar Co., Ltd. | CSI-30K-T480GL03-U {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac Grid Support Utility Interactive Inverter | 29.883 | 480 | 98.5 | CSA Group | [9/26/2023] | CSA Group | [9/26/2023] | [A2] | 2024-01-11 | [9/26/2023] | 2024-01-11 | CSA Group | 2023-09-14 | 2024-01-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 2.988 | 5.977 | 8.965 | 14.941 | 22.412 | 29.883 | 97.84 | 98.48 | 98.58 | 98.53 | 98.48 | 98.23 | 98.47 | 98.05 | 98.49 | 98.59 | 98.53 | 98.44 | 98.29 | 98.46 | 98 | 98.44 | 98.58 | 98.56 | 98.49 | 98.31 | 98.48 | 2024-01-11
CSI Solar Co., Ltd. | CSI-30K-T480GL01-UB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac, Long Separate Wiring Box, Three-Phase Grid Support Utility Interactive Inverter | 29.948 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/06/2020] | [1D] | 2020-11-23 | [03/06/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 417 | 700 | 800 | 2.9948 | 5.9895 | 8.9843 | 14.9738 | 22.4607 | 29.9477 | 97.7689 | 98.392 | 98.4344 | 98.5669 | 98.4121 | 98.3166 | 98.4158 | 97.814 | 98.4242 | 98.504 | 98.651 | 98.42 | 98.356 | 98.4514 | 97.89 | 98.4279 | 98.517 | 98.6982 | 98.451 | 98.365 | 98.4829 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-30KTL-GS-FLB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box | 30 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [03/29/2019] | [1D] | 2019-05-01 | [03/29/2019] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 15 |  |  | 580 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.1367 | 97.9124 | 97.905 | 98.3089 | 97.8705 | 97.9174 | 97.9418 | 97.3783 | 98.0388 | 98.0359 | 98.3477 | 98.1139 | 97.915 | 98.1105 | 97.12 | 97.8656 | 97.9617 | 98.2389 | 97.9687 | 97.8103 | 97.9776 | 2019-05-01 | 2021-12-01
CSI Solar Co., Ltd. | CSI-33K-T480GL03-U {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 33 kW, 480 Vac Grid Support Utility Interactive Inverter | 32.865 | 480 | 98.5 | CSA Group | [9/26/2023] | CSA Group | [9/26/2023] | [A2] | 2024-01-11 | [9/26/2023] | 2024-01-11 | CSA Group | 2023-09-14 | 2024-01-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 3.287 | 6.573 | 9.86 | 16.433 | 24.649 | 32.865 | 98.21 | 98.56 | 98.6 | 98.54 | 98.46 | 98.33 | 98.48 | 98.38 | 98.63 | 98.63 | 98.62 | 98.53 | 98.38 | 98.55 | 98.23 | 98.6 | 98.62 | 98.58 | 98.51 | 98.35 | 98.52 | 2024-01-11
CSI Solar Co., Ltd. | CSI-36K-T480GL03-U {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac Grid Support Utility Interactive Inverter | 35.866 | 480 | 98.5 | CSA Group | [9/26/2023] | CSA Group | [9/26/2023] | [A2] | 2024-01-11 | [9/26/2023] | 2024-01-11 | CSA Group | 2023-09-14 | 2024-01-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 3.587 | 7.173 | 10.76 | 17.933 | 26.899 | 35.866 | 98.07 | 98.58 | 98.63 | 98.53 | 98.42 | 98.19 | 98.45 | 98.47 | 98.61 | 98.67 | 98.62 | 98.5 | 98.28 | 98.54 | 98.18 | 98.54 | 98.61 | 98.53 | 98.46 | 98.12 | 98.47 | 2024-01-11
CSI Solar Co., Ltd. | CSI-36K-T480GL01-UB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac, Long Separate Wiring Box, Three-Phase Grid Support Utility Interactive Inverter | 35.925 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/06/2020] | [1D] | 2020-11-23 | [03/06/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 500 | 700 | 800 | 3.5925 | 7.185 | 10.7775 | 17.9625 | 26.9438 | 35.9251 | 97.7435 | 98.365 | 98.4061 | 98.579 | 98.4309 | 98.3073 | 98.4221 | 97.796 | 98.3474 | 98.465 | 98.636 | 98.468 | 98.334 | 98.4633 | 97.826 | 98.4038 | 98.496 | 98.6621 | 98.483 | 98.319 | 98.4837 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-36KTL-GS-FLB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box | 36 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [03/29/2019] | [1D] | 2019-05-01 | [03/29/2019] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 15 |  |  | 580 | 650 | 780 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3556 | 98.1469 | 98.1132 | 98.3457 | 98.0215 | 98.1483 | 98.0865 | 97.6545 | 98.3164 | 98.2591 | 98.438 | 98.343 | 98.1379 | 98.3138 | 97.3624 | 98.154 | 98.2138 | 98.3749 | 98.1715 | 98.0758 | 98.1813 | 2019-05-01 | 2021-12-01
CSI Solar Co., Ltd. | CSI-40K-T480GL03-U {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 40 kW, 480 Vac Grid Support Utility Interactive Inverter | 39.841 | 480 | 98.5 | CSA Group | [9/26/2023] | CSA Group | [9/26/2023] | [A2] | 2024-01-11 | [9/26/2023] | 2024-01-11 | CSA Group | 2023-09-14 | 2024-01-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 3.984 | 7.968 | 11.952 | 19.92 | 29.88 | 39.841 | 97.47 | 98.22 | 98.59 | 98.59 | 98.58 | 98.15 | 98.5 | 98.08 | 98.33 | 98.61 | 98.55 | 98.53 | 97.96 | 98.48 | 97.93 | 98.3 | 98.55 | 98.59 | 98.54 | 97.84 | 98.48 | 2024-01-11
CSI Solar Co., Ltd. | CSI-40K-T480GL01-UB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 40 kW, 480 Vac, Long Separate Wiring Box, Three-Phase Grid Support Utility Interactive Inverter | 39.926 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/06/2020] | [1D] | 2020-11-23 | [03/06/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 556 | 700 | 800 | 3.9926 | 7.9852 | 11.9778 | 19.9629 | 29.9444 | 39.9259 | 97.7566 | 98.3499 | 98.431 | 98.5651 | 98.4319 | 98.3273 | 98.4234 | 97.787 | 98.3669 | 98.459 | 98.628 | 98.441 | 98.347 | 98.4479 | 97.832 | 98.4148 | 98.466 | 98.635 | 98.515 | 98.336 | 98.493 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-40KTL-GS-B {480V} | N | N | Y | Y | Y | N | N | N | 40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box and external Fan | 40 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/29/2019] | [1D] | 2019-05-15 | [03/29/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.47 | 98.0068 | 98.0574 | 98.1972 | 98.114 | 98.0292 | 98.0893 | 97.9259 | 98.3089 | 98.392 | 98.7145 | 98.5725 | 98.3423 | 98.5301 | 97.5823 | 98.1565 | 98.1932 | 98.4353 | 98.3489 | 98.2444 | 98.3028 | 2019-05-15 | 2021-12-01
CSI Solar Co., Ltd. | CSI-40KTL-GS-FLB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box | 40 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/29/2019] | [1D] | 2019-05-01 | [03/29/2019] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.4777 | 98.0039 | 98.0564 | 98.1952 | 98.1258 | 98.0274 | 98.0951 | 97.9247 | 98.3105 | 98.4002 | 98.7211 | 98.5785 | 98.342 | 98.5357 | 97.5764 | 98.1504 | 98.1795 | 98.4337 | 98.3428 | 98.244 | 98.2971 | 2019-05-01 | 2021-12-01
CSI Solar Co., Ltd. | CSI-50K-T480GL03-U {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter | 49.848 | 480 | 98.5 | CSA Group | [9/26/2023] | CSA Group | [9/26/2023] | [A2] | 2024-01-11 | [9/26/2023] | 2024-01-11 | CSA Group | 2023-09-14 | 2024-01-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 4.985 | 9.97 | 14.955 | 24.924 | 37.386 | 49.848 | 97.74 | 98.52 | 98.55 | 98.63 | 98.46 | 98.16 | 98.46 | 97.43 | 98.38 | 98.69 | 98.73 | 98.57 | 98.36 | 98.55 | 97.5 | 98.2 | 98.53 | 98.64 | 98.51 | 98.34 | 98.47 | 2024-01-11
CSI Solar Co., Ltd. | CSI-50K-T480GL01-UB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter | 49.916 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/06/2020] | [1D] | 2020-11-23 | [03/06/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 568 | 720 | 850 | 4.9916 | 9.9832 | 14.9748 | 24.9581 | 37.4371 | 49.9161 | 97.752 | 98.3642 | 98.434 | 98.585 | 98.42 | 98.313 | 98.4215 | 97.791 | 98.3809 | 98.447 | 98.645 | 98.443 | 98.352 | 98.4522 | 97.84 | 98.411 | 98.483 | 98.68 | 98.493 | 98.3201 | 98.4922 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-50KTL-GS-B {480V} | N | N | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac, Seperated Wiring Box, 3-phase Grid Support Utility Interactive Inverter, | 50 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/06/2020] | [1D] | 2020-11-23 | [03/06/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.7362 | 98.4442 | 98.4559 | 98.5822 | 98.45 | 98.3475 | 98.4445 | 97.7983 | 98.5313 | 98.5521 | 98.7004 | 98.5123 | 98.3959 | 98.5232 | 97.8768 | 98.5781 | 98.6506 | 98.7596 | 98.5678 | 98.4644 | 98.5857 | 2018-02-01 | 2021-12-01
CSI Solar Co., Ltd. | CSI-50KTL-GS-FLB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac, Seperated Wiring Box, Fanless, 3-phase Grid Support Utility Interactive Inverter, | 50 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/06/2020] | [1D] | 2020-11-23 | [03/06/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5167 | 98.5279 | 98.441 | 98.5562 | 98.3221 | 98.4464 | 98.3698 | 97.7469 | 98.5505 | 98.5222 | 98.6539 | 98.4338 | 98.4888 | 98.4718 | 97.9805 | 98.7 | 98.8047 | 98.7919 | 98.5679 | 98.5006 | 98.6231 | 2018-02-01 | 2021-12-01
CSI Solar Co., Ltd. | CSI-60K-T480GL03-U {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 59.898 | 480 | 98.5 | CSA Group | [9/26/2023] | CSA Group | [9/26/2023] | [A2] | 2024-01-11 | [9/26/2023] | 2024-01-11 | CSA Group | 2023-09-14 | 2024-01-11 |  | N | N | 3.1623 |  |  | 580 | 720 | 850 | 5.99 | 11.98 | 17.969 | 29.949 | 44.923 | 59.898 | 97.76 | 98.42 | 98.58 | 98.57 | 98.47 | 98.17 | 98.46 | 97.62 | 98.48 | 98.69 | 98.71 | 98.58 | 98.38 | 98.56 | 97.48 | 98.31 | 98.5 | 98.63 | 98.49 | 98.22 | 98.46 | 2024-01-11
CSI Solar Co., Ltd. | CSI-60K-T480GL01-UB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 59.933 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/06/2020] | [1D] | 2020-11-23 | [03/06/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 526 | 720 | 850 | 5.9933 | 11.9866 | 17.9798 | 29.9664 | 44.9496 | 59.9328 | 97.739 | 98.411 | 98.444 | 98.579 | 98.412 | 98.28 | 98.4173 | 97.787 | 98.4024 | 98.465 | 98.622 | 98.441 | 98.342 | 98.4489 | 97.809 | 98.434 | 98.522 | 98.689 | 98.48 | 98.326 | 98.4921 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-60KTL-GS-B {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kW, 480 Vac, Seperated Wiring Box, 3-phase Grid Support Utility Interactive Inverter, | 60 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/06/2020] | [1D] | 2020-11-23 | [03/06/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 580 | 650 | 720 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7251 | 98.3108 | 98.4189 | 98.5501 | 98.3711 | 98.2238 | 98.3782 | 97.8227 | 98.4496 | 98.5404 | 98.6262 | 98.499 | 98.3294 | 98.4926 | 97.8622 | 98.5252 | 98.5865 | 98.7 | 98.5526 | 98.4499 | 98.5535 | 2018-02-01 | 2021-12-01
CSI Solar Co., Ltd. | CSI-66K-T480GL01-UB {480V} | N | N | Y | Y | Y | Y | Y* | Y | 66 kW, 480 Vac Grid Support Utility Interactive Inverter | 65.926 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/06/2020] | [1D] | 2020-11-23 | [03/06/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 579 | 720 | 850 | 6.5926 | 13.1851 | 19.7777 | 32.9628 | 49.4441 | 65.9255 | 97.752 | 98.351 | 98.413 | 98.588 | 98.42 | 98.31 | 98.4188 | 97.773 | 98.343 | 98.48 | 98.677 | 98.436 | 98.319 | 98.4549 | 97.807 | 98.369 | 98.501 | 98.657 | 98.487 | 98.321 | 98.483 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-66KTL-GS-B {480V} | N | N | Y | Y | Y | Y | Y* | Y | 66 kW, 480 Vac, Seperated Wiring Box, 3-phase Grid Support Utility Interactive Inverter | 66 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [03/06/2020] | [1D] | 2020-11-23 | [03/06/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 580 | 650 | 720 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.5717 | 98.3763 | 98.4763 | 98.5633 | 98.4214 | 98.3118 | 98.416 | 97.7441 | 98.5006 | 98.5537 | 98.7042 | 98.4989 | 98.3902 | 98.513 | 97.7721 | 98.6713 | 98.6538 | 98.7738 | 98.5561 | 98.4918 | 98.5847 | 2018-02-01 | 2021-12-01
CSI Solar Co., Ltd. | CSI-75K-T480GL03-U {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive Inverter | 74.574 | 480 | 98.5 | CSA Group | [8/6/2022] | CSA Group | [8/6/2022] | [1C] | 2023-05-01 | [8/6/2022] | 2023-05-01 | CSA Group | 2022-11-03 | 2023-05-01 |  | N | N | 2 |  |  | 550 | 730 | 850 | 7.4574 | 14.9148 | 22.3723 | 37.2871 | 55.9306 | 74.5742 | 97.1519 | 97.7396 | 97.9756 | 98.0455 | 97.9997 | 97.7577 | 97.9474 | 98.2493 | 98.6811 | 98.7466 | 98.7034 | 98.5655 | 98.3686 | 98.5995 | 97.9069 | 98.3276 | 97.9953 | 98.5443 | 98.3567 | 98.2661 | 98.3288 | 2023-05-01
CSI Solar Co., Ltd. | CSI-75K-T480GL02-U {480V} | N | N | Y | Y | Y | Y | Y* | Y | 75 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 75 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [10/16/2020] | [V1C] | 2020-11-23 | [10/16/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 550 | 720 | 850 | 7.5002 | 15.0005 | 22.5007 | 37.5012 | 56.2517 | 75.0023 | 98.147 | 98.5383 | 98.525 | 98.6238 | 98.3792 | 98.2162 | 98.4386 | 98.1775 | 98.5215 | 98.5439 | 98.6666 | 98.4445 | 98.2384 | 98.4859 | 98.244 | 98.5737 | 99.0148 | 98.6211 | 98.5743 | 98.294 | 98.6098 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-80K-T480GL03-U {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 85 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 79.446 | 480 | 98.5 | CSA Group | [8/6/2022] | CSA Group | [8/6/2022] | [1C] | 2023-05-01 | [8/6/2022] | 2023-05-01 | CSA Group | 2022-11-03 | 2023-05-01 |  | N | N | 2 |  |  | 550 | 730 | 850 | 7.9446 | 15.8892 | 23.8339 | 39.7231 | 59.5846 | 79.4462 | 97.2634 | 97.826 | 98.0173 | 98.037 | 97.8924 | 97.6791 | 97.8986 | 98.3446 | 98.6912 | 98.743 | 98.6499 | 98.4565 | 98.3341 | 98.5326 | 98.0783 | 98.4089 | 98.5773 | 98.5359 | 98.3844 | 98.2002 | 98.4191 | 2023-05-01
CSI Solar Co., Ltd. | CSI-80K-T480GL02-U {480V} | N | N | Y | Y | Y | Y | Y* | Y | 85 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 80 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [10/16/2020] | [V1C] | 2020-11-23 | [10/16/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 550 | 720 | 850 | 8.0003 | 16.0006 | 24.0009 | 40.0015 | 60.0023 | 80.0031 | 98.1441 | 98.5363 | 98.5241 | 98.6265 | 98.3794 | 98.2123 | 98.4387 | 98.1764 | 98.5232 | 98.543 | 98.6654 | 98.4447 | 98.2424 | 98.4859 | 98.2451 | 98.5776 | 99.0149 | 98.6271 | 98.575 | 98.2898 | 98.6114 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-90K-T480GL03-U {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 90 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 89.449 | 480 | 98 | CSA Group | [8/6/2022] | CSA Group | [8/6/2022] | [1C] | 2023-05-01 | [8/6/2022] | 2023-05-01 | CSA Group | 2022-11-03 | 2023-05-01 |  | N | N | 2 |  |  | 550 | 730 | 850 | 8.9449 | 17.8897 | 26.8346 | 44.7243 | 67.0864 | 89.4486 | 97.2768 | 97.7779 | 98.0978 | 98.0182 | 97.7335 | 97.5594 | 97.8123 | 98.4597 | 98.7601 | 98.72 | 98.6416 | 98.4168 | 98.2225 | 98.5096 | 98.1892 | 98.553 | 98.5772 | 98.5212 | 98.2871 | 98.094 | 98.3708 | 2023-05-01
CSI Solar Co., Ltd. | CSI-90K-T480GL02-U {480V} | N | N | Y | Y | Y | Y | Y* | Y | 90 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 90 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [10/16/2020] | [V1C] | 2020-11-23 | [10/16/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 550 | 720 | 850 | 9.0005 | 18.001 | 27.0015 | 45.0024 | 67.5036 | 90.0049 | 98.1425 | 98.5301 | 98.5175 | 98.6202 | 98.382 | 98.2129 | 98.4376 | 98.1677 | 98.5208 | 98.5367 | 98.6571 | 98.4429 | 98.2296 | 98.4814 | 98.24 | 98.5713 | 99.0158 | 98.6197 | 98.5715 | 98.2914 | 98.6076 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-100K-T480GL03-U {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 99.368 | 480 | 98 | CSA Group | [8/6/2022] | CSA Group | [8/6/2022] | [1C] | 2023-05-01 | [8/6/2022] | 2023-05-01 | CSA Group | 2022-11-03 | 2023-05-01 |  | N | N | 2 |  |  | 550 | 730 | 850 | 9.9368 | 19.8736 | 29.8105 | 49.6841 | 74.5262 | 99.3682 | 97.2872 | 97.736 | 97.7798 | 97.8454 | 97.733 | 97.4318 | 97.7295 | 98.5174 | 98.7659 | 98.7368 | 98.6111 | 98.3712 | 98.1531 | 98.4801 | 98.2563 | 98.5521 | 98.5681 | 98.4642 | 98.2153 | 98.045 | 98.3199 | 2023-05-01
CSI Solar Co., Ltd. | CSI-100K-T480GL02-U {480V} | N | N | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 100 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [10/16/2020] | [V1C] | 2020-11-23 | [10/16/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 550 | 720 | 850 | 10.0004 | 20.0008 | 30.0012 | 50.002 | 75.003 | 100.004 | 98.1406 | 98.5261 | 98.5197 | 98.6189 | 98.3796 | 98.2109 | 98.436 | 98.1693 | 98.5244 | 98.5388 | 98.6582 | 98.442 | 98.2301 | 98.4817 | 98.242 | 98.5714 | 99.0139 | 98.6188 | 98.571 | 98.2889 | 98.607 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-125KTL-GS-E {600V} | N | N | Y | Y | Y | Y | Y* | Y | 125 kW, 600 Vac, 3-phase Grid Support Utility Interactive Inverter, single input | 125 | 600 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [10/16/2020] | [V08] | 2020-11-23 | [10/16/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 860 | 950 | 1250 | 12.5083 | 25.0165 | 37.5248 | 62.5413 | 93.812 | 125.0827 | 98.9167 | 99.0279 | 98.941 | 98.9462 | 98.8521 | 98.7464 | 98.8886 | 98.5469 | 98.8405 | 98.7722 | 98.8039 | 98.6338 | 98.6288 | 98.6928 | 98.2805 | 98.7 | 98.7947 | 98.6619 | 98.4679 | 98.3006 | 98.5436 | 2019-08-15 | 2021-12-01
CSI Solar Co., Ltd. | CSI-125K-T600GL02-U {600V} | N | N | Y | Y | Y | Y | Y* | Y | 125 kW, 600 Vac, 3-phase Grid Support Utility Interactive Inverter, single input | 125.083 | 600 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [10/16/2020] | [V08] | 2020-11-23 | [10/16/2020] | 2020-11-23 | CSA Group | 2020-10-16 | 2020-11-23 |  | N | N | 1 |  |  | 860 | 1080 | 1250 | 12.5083 | 25.0165 | 37.5248 | 62.5413 | 93.812 | 125.0827 | 98.2442 | 98.6339 | 98.622 | 98.725 | 98.4773 | 98.3136 | 98.537 | 98.2735 | 98.6299 | 98.6462 | 98.7609 | 98.5469 | 98.336 | 98.5864 | 98.3436 | 98.6734 | 99.1159 | 98.7211 | 98.6759 | 98.3966 | 98.7108 | 2020-11-23 | 2021-12-01
CSI Solar Co., Ltd. | CSI-185K-T600GL02-U {600V} | N | N | Y | Y | Y | Y | Y* | Y | 185 kW, 600 Vac Grid Support Utility Interactive Inverter | 185.005 | 600 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [11/10/2020] | [V18] | 2021-01-21 | [11/10/2020] | 2021-01-21 | CSA Group | 2020-11-10 | 2021-01-21 |  | N | N | 1 |  |  | 850 | 1080 | 1300 | 18.5005 | 37.0011 | 55.5016 | 92.5026 | 138.7539 | 185.0053 | 97.818 | 98.477 | 98.621 | 98.627 | 98.457 | 98.25 | 98.4775 | 97.932 | 98.566 | 98.654 | 98.582 | 98.404 | 98.181 | 98.4495 | 97.65 | 98.488 | 98.579 | 98.893 | 98.698 | 98.444 | 98.6596 | 2021-01-21 | 2021-12-01
CSI Solar Co., Ltd. | CSI-185K-T600GL03-U {600V} | N | N | Y | Y | Y | Y | Y* | Y | 185 kW, 600 Vac Grid Support Utility Interactive Inverter | 185.005 | 600 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [8/10/2021] | [V17] | 2022-05-01 | [8/10/2021] | 2022-05-01 | CSA Group | 2021-10-21 | 2022-05-01 |  | N | N | 1 |  |  | 850 | 1080 | 1300 | 18.5005 | 37.0011 | 55.5016 | 92.5026 | 138.7539 | 185.0053 | 97.818 | 98.477 | 98.621 | 98.627 | 98.457 | 98.25 | 98.4775 | 97.932 | 98.566 | 98.654 | 98.582 | 98.404 | 98.181 | 98.4495 | 97.65 | 98.488 | 98.579 | 98.893 | 98.698 | 98.444 | 98.6596 | 2022-05-02
CSI Solar Co., Ltd. | CSI-255K-T800GL02-U {800V} | N | N | Y | Y | Y | Y | Y* | Y | 255 kW, 800 Vac Grid Support Utility Interactive Inverter | 255.013 | 800 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [11/10/2020] | [V18] | 2021-01-21 | [11/10/2020] | 2021-01-21 | CSA Group | 2020-11-10 | 2021-01-21 |  | N | N | 1 |  |  | 850 | 1080 | 1300 | 25.5013 | 51.0025 | 76.5038 | 127.5063 | 191.2595 | 255.0126 | 97.818 | 98.477 | 98.621 | 98.627 | 98.457 | 98.25 | 98.4775 | 97.645 | 98.299 | 98.495 | 98.546 | 98.427 | 98.255 | 98.4139 | 98.059 | 98.701 | 98.84 | 98.835 | 98.696 | 98.521 | 98.7085 | 2021-01-21 | 2021-12-01
CSI Solar Co., Ltd. | CSI-255K-T800GL03-U {800V} | N | N | Y | Y | Y | Y | Y* | Y | 255 kW, 800 Vac Grid Support Utility Interactive Inverter | 255.013 | 800 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [8/10/2021] | [V17] | 2022-05-01 | [8/10/2021] | 2022-05-01 | CSA Group | 2021-10-22 | 2022-05-01 |  | N | N | 1 |  |  | 850 | 1080 | 1300 | 25.5013 | 51.0025 | 76.5038 | 127.5063 | 191.2595 | 255.0126 | 97.818 | 98.477 | 98.621 | 98.627 | 98.457 | 98.25 | 98.4775 | 97.645 | 98.299 | 98.495 | 98.546 | 98.427 | 98.255 | 98.4139 | 98.059 | 98.701 | 98.84 | 98.835 | 98.696 | 98.521 | 98.7085 | 2022-05-02
Darfon Electronics Corp. | H5001xxxxxx {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 5000 W, 240 Vac, Hybrid PV and Battery Grid Support Utility Interactive Inverter, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer). Inverter is capable of PCS functionality. | 4.844 | 240 | 94.5 | No Information Submitted | No Information Submitted | Intertek | [07/28/2020] | [82,372] | 2020-11-02 | [07/28/2020] | 2020-11-02 | Intertek | 2020-08-12 | 2020-11-02 |  | N | N | 28.48 |  |  | 300 | 360 | 380 | 0.48442 | 0.96883 | 1.4533 | 2.4221 | 3.6331 | 4.8442 | 86.6736 | 92.8161 | 94.3502 | 95.2023 | 95.0579 | 94.4449 | 94.5252 | 87.1365 | 93.1676 | 94.6479 | 95.4859 | 95.3797 | 94.8013 | 94.845 | 87.1729 | 93.1946 | 94.6523 | 95.4841 | 95.3494 | 94.7714 | 94.8304 | 2020-11-02 | 2021-01-11
Darfon Electronics Corp. | H5000xxxxxx {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 5000 W, 240 Vac, Hybrid PV and Battery Grid support Utility Interactive Inverter with PCS functionality, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer). Inverter is capable of PCS functionality. | 5.074 | 240 | 95.5 | No Information Submitted | No Information Submitted | Intertek | [07/28/2020] | [82,372] | 2018-10-15 | [07/28/2020] | 2020-09-11 | Intertek | 2020-09-02 | 2020-09-11 |  | N | N | 0.43 |  |  | 300 | 360 | 380 | 0.508 | 1.016 | 1.524 | 2.54 | 3.81 | 5.076 | 89.2283 | 93.7363 | 94.9074 | 95.7518 | 95.8863 | 95.613 | 95.3531 | 89.4891 | 93.9486 | 95.2566 | 95.9139 | 96.0338 | 95.8858 | 95.5419 | 89.3177 | 94.0048 | 95.2025 | 95.9477 | 96.0161 | 95.9196 | 95.5308 | 2018-03-15 | 2021-01-11
Darfon Electronics Corp. | H7xxxxxx {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 9600 W, 240 Vac, Grid Support Utility Interactive Inverter, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer) | 9.604 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/5/2022] | [DSP1 V5.1, DSP2 V6.2] | 2022-10-01 | [8/5/2022] | 2022-10-01 | Intertek | 2022-07-26 | 2022-10-01 |  | N | N | 26.9 |  |  | 230 | 360 | 410 | 0.9604 | 1.9208 | 2.8812 | 4.802 | 7.203 | 9.604 | 91.3976 | 94.7078 | 95.7095 | 96.1271 | 96.2157 | 96.023 | 95.8586 | 92.0634 | 95.5511 | 96.3626 | 96.8436 | 96.8099 | 96.5703 | 96.4985 | 92.3296 | 95.6888 | 96.5581 | 97.0053 | 96.9658 | 96.7095 | 96.6631 | 2022-11-01
dcbel Inc. | Dcbel Ara (DBHS-ARxx-xx) {240V} | Y | Y | N | N | N | N | N |  | 7.62 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.624 | 240 | 92 | TUV SUD America | [5/7/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Home Energy Appliance including grid support solar inverter | N | N | 32.5 |  |  | 450 | 460 | 470 | 0.762 | 1.525 | 2.287 | 3.812 | 5.718 | 7.624 | 84.3 | 90.7 | 92.42 | 93.07 | 92.35 | 92.02 | 92.09 | 82.61 | 90.67 | 92.41 | 93.11 | 92.35 | 92.04 | 92.03 | 84.62 | 90.66 | 92.4 | 93.08 | 92.34 | 92.07 | 92.1 | 2026-04-01
Delta Electronics | SOLIVIA 3.8 NA G4 TL {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3800 W, 208 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 3.32 | 208 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [10/15/2020] | [02.05.01] | 2018-10-15 | [10/15/2020] | 2020-11-12 | Intertek | 2020-09-30 | 2020-11-12 |  | Y | N | 1.14 |  |  | 100 | 380 | 500 | 0.33 | 0.66 | 1 | 1.66 | 2.49 | 3.32 | 94.6 | 96.1 | 97 | 97.3 | 97.1 | 96.8 | 97 | 96.3 | 96.9 | 97.8 | 97.9 | 98.1 | 97.5 | 97.8 | 95.9 | 95.8 | 96.9 | 97.4 | 97.4 | 97.1 | 97.2 | 2017-10-16 | 2020-11-12
Delta Electronics | M4-TL-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 3648 W, 208 Vac transformerless Grid Support Utility Interactive Inverter | 3.33 | 208 | 97 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.92 |  |  | 180 | 380 | 480 | 0.3328 | 0.6656 | 0.9984 | 1.664 | 2.496 | 3.328 | 92 | 94.6 | 95.7 | 96.5 | 96.7 | 96.5 | 96.2 | 93 | 95.7 | 97.3 | 97.3 | 97.8 | 97.4 | 97.3 | 92.9 | 95.9 | 96.8 | 97.5 | 97.6 | 97.5 | 97.2 | 2018-03-01 | 2023-02-01
Delta Electronics | E4_BDI {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3328 W, 208 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 3.3413 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.24 |  |  | 280 | 380 | 480 | 0.33413 | 0.66827 | 1.0024 | 1.6707 | 2.506 | 3.3413 | 92.6852 | 95.2806 | 96.3508 | 97.0447 | 97.0686 | 97.336 | 96.7261 | 92.1027 | 95.4066 | 96.5531 | 97.315 | 97.5791 | 97.6175 | 97.0747 | 89.0319 | 94.0125 | 95.5747 | 96.8148 | 97.2577 | 97.3776 | 96.4774 | 2022-06-01 | 2024-04-02
Delta Electronics | E4-TL-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3328 W, 208 Vac, transformerless, Bi-directional, Multi-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 3.36 | 208 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2020-08-11 | [6/2/2022] | 2020-08-11 | CSA Group | 2022-11-25 | 2020-08-11 |  | Y | N | 1.21 |  |  | 200 | 380 | 480 | 0.33599 | 0.67197 | 1.008 | 1.6799 | 2.5199 | 3.3599 | 92.7058 | 95.316 | 96.0794 | 96.9375 | 97.261 | 97.2579 | 96.7716 | 94.6716 | 96.7433 | 97.431 | 97.8832 | 97.9342 | 97.8306 | 97.6679 | 93.5334 | 96.0786 | 96.9192 | 97.5645 | 97.7603 | 97.6747 | 97.3608 | 2020-08-11 | 2024-04-02
Delta Electronics | SOLIVIA 3.8 NA G4 TL {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3800 W, 240 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 3.81 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [10/15/2020] | [02.05.01] | 2018-10-15 | [10/15/2020] | 2020-11-12 | Intertek | 2020-09-30 | 2020-11-12 |  | Y | N | 1.19 |  |  | 100 | 380 | 500 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 94.1 | 95.9 | 96.9 | 97.3 | 97.2 | 96.8 | 97 | 95.5 | 96.9 | 98 | 98.3 | 98.1 | 98 | 98 | 94.6 | 95.6 | 97.3 | 97.8 | 97.8 | 97.6 | 97.5 | 2017-10-16 | 2020-11-12
Delta Electronics | M4-TL-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 4000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter | 3.84 | 240 | 97.5 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 2.03 |  |  | 180 | 380 | 480 | 0.384 | 0.768 | 1.152 | 1.92 | 2.88 | 3.84 | 92.9 | 95.1 | 96.1 | 96.9 | 96.9 | 96.7 | 96.6 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 98 | 98 | 93.6 | 96.4 | 97.2 | 97.7 | 97.8 | 97.7 | 97.5 | 2018-03-01 | 2023-02-01
Delta Electronics | E4-TL-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3840 W, 240 Vac, transformerless, Bi-directional, Multi-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 3.87 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2020-08-11 | [6/2/2022] | 2020-08-11 | CSA Group | 2022-11-25 | 2020-08-11 |  | Y | N | 1.27 |  |  | 200 | 380 | 400 | 0.38696 | 0.77392 | 1.1609 | 1.9348 | 2.9022 | 3.8696 | 92.8573 | 95.3032 | 96.0816 | 97.008 | 97.3433 | 97.3609 | 96.8409 | 95.3025 | 97.1049 | 97.7261 | 98.0933 | 98.1429 | 98.1114 | 97.9154 | 94.285 | 96.4536 | 97.2773 | 97.8608 | 98.0038 | 97.9448 | 97.6574 | 2020-08-11 | 2024-04-02
Delta Electronics | E4_BDI {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3480 W, 240 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 3.8982 | 240 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.3 |  |  | 280 | 380 | 480 | 0.38982 | 0.77964 | 1.1695 | 1.9491 | 2.9236 | 3.8982 | 92.7724 | 95.442 | 96.4856 | 97.125 | 97.3647 | 97.4288 | 96.9323 | 93.2521 | 96.152 | 97.0569 | 97.6876 | 97.8589 | 97.9251 | 97.4604 | 90.5052 | 94.6892 | 96.1085 | 97.2209 | 97.5572 | 97.6718 | 96.893 | 2022-06-01 | 2024-04-02
Delta Electronics | M5-TL-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 4560 W, 208 Vac transformerless Grid Support Utility Interactive Inverter | 4.16 | 208 | 97.5 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.24 |  |  | 220 | 380 | 480 | 0.416 | 0.832 | 1.248 | 2.08 | 3.12 | 4.16 | 94.5 | 96.1 | 96.9 | 97.3 | 97.2 | 96.9 | 97 | 95.8 | 97.3 | 97.8 | 98 | 97.8 | 97.6 | 97.7 | 95 | 96.8 | 97.4 | 97.7 | 97.7 | 97.4 | 97.5 | 2018-03-01 | 2023-02-01
Delta Electronics | M5-TL-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 5000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter | 4.86 | 240 | 97.5 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.26 |  |  | 220 | 380 | 480 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 94.3 | 96.1 | 96.9 | 97.3 | 97.2 | 96.9 | 97 | 96.3 | 97.6 | 98 | 98.2 | 98 | 97.8 | 97.9 | 95.6 | 97.2 | 97.7 | 98 | 97.9 | 97.7 | 97.8 | 2018-03-01 | 2023-02-01
Delta Electronics | M6-TL-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 5472 W, 208 Vac transformerless Grid Support Utility Interactive Inverter. | 4.99 | 208 | 97 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.86 |  |  | 200 | 380 | 480 | 0.4992 | 0.9984 | 1.4976 | 2.496 | 3.744 | 4.992 | 94 | 95.6 | 96.5 | 97 | 97 | 96.7 | 96.7 | 95.7 | 97.2 | 97.7 | 97.8 | 97.7 | 97.3 | 97.6 | 94.6 | 96.5 | 97.2 | 97.5 | 97.5 | 97.2 | 97.3 | 2018-03-01 | 2023-02-01
Delta Electronics | E6-TL-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4992 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 4.992 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.86 |  |  | 200 | 380 | 480 | 0.4992 | 0.9984 | 1.4976 | 2.496 | 3.744 | 4.992 | 94.0016 | 95.6485 | 96.4705 | 97.0318 | 96.9884 | 96.6789 | 96.7334 | 95.696 | 97.2204 | 97.6522 | 97.8362 | 97.6671 | 97.3491 | 97.5837 | 94.6317 | 96.517 | 97.1735 | 97.5416 | 97.4711 | 97.1739 | 97.274 | 2018-08-01 | 2024-04-02
Delta Electronics | E6_BDI {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4992 W, 208 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 5.025 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 3.07 |  |  | 280 | 380 | 480 | 0.50521 | 1.0104 | 1.5156 | 2.5261 | 3.7891 | 5.0521 | 94.108 | 96.4743 | 96.8432 | 97.2485 | 97.2693 | 96.4695 | 97.0076 | 94.1138 | 96.5094 | 97.1953 | 97.5538 | 97.5799 | 97.5277 | 97.3335 | 92.1224 | 95.6496 | 96.6604 | 97.2666 | 97.3945 | 97.3385 | 96.9786 | 2022-06-01 | 2024-04-02
Delta Electronics | SOLIVIA 5.2 NA G4 TL {208V} | N | N | Y | Y | Y | Y | Y* | Y | 5200 W, 208 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 5.2 | 208 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [10/15/2020] | [02.05.01] | 2018-10-15 | [10/15/2020] | 2020-11-12 | Intertek | 2020-09-30 | 2020-11-12 |  | Y | N | 1.31 |  |  | 100 | 380 | 500 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 93.6 | 95.6 | 96.3 | 97.2 | 97.1 | 96.8 | 96.8 | 95.2 | 96.6 | 97.5 | 98 | 98 | 97.7 | 97.7 | 93.6 | 96.3 | 97 | 97.7 | 97.7 | 97.5 | 97.4 | 2017-10-16 | 2020-11-12
Delta Electronics | SOLIVIA 5.2 NA G4 TL {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5200 W, 240 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 5.2 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [10/15/2020] | [02.05.01] | 2018-10-15 | [10/15/2020] | 2020-11-12 | Intertek | 2020-09-30 | 2020-11-12 |  | Y | N | 1.42 |  |  | 100 | 380 | 500 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 94 | 95.8 | 96.4 | 97.3 | 97.4 | 97.1 | 97 | 95.2 | 97 | 97.5 | 98.2 | 98.3 | 98.1 | 98 | 93.8 | 96.6 | 97.2 | 97.9 | 98 | 98 | 97.7 | 2017-10-16 | 2020-11-12
Delta Electronics | E6-TL-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5760 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 5.76 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 2.25 |  |  | 200 | 380 | 480 | 0.576 | 1.152 | 1.728 | 2.88 | 4.32 | 5.76 | 93.9636 | 95.7324 | 96.5328 | 97.1183 | 97.0624 | 96.7746 | 96.8057 | 96.2574 | 97.615 | 97.9819 | 98.0814 | 97.6804 | 97.6267 | 97.738 | 95.2386 | 96.9825 | 97.5357 | 97.8342 | 97.7548 | 97.4585 | 97.5911 | 2018-08-01 | 2024-04-02
Delta Electronics | M6-TL-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 6000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter | 5.76 | 240 | 97.5 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 2.25 |  |  | 200 | 380 | 480 | 0.576 | 1.152 | 1.728 | 2.88 | 4.32 | 5.76 | 94 | 95.7 | 96.5 | 97.1 | 97.1 | 96.8 | 96.8 | 96.3 | 97.6 | 98 | 98.1 | 97.7 | 97.6 | 97.7 | 95.2 | 97 | 97.5 | 97.8 | 97.8 | 97.5 | 97.6 | 2018-03-01 | 2023-02-01
Delta Electronics | E6_BDI {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5760 W, 240 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 5.823 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 3.56 |  |  | 280 | 380 | 480 | 0.58227 | 1.1645 | 1.7468 | 2.9113 | 4.367 | 5.8227 | 94.3806 | 96.5167 | 97.113 | 97.2899 | 97.4038 | 97.3849 | 97.1788 | 95.1918 | 96.9824 | 97.6172 | 97.8772 | 97.8794 | 97.8499 | 97.6936 | 93.3812 | 96.121 | 97.0916 | 97.579 | 97.6894 | 97.6744 | 97.3429 | 2022-06-01 | 2024-04-02
Delta Electronics | SOLIVIA 6.6 NA G4 TL {208V} | N | N | Y | Y | Y | Y | Y* | Y | 6600 W, 208 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 6.6 | 208 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [10/15/2020] | [02.05.01] | 2018-10-15 | [10/15/2020] | 2020-11-12 | Intertek | 2020-09-30 | 2020-11-12 |  | Y | N | 1.23 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 96.8 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1 | 97.4 | 2017-10-16 | 2020-11-12
Delta Electronics | SOLIVIA 6.6 NA G4 TL {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6600W, 208Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 6.6 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [10/15/2020] | [02.05.01] | 2018-10-15 | [10/15/2020] | 2020-11-12 | Intertek | 2020-09-30 | 2020-11-12 |  | Y | N | 1.45 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.3 | 96.2 | 96.9 | 97.4 | 97.2 | 96.8 | 97 | 96 | 97.3 | 97.9 | 98.3 | 98.2 | 97.9 | 98 | 95 | 96.8 | 97.6 | 98 | 98 | 97.7 | 97.7 | 2017-10-16 | 2020-11-12
Delta Electronics | SOLIVIA 7.6 NA G4 TL {208V} | N | N | Y | Y | Y | Y | Y* | Y | 7600 W, 208 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 6.6 | 208 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [10/15/2020] | [02.05.01] | 2018-10-15 | [10/15/2020] | 2020-11-12 | Intertek | 2020-09-30 | 2020-11-12 |  | Y | N | 1.23 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 96.8 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1 | 97.4 | 2017-10-16 | 2020-11-12
Delta Electronics | E8-TL-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6656 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 6.656 | 208 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.15 |  |  | 270 | 380 | 480 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 95.2308 | 96.891 | 97.3835 | 97.6343 | 97.4276 | 97.0506 | 97.3322 | 95.9476 | 97.4104 | 97.7946 | 97.9487 | 97.6997 | 97.3918 | 97.6634 | 94.855 | 96.7763 | 97.3739 | 97.6604 | 97.5174 | 97.1621 | 97.3689 | 2018-08-01 | 2024-04-02
Delta Electronics | M8-TL-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 7296 W, 208 Vac transformerless Grid Support Utility Interactive Inverter | 6.66 | 208 | 97.5 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.15 |  |  | 270 | 380 | 480 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 95.2 | 96.9 | 97.4 | 97.6 | 97.4 | 97.1 | 97.3 | 95.9 | 97.4 | 97.8 | 97.9 | 97.7 | 97.4 | 97.7 | 94.9 | 96.8 | 97.4 | 97.7 | 97.5 | 97.2 | 97.4 | 2018-03-01 | 2023-02-01
Delta Electronics | E8 Plus-TL-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6656 W, 208 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 6.6768 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2023-02-01 | [6/2/2022] | 2023-02-01 | CSA Group | 2022-11-25 | 2023-02-01 |  | N | N | 3.22 |  |  | 280 | 380 | 480 | 0.66768 | 1.3354 | 2.003 | 3.3384 | 5.0076 | 6.6768 | 94.1111 | 96.1543 | 96.4098 | 96.628 | 96.563 | 96.3234 | 96.4278 | 95.4902 | 97.0363 | 97.4287 | 97.5565 | 97.4235 | 97.3169 | 97.35 | 94.0635 | 96.4144 | 97.0161 | 97.3508 | 97.3059 | 97.1682 | 97.0994 | 2023-02-01 | 2024-04-02
Delta Electronics | E8_BDI {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6656 W, 208 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 6.677 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 3.22 |  |  | 280 | 380 | 480 | 0.66768 | 1.3354 | 2.003 | 3.3384 | 5.0076 | 6.6768 | 94.1111 | 96.1543 | 96.4098 | 96.628 | 96.563 | 96.3234 | 96.4278 | 95.4902 | 97.0363 | 97.4287 | 97.5565 | 97.4235 | 97.3169 | 97.35 | 94.0635 | 96.4144 | 97.0161 | 97.3508 | 97.3059 | 97.1682 | 97.0994 | 2022-06-01 | 2024-04-02
Delta Electronics | SOLIVIA 7.6 NA G4 TL {240V} | N | N | Y | Y | Y | Y | Y* | Y | 7600 W, 240 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 7.6 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [10/15/2020] | [02.05.01] | 2018-10-15 | [10/15/2020] | 2020-11-12 | Intertek | 2020-09-30 | 2020-11-12 |  | Y | N | 1.43 |  |  | 100 | 380 | 500 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95 | 96.4 | 97.3 | 97.4 | 97 | 96.4 | 97 | 96.3 | 97.4 | 98.1 | 98.3 | 98 | 97.7 | 98 | 95.5 | 97.2 | 97.7 | 98 | 97.9 | 97.5 | 97.7 | 2017-10-16 | 2020-11-12
Delta Electronics | E8-TL-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 7.68 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.19 |  |  | 270 | 380 | 480 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.2202 | 96.7865 | 97.3605 | 97.6615 | 97.5147 | 97.0633 | 97.3763 | 96.5571 | 97.7682 | 98.0917 | 98.1644 | 97.9971 | 97.6404 | 97.9567 | 95.5533 | 97.2136 | 97.7339 | 97.9476 | 97.8481 | 97.5018 | 97.7144 | 2018-08-01 | 2024-04-02
Delta Electronics | M8-TL-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 8000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter | 7.68 | 240 | 97.5 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.19 |  |  | 270 | 380 | 480 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.2 | 96.8 | 97.4 | 97.7 | 97.5 | 97.1 | 97.4 | 96.6 | 97.8 | 98.1 | 98.2 | 98 | 97.6 | 98 | 95.6 | 97.2 | 97.7 | 97.9 | 97.8 | 97.5 | 97.7 | 2018-03-01 | 2023-02-01
Delta Electronics | E8 Plus-TL-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7680 W, 240 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 7.716 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2023-02-01 | [6/2/2022] | 2023-02-01 | CSA Group | 2022-11-25 | 2023-02-01 |  | N | N | 2.72 |  |  | 280 | 380 | 480 | 0.7716 | 1.5432 | 2.3148 | 3.858 | 5.787 | 7.716 | 94.8576 | 96.6091 | 96.812 | 97.0141 | 96.9294 | 96.6893 | 96.8222 | 96.1358 | 97.4848 | 97.7923 | 97.8646 | 97.7763 | 97.6446 | 97.71 | 92.947 | 96.8614 | 97.4026 | 97.6609 | 97.6155 | 97.5054 | 97.3695 | 2023-02-01 | 2024-04-02
Delta Electronics | E8_BDI {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7680 W, 240 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 7.716 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 2.72 |  |  | 280 | 380 | 480 | 0.7716 | 1.5432 | 2.3148 | 3.858 | 5.787 | 7.716 | 94.8576 | 96.6091 | 96.812 | 97.0141 | 96.9294 | 96.6893 | 96.8222 | 96.1358 | 97.4848 | 97.7923 | 97.8646 | 97.7763 | 97.6446 | 97.71 | 92.947 | 96.8614 | 97.4026 | 97.6609 | 97.6155 | 97.5054 | 97.3695 | 2022-06-01 | 2024-04-02
Delta Electronics | M10-TL-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 208 Vac Transformerless, Bi-directional Grid Support Utility Interactive Inverter | 8.36 | 208 | 97.5 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2019-05-15 | [6/2/2022] | 2020-02-11 | CSA Group | 2022-11-25 | 2020-02-11 |  | Y | N | 1.35 |  |  | 280 | 380 | 480 | 0.836 | 1.672 | 2.508 | 4.18 | 6.27 | 8.36 | 95.6582 | 97.2037 | 97.6275 | 97.6939 | 97.3331 | 96.7189 | 97.34 | 96.1037 | 97.4684 | 97.8423 | 97.88 | 97.4815 | 96.939 | 97.5256 | 95.3231 | 96.9699 | 97.4951 | 97.6758 | 97.379 | 96.7989 | 97.3235 | 2019-05-15 | 2023-02-01
Delta Electronics | M10-4-TL-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 8320 W, 208 Vac transformerless Grid Support Utility Interactive Inverter | 8.385 | 208 | 97.5 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2020-08-11 | [6/2/2022] | 2020-08-11 | CSA Group | 2022-11-25 | 2020-08-11 |  | Y | N | 1.35 |  |  | 280 | 350 | 480 | 0.83848 | 1.677 | 2.5154 | 4.1924 | 6.2886 | 8.3848 | 95.9763 | 97.0349 | 97.2944 | 97.3825 | 97.18 | 96.8443 | 97.164 | 96.735 | 97.5607 | 97.6985 | 97.6022 | 97.3608 | 97.0685 | 97.4224 | 95.5251 | 96.9805 | 97.3434 | 97.441 | 97.2115 | 96.9273 | 97.1823 | 2020-08-11 | 2023-02-01
Delta Electronics | E10_BDI {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8320 W, 208 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 8.4 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.35 |  |  | 280 | 380 | 480 | 0.83996 | 1.6799 | 2.5199 | 4.1998 | 6.2997 | 8.3996 | 95.9763 | 97.0349 | 97.2944 | 97.3825 | 97.18 | 96.8443 | 97.164 | 96.7105 | 97.4869 | 97.6286 | 97.5273 | 97.1983 | 96.819 | 97.295 | 95.5251 | 96.9805 | 97.3434 | 97.441 | 97.2115 | 96.9273 | 97.1823 | 2022-06-01 | 2024-04-02
Delta Electronics | E10-TL-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8320 W, 208 Vac, transformerless Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 8.4 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.35 |  |  | 280 | 380 | 480 | 0.83996 | 1.6799 | 2.5199 | 4.1998 | 6.2997 | 8.3996 | 95.9763 | 97.0349 | 97.2944 | 97.3825 | 97.18 | 96.8443 | 97.164 | 96.7105 | 97.4869 | 97.6286 | 97.5273 | 97.1983 | 96.819 | 97.295 | 95.5251 | 96.9805 | 97.3434 | 97.441 | 97.2115 | 96.9273 | 97.1823 | 2022-06-01 | 2024-04-02
Delta Electronics | M10-TL-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac Transformerless, Bi-directional Grid Support Utility Interactive Inverter | 9.62 | 240 | 97.5 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2019-05-15 | [6/2/2022] | 2020-02-11 | CSA Group | 2022-11-25 | 2020-02-11 |  | Y | N | 1.41 |  |  | 280 | 380 | 480 | 0.96203 | 1.9241 | 2.8861 | 4.8101 | 7.2152 | 9.6203 | 95.8434 | 97.2454 | 97.6952 | 97.7815 | 97.4547 | 96.8686 | 97.448 | 96.6236 | 97.7885 | 98.0915 | 98.1079 | 97.7286 | 97.0794 | 97.7781 | 95.9166 | 97.3593 | 97.8019 | 97.9562 | 97.6575 | 97.2218 | 97.6313 | 2019-05-15 | 2023-02-01
Delta Electronics | E10_BDI {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9600 W, 240 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 9.674 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.38 |  |  | 280 | 380 | 480 | 0.96742 | 1.9348 | 2.9023 | 4.8371 | 7.2557 | 9.6742 | 96.0741 | 97.0988 | 97.3615 | 97.4925 | 97.321 | 96.9976 | 97.2847 | 97.044 | 97.7732 | 97.9269 | 97.8348 | 97.6061 | 97.3666 | 97.6665 | 96.1551 | 97.378 | 97.6757 | 97.7252 | 97.497 | 97.2601 | 97.4949 | 2022-06-01 | 2024-04-02
Delta Electronics | E10-TL-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9600 W, 240 Vac, transformerless Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 9.674 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.38 |  |  | 280 | 380 | 480 | 0.96742 | 1.9348 | 2.9023 | 4.8371 | 7.2557 | 9.6742 | 96.0741 | 97.0988 | 97.3615 | 97.4925 | 97.321 | 96.9976 | 97.2847 | 97.044 | 97.7732 | 97.9269 | 97.8348 | 97.6061 | 97.3666 | 97.6665 | 96.1551 | 97.378 | 97.6757 | 97.7252 | 97.497 | 97.2601 | 97.4949 | 2022-06-01 | 2024-04-02
Delta Electronics | M10-4-TL-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 9600 W, 240 Vac transformerless Grid Support Utility Interactive Inverter | 9.674 | 240 | 97.5 | CSA Group | [6/2/2022] | CSA Group | [6/2/2022] | [1.6.2] | 2020-08-11 | [6/2/2022] | 2020-08-11 | CSA Group | 2022-11-25 | 2020-08-11 |  | Y | N | 1.38 |  |  | 280 | 380 | 480 | 0.96742 | 1.9348 | 2.9023 | 4.8371 | 7.2557 | 9.6742 | 96.0741 | 97.0988 | 97.3615 | 97.4925 | 97.321 | 96.9976 | 97.2847 | 97.044 | 97.7732 | 97.9269 | 97.8348 | 97.6061 | 97.3666 | 97.6665 | 96.1551 | 97.378 | 97.6757 | 97.7252 | 97.497 | 97.2601 | 97.4949 | 2020-08-11 | 2023-02-01
Delta Electronics | S12_BDI {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.984 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 10.0568 | 208 | 97 | CSA Group | [5/6/2024] | CSA Group | [5/6/2024] | [01.00.17] | 2024-08-12 | [5/6/2024] | 2024-08-12 | CSA Group | 2023-11-01 | 2024-06-11 |  | N | N | 16.23 |  |  | 200 | 380 | 480 | 1.0057 | 2.0114 | 3.017 | 5.0284 | 7.5426 | 10.0568 | 94.5201 | 96.389 | 96.8997 | 96.9415 | 96.5333 | 95.9709 | 96.5472 | 95.9899 | 97.4283 | 97.7143 | 97.6655 | 97.2997 | 96.965 | 97.3636 | 95.4895 | 97.1344 | 97.5396 | 97.6477 | 97.4208 | 96.8726 | 97.3637 | 2024-06-11 | 2024-08-12
Delta Electronics | S12_BDI {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.520 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.5886 | 240 | 97.5 | CSA Group | [5/6/2024] | CSA Group | [5/6/2024] | [01.00.17] | 2024-08-12 | [5/6/2024] | 2024-08-12 | CSA Group | 2023-11-01 | 2024-06-11 |  | N | N | 16.48 |  |  | 200 | 380 | 480 | 1.1589 | 2.3177 | 3.4766 | 5.7943 | 8.6914 | 11.5886 | 94.7826 | 96.6129 | 97.0546 | 97.1271 | 96.6484 | 96.0211 | 96.6899 | 96.5172 | 97.7857 | 97.9547 | 97.9185 | 97.5962 | 97.3165 | 97.6593 | 96.0248 | 97.4984 | 97.8115 | 97.8312 | 97.6456 | 97.2776 | 97.6139 | 2024-06-11 | 2024-08-12
Delta Electronics | M24U_120 {480V} | N | N | Y | Y | Y | Y | N | N | 24 kW, 480 Vac Grid Support Utility Interactive Inverter | 26.403 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.6 |  |  | 415 | 710 | 830 | 2.64 | 5.28 | 7.92 | 13.2 | 19.8 | 26.4 | 95.28 | 96.42 | 97.03 | 97.41 | 97.46 | 97.3 | 97.25 | 97.39 | 98.27 | 98.56 | 98.65 | 98.65 | 98.57 | 98.57 | 96.51 | 97.77 | 98.06 | 98.35 | 98.36 | 98.27 | 98.21 | 2017-12-15 | 2020-03-02
Delta Electronics | M24U_121 {480V} | N | N | Y | Y | Y | Y | N | N | 24 kW, 480 Vac Grid Support Utility Interactive Inverter | 26.403 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.6 |  |  | 415 | 710 | 830 | 2.64 | 5.28 | 7.92 | 13.2 | 19.8 | 26.4 | 95.28 | 96.42 | 97.03 | 97.41 | 97.46 | 97.3 | 97.25 | 97.39 | 98.27 | 98.56 | 98.65 | 98.65 | 98.57 | 98.57 | 96.51 | 97.77 | 98.06 | 98.35 | 98.36 | 98.27 | 98.21 | 2017-12-15 | 2020-03-02
Delta Electronics | M24U_122 {480V} | N | N | Y | Y | Y | Y | N | N | 24 kW, 480 Vac Grid Support Utility Interactive Inverter | 26.403 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.6 |  |  | 415 | 710 | 830 | 2.64 | 5.28 | 7.92 | 13.2 | 19.8 | 26.4 | 95.28 | 96.42 | 97.03 | 97.41 | 97.46 | 97.3 | 97.25 | 97.39 | 98.27 | 98.56 | 98.65 | 98.65 | 98.57 | 98.57 | 96.51 | 97.77 | 98.06 | 98.35 | 98.36 | 98.27 | 98.21 | 2017-12-15 | 2020-03-02
Delta Electronics | E30-TL {277V} | Y | N | Y | Y | Y | N | N | N | 30 kW, 277 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 30.488 | 277 | 98 | No Information Submitted | No Information Submitted | CSA Group | [07/01/2019] | [Controller A: V1.1.3, Controller B: V1.1.1] | 2019-08-01 | [07/01/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1.59 |  |  | 515 | 750 | 830 | 3.0488 | 6.0975 | 9.1463 | 15.2438 | 22.8657 | 30.4876 | 95.9222 | 97.1353 | 97.5449 | 97.7515 | 97.701 | 97.4796 | 97.5823 | 97.4461 | 98.3209 | 98.5555 | 98.6266 | 98.581 | 98.4647 | 98.5233 | 96.9725 | 98.1055 | 98.382 | 98.4809 | 98.4516 | 98.3166 | 98.3662 | 2019-08-01
Delta Electronics | M28U_120 {480V} | N | N | Y | Y | Y | Y | N | N | 28 kW, 480 Vac Grid Support Utility Interactive Inverter | 30.709 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.4 |  |  | 485 | 710 | 830 | 3.07 | 6.14 | 9.21 | 15.35 | 23.03 | 30.71 | 95.98 | 97.06 | 97.64 | 97.78 | 97.74 | 97.52 | 97.62 | 97.67 | 98.38 | 98.6 | 98.65 | 98.6 | 98.49 | 98.56 | 96.9 | 97.95 | 98.21 | 98.35 | 98.32 | 98.18 | 98.23 | 2017-12-15 | 2020-03-02
Delta Electronics | M28U_121 {480V} | N | N | Y | Y | Y | Y | N | N | 28 kW, 480 Vac Grid Support Utility Interactive Inverter | 30.709 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.4 |  |  | 485 | 710 | 830 | 3.07 | 6.14 | 9.21 | 15.35 | 23.03 | 30.71 | 95.98 | 97.06 | 97.64 | 97.78 | 97.74 | 97.52 | 97.62 | 97.67 | 98.38 | 98.6 | 98.65 | 98.6 | 98.49 | 98.56 | 96.9 | 97.95 | 98.21 | 98.35 | 98.32 | 98.18 | 98.23 | 2017-12-15 | 2020-03-02
Delta Electronics | M28U_122 {480V} | N | N | Y | Y | Y | Y | N | N | 28 kW, 480 Vac Grid Support Utility Interactive Inverter | 30.709 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.4 |  |  | 485 | 710 | 830 | 3.07 | 6.14 | 9.21 | 15.35 | 23.03 | 30.71 | 95.98 | 97.06 | 97.64 | 97.78 | 97.74 | 97.52 | 97.62 | 97.67 | 98.38 | 98.6 | 98.65 | 98.6 | 98.49 | 98.56 | 96.9 | 97.95 | 98.21 | 98.35 | 98.32 | 98.18 | 98.23 | 2017-12-15 | 2020-03-02
Delta Electronics | M36U_120 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac Grid Support Utility Interactive Inverter | 39.737 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | CSA Group | 2020-10-07 | 2020-11-12 |  | N | N | 2.9 |  |  | 520 | 710 | 830 | 3.97 | 7.95 | 11.92 | 19.87 | 29.8 | 39.74 | 96.36 | 97.47 | 97.83 | 97.97 | 97.81 | 97.59 | 97.76 | 97.75 | 98.45 | 98.6 | 98.6 | 98.43 | 98.28 | 98.45 | 96.89 | 97.92 | 98.22 | 98.3 | 98.16 | 97.95 | 98.12 | 2017-12-15 | 2020-11-12
Delta Electronics | M36U_121 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac Grid Support Utility Interactive Inverter | 39.737 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | CSA Group | 2020-10-07 | 2020-04-21 |  | N | N | 2.9 |  |  | 520 | 710 | 830 | 3.97 | 7.95 | 11.92 | 19.87 | 29.8 | 39.74 | 96.36 | 97.47 | 97.83 | 97.97 | 97.81 | 97.59 | 97.76 | 97.75 | 98.45 | 98.6 | 98.6 | 98.43 | 98.28 | 98.45 | 96.89 | 97.92 | 98.22 | 98.3 | 98.16 | 97.95 | 98.12 | 2017-12-15 | 2020-11-12
Delta Electronics | M36U_122 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac Grid Support Utility Interactive Inverter | 39.737 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | CSA Group | 2020-10-07 | 2020-11-12 |  | N | N | 2.9 |  |  | 520 | 710 | 830 | 3.97 | 7.95 | 11.92 | 19.87 | 29.8 | 39.74 | 96.36 | 97.47 | 97.83 | 97.97 | 97.81 | 97.59 | 97.76 | 97.75 | 98.45 | 98.6 | 98.6 | 98.43 | 98.28 | 98.45 | 96.89 | 97.92 | 98.22 | 98.3 | 98.16 | 97.95 | 98.12 | 2017-12-15 | 2020-11-12
Delta Electronics | M42U_120 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 42 kW, 480 Vac Grid Support Utility Interactive Inverter | 45.972 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | CSA Group | 2020-10-07 | 2020-11-12 |  | N | N | 2.9 |  |  | 545 | 710 | 830 | 4.6 | 9.19 | 13.79 | 22.99 | 34.48 | 45.97 | 96.83 | 97.76 | 97.97 | 98.02 | 97.8 | 97.54 | 97.81 | 97.98 | 98.53 | 98.6 | 98.55 | 98.35 | 98.16 | 98.41 | 97.21 | 98.04 | 98.26 | 98.26 | 98.07 | 97.86 | 98.09 | 2017-12-15 | 2020-11-12
Delta Electronics | M42U_121 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 42 kW, 480 Vac Grid Support Utility Interactive Inverter | 45.972 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | CSA Group | 2020-10-07 | 2020-04-21 |  | N | N | 2.9 |  |  | 545 | 710 | 830 | 4.6 | 9.19 | 13.79 | 22.99 | 34.48 | 45.97 | 96.83 | 97.76 | 97.97 | 98.02 | 97.8 | 97.54 | 97.81 | 97.98 | 98.53 | 98.6 | 98.55 | 98.35 | 98.16 | 98.41 | 97.21 | 98.04 | 98.26 | 98.26 | 98.07 | 97.86 | 98.09 | 2017-12-15 | 2020-11-12
Delta Electronics | M42U_122 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 42 kW, 480 Vac Grid Support Utility Interactive Inverter | 45.972 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | [03/11/2019] | 2020-03-02 | CSA Group | 2020-10-07 | 2020-11-12 |  | N | N | 2.9 |  |  | 545 | 710 | 830 | 4.6 | 9.19 | 13.79 | 22.99 | 34.48 | 45.97 | 96.83 | 97.76 | 97.97 | 98.02 | 97.8 | 97.54 | 97.81 | 97.98 | 98.53 | 98.6 | 98.55 | 98.35 | 98.16 | 98.41 | 97.21 | 98.04 | 98.26 | 98.26 | 98.07 | 97.86 | 98.09 | 2017-12-15 | 2020-11-12
Delta Electronics | M60U_260 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 66 kW, 480 Vac, Grid Support Utility Interactive Inverter | 59.012 | 480 | 98 | Intertek | [8/31/2022] | Intertek | [1/14/2022] | [1.1X, 1.2X, 1.3X, 1.4X, 1.5X, 1.6X, 1.7X, 1.8X, 1.9X] | 2022-06-01 | [1/14/2022] | 2022-06-01 | CSA Group | 2022-04-12 | 2022-06-01 |  | N | N | 3.05 |  |  | 390 | 710 | 900 | 5.9012 | 11.8024 | 17.7036 | 29.506 | 44.259 | 59.012 | 94.37 | 96.26 | 97.17 | 97.98 | 98.17 | 98.13 | 97.7606 | 96.834 | 97.216 | 98.42 | 98.582 | 98.542 | 98.432 | 98.3956 | 94.07 | 96.428 | 97.158 | 97.56 | 97.622 | 97.698 | 97.3553 | 2022-06-01 | 2024-11-01
Delta Electronics | M60U_280 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 60.019 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/9/2021] | [1.1X, 1.2X, 1.3X, 1.4X, 1.5X, 1.6X, 1.1X, 1.2X, 1.3X, 1.4X, 1.5X, 1.6X, 1.1X, 1.2X, 1.3X, 1.4X, 1.5X, 1.6X] | 2022-05-11 | [12/9/2021] | 2022-05-11 | CSA Group | 2020-10-07 | 2022-05-11 |  | N | N | 3.05 |  |  | 550 | 710 | 840 | 6.0019 | 12.0038 | 18.0057 | 30.0095 | 45.0142 | 60.019 | 96.394 | 97.792 | 98.18 | 98.53 | 98.606 | 98.468 | 98.4028 | 96.534 | 98.058 | 98.4712 | 98.748 | 98.722 | 98.644 | 98.5727 | 95.184 | 97.278 | 97.946 | 98.33 | 98.472 | 98.4 | 98.1842 | 2022-05-11
Delta Electronics | M60U_120 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 65.47 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/21/2020] | [V1.47, V1.5X, V1.6X, V1.7X, V1.8X] | 2018-10-15 | [01/21/2020] | 2020-02-11 | CSA Group | 2020-10-07 | 2020-11-12 |  | N | N | 2.863 |  |  | 540 | 710 | 800 | 6.55 | 13.09 | 19.64 | 32.74 | 49.1 | 65.47 | 96.77 | 97.69 | 97.62 | 98.1 | 98.02 | 97.46 | 97.89 | 98.52 | 98.59 | 98.63 | 98.71 | 98.46 | 98.29 | 98.54 | 97.76 | 98.59 | 98.41 | 98.51 | 98.32 | 98.14 | 98.35 | 2017-12-15 | 2020-11-12
Delta Electronics | M60U_121 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 65.47 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/21/2020] | [V1.47, V1.5X, V1.6X, V1.7X, V1.8X] | 2018-10-15 | [01/21/2020] | 2020-02-11 | CSA Group | 2020-10-07 | 2020-04-21 |  | N | N | 2.863 |  |  | 540 | 710 | 800 | 6.55 | 13.09 | 19.64 | 32.74 | 49.1 | 65.47 | 96.77 | 97.69 | 97.62 | 98.1 | 98.02 | 97.46 | 97.89 | 98.52 | 98.59 | 98.63 | 98.71 | 98.46 | 98.29 | 98.54 | 97.76 | 98.59 | 98.41 | 98.51 | 98.32 | 98.14 | 98.35 | 2017-12-15 | 2020-11-12
Delta Electronics | M60U_122 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 65.47 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/21/2020] | [V1.47, V1.5X, V1.6X, V1.7X, V1.8X] | 2018-10-15 | [01/21/2020] | 2020-02-11 | CSA Group | 2020-10-07 | 2020-11-12 |  | N | N | 2.863 |  |  | 540 | 710 | 800 | 6.55 | 13.09 | 19.64 | 32.74 | 49.1 | 65.47 | 96.77 | 97.69 | 97.62 | 98.1 | 98.02 | 97.46 | 97.89 | 98.52 | 98.59 | 98.63 | 98.71 | 98.46 | 98.29 | 98.54 | 97.76 | 98.59 | 98.41 | 98.51 | 98.32 | 98.14 | 98.35 | 2017-12-15 | 2020-11-12
Delta Electronics | M80U_280 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 83 kW, 480 Vac Grid Support Utility Interactive Inverter | 80.023 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/9/2021] | [1.1X, 1.2X, 1.3X, 1.4X, 1.5X, 1.6X, 1.1X, 1.2X, 1.3X, 1.4X, 1.5X, 1.6X, 1.1X, 1.2X, 1.3X, 1.4X, 1.5X, 1.6X] | 2022-05-11 | [12/9/2021] | 2022-05-11 | CSA Group | 2020-10-07 | 2022-05-11 |  | N | N | 3.05 |  |  | 550 | 710 | 840 | 8.0023 | 16.0046 | 24.0069 | 40.0115 | 60.0172 | 80.023 | 97.076 | 98.04 | 98.418 | 98.648 | 98.572 | 98.288 | 98.4688 | 97.26 | 98.354 | 98.658 | 98.776 | 98.658 | 98.43 | 98.6003 | 96.04 | 97.662 | 98.192 | 98.414 | 98.362 | 98.142 | 98.2136 | 2022-05-11
Delta Electronics | M80U_120 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 80 kW, 480 Vac Grid Support Utility Interactive Inverter | 82.764 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/21/2020] | [V1.47, V1.5X, V1.6X, V1.7X, V1.8X] | 2018-10-15 | [01/21/2020] | 2020-02-11 | CSA Group | 2020-10-07 | 2020-11-12 |  | N | N | 2.6 |  |  | 600 | 710 | 800 | 8.28 | 16.55 | 24.83 | 41.38 | 62.07 | 82.76 | 97.48 | 98.39 | 98.4 | 98.22 | 97.97 | 97.79 | 98.06 | 98.31 | 98.79 | 98.85 | 98.69 | 98.54 | 98.18 | 98.59 | 98.37 | 98.68 | 98.69 | 98.49 | 98.23 | 98.09 | 98.36 | 2017-12-15 | 2020-11-12
Delta Electronics | M80U_121 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 80 kW, 480 Vac Grid Support Utility Interactive Inverter | 82.764 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/21/2020] | [V1.47, V1.5X, V1.6X, V1.7X, V1.8X] | 2018-10-15 | [01/21/2020] | 2020-02-11 | CSA Group | 2020-10-07 | 2020-04-21 |  | N | N | 2.6 |  |  | 600 | 710 | 800 | 8.28 | 16.55 | 24.83 | 41.38 | 62.07 | 82.76 | 97.48 | 98.39 | 98.4 | 98.22 | 97.97 | 97.79 | 98.06 | 98.31 | 98.79 | 98.85 | 98.69 | 98.54 | 98.18 | 98.59 | 98.37 | 98.68 | 98.69 | 98.49 | 98.23 | 98.09 | 98.36 | 2017-12-15 | 2020-11-12
Delta Electronics | M80U_122 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 80 kW, 480 Vac Grid Support Utility Interactive Inverter | 82.764 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/21/2020] | [V1.47, V1.5X, V1.6X, V1.7X, V1.8X] | 2018-10-15 | [01/21/2020] | 2020-02-11 | CSA Group | 2020-10-07 | 2020-11-12 |  | N | N | 2.6 |  |  | 600 | 710 | 800 | 8.28 | 16.55 | 24.83 | 41.38 | 62.07 | 82.76 | 97.48 | 98.39 | 98.4 | 98.22 | 97.97 | 97.79 | 98.06 | 98.31 | 98.79 | 98.85 | 98.69 | 98.54 | 98.18 | 98.59 | 98.37 | 98.68 | 98.69 | 98.49 | 98.23 | 98.09 | 98.36 | 2017-12-15 | 2020-11-12
Delta Electronics | M100U_280 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac Grid Support Utility Interactive Inverter | 99.975 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/9/2021] | [1.1X, 1.2X, 1.3X, 1.4X, 1.5X, 1.6X, 1.1X, 1.2X, 1.3X, 1.4X, 1.5X, 1.6X, 1.1X, 1.2X, 1.3X, 1.4X, 1.5X, 1.6X] | 2022-05-11 | [12/9/2021] | 2022-05-11 | CSA Group | 2020-10-07 | 2022-05-11 |  | N | N | 3.05 |  |  | 550 | 710 | 840 | 9.9975 | 19.995 | 29.9925 | 49.9875 | 74.9812 | 99.975 | 98.386 | 98.53 | 98.664 | 98.414 | 98.158 | 97.874 | 98.286 | 98.428 | 98.946 | 98.746 | 98.574 | 98.378 | 98.136 | 98.4816 | 97.658 | 98.446 | 98.6 | 98.42 | 98.258 | 97.844 | 98.2978 | 2022-05-11
Delta Electronics | M125HV {600V} | N | N | Y | Y | Y | Y | Y* | Y | 125 kw, 600 Vac Grid Support Utility Interactive Inverter | 124.468 | 600 | 99 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/25/2019] | [DSP: 1.15, RED: 1.12, COMM: 1.2, ARC: 1.12, SCM: 1.12] | 2019-05-01 | [03/25/2019] | 2020-06-01 | CSA Group | 2020-10-07 | 2020-11-12 |  | N | N | 0 |  |  | 860 | 1000 | 1200 | 12.4468 | 24.8937 | 37.3405 | 62.2342 | 93.3513 | 124.4684 | 98.918 | 99.156 | 99.1897 | 99.102 | 98.848 | 98.528 | 98.9445 | 98.3448 | 98.786 | 98.866 | 98.9082 | 98.8042 | 98.344 | 98.7912 | 97.694 | 98.374 | 98.5076 | 98.648 | 98.5836 | 98.2445 | 98.525 | 2019-05-01 | 2020-11-12
Delta Electronics | DP350U-US-XX {800V} | N | Y | Y | Y | Y | N | N |  | 350 kW, 800 Vac Grid Support Utility Interactive Inverter | 352.401 | 800 | 98.5 | CSA Group | [12/16/2025] | CSA Group | [12/16/2025] | [V1.01, V1.03] | 2026-03-11 | [12/16/2025] | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 8.64 |  |  | 850 | 1150 | 1330 | 35.24 | 70.48 | 105.72 | 176.2 | 264.3 | 352.401 | 97.24 | 98.04 | 98.37 | 98.49 | 98.33 | 98.03 | 98.3 | 98.71 | 99.09 | 99.16 | 99.12 | 98.94 | 98.7 | 98.99 | 98.08 | 98.76 | 98.94 | 98.95 | 98.8 | 98.55 | 98.81 | 2026-03-11
Destin Power Inc. | SAVEEN1000-ES02H.US {440V} | N | N | Y | N | N | N | N | N | 1000 kW, 440 Vac, Grid Support Utility Interactive Inverter ESS for Indoor ESS PCS | 1000 | 440 | 98 | No Information Submitted | No Information Submitted | TUV SUD America | [01/11/2018] | [1.00.4] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 3 kVA ABB Korea distribution transformer. | N | N | 149.25 |  |  | 740 | 830 | 900 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.9762 | 97.2102 | 97.9516 | 98.4084 | 98.507 | 98.421 | 98.2093 | 94.252 | 96.7644 | 97.5816 | 98.1856 | 98.3254 | 98.2608 | 97.9626 | 93.5872 | 96.4774 | 97.3838 | 98.0058 | 98.2088 | 98.1694 | 97.7938 | 2018-11-01
Dyness Digital Energy Technology Co., LTD. | TX5K-HM {240V} | Y | Y | N | N | N | N | Y* | Y | 5kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment with PCS functionality | 5.02 | 240 | 96.5 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.13 |  |  | 180 | 390 | 500 | 0.50196 | 1.0039 | 1.5059 | 2.5098 | 3.7647 | 5.0196 | 94.3948 | 95.1559 | 95.9225 | 96.4043 | 96.1781 | 95.982 | 96.0627 | 95.6471 | 95.6407 | 96.5546 | 97.0291 | 97.2939 | 97.4239 | 97.0075 | 94.6422 | 95.0472 | 96.6033 | 97.424 | 97.4802 | 97.2415 | 97.1161 | 2023-12-21 | 2026-08-11 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Dyness Digital Energy Technology Co., LTD. | TX6K-HM {240V} | Y | Y | N | N | N | N | Y* | Y | 6kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment with PCS functionality | 6.018 | 240 | 97 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.12 |  |  | 210 | 390 | 500 | 0.60182 | 1.2036 | 1.8055 | 3.0091 | 4.5137 | 6.0182 | 92.6479 | 95.9948 | 96.4057 | 96.7027 | 96.4924 | 96.2024 | 96.333 | 93.9821 | 96.2752 | 96.9071 | 97.4028 | 97.411 | 97.3709 | 97.1529 | 91.4555 | 96.2207 | 97.4889 | 97.3222 | 97.4054 | 97.242 | 97.0925 | 2023-12-21 | 2026-08-11 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Dyness Digital Energy Technology Co., LTD. | TX7.6K-HM {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment with PCS functionality | 7.64 | 240 | 97 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.12 |  |  | 185 | 390 | 500 | 0.76402 | 1.528 | 2.2921 | 3.8201 | 5.7302 | 7.6402 | 95.2305 | 95.9104 | 96.3382 | 96.39 | 96.181 | 95.7506 | 96.1707 | 95.4068 | 96.4292 | 97.2246 | 97.2413 | 97.0365 | 97.244 | 97.0169 | 96.2864 | 96.8139 | 97.017 | 97.3106 | 97.2882 | 97.0989 | 97.1871 | 2023-12-21 | 2026-08-11 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Dyness Digital Energy Technology Co., LTD. | TX9.6K-HM {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment with PCS functionality | 9.648 | 240 | 96.5 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.14 |  |  | 170 | 390 | 500 | 0.96476 | 1.9295 | 2.8943 | 4.8238 | 7.2357 | 9.6476 | 94.8673 | 95.8966 | 96.2493 | 96.2284 | 95.8369 | 95.1616 | 95.899 | 95.3977 | 96.8238 | 96.9913 | 97.2596 | 96.9305 | 97.0122 | 96.9444 | 96.3825 | 97.453 | 97.2273 | 97.3321 | 97.3189 | 96.8944 | 97.2587 | 2023-12-21 | 2026-08-11 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Dyness Digital Energy Technology Co., LTD. | TX11.4K-HM {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment with PCS functionality | 11.498 | 240 | 96.5 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.13 |  |  | 200 | 390 | 500 | 1.1498 | 2.2996 | 3.4495 | 5.7491 | 8.6237 | 11.4982 | 95.0784 | 96.3007 | 96.5753 | 96.4491 | 96.0568 | 95.4541 | 96.1443 | 95.9408 | 96.9844 | 97.1686 | 97.3098 | 96.831 | 96.8025 | 96.9427 | 97.1581 | 97.7094 | 97.3526 | 97.3607 | 97.0294 | 96.6666 | 97.1588 | 2023-12-21 | 2026-08-11 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
EcoFlow Inc. | EF-PCS-24 {208V, 11.5kW} | Y | Y | N | N | N | N | Y* | Y | 11.5 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.4436 | 208 | 96 | SGS | [6/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-06-18 | 2025-08-11 |  | N | N | 115.89 |  |  | 120 | 370 | 480 | 1.1444 | 2.2887 | 3.4331 | 5.7218 | 8.5827 | 11.4436 | 92.506 | 94.602 | 94.35 | 96.164 | 95.27 | 95.384 | 95.2091 | 91.666 | 95.36 | 95.804 | 96.418 | 96.484 | 96.6 | 96.1454 | 91.85 | 95.408 | 96.364 | 96.98 | 97.104 | 97.006 | 96.6893 | 2025-08-11 | 2026-06-01 | N | Y | N | N | N | N | N | N | No Information Submitted
EcoFlow Inc. | EF-PCS-24 {240V, 11.5kW} | Y | Y | N | N | N | N | Y* | Y | 11.5 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.4442 | 240 | 96 | SGS | [6/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-06-18 | 2025-08-11 |  | N | N | 115.86 |  |  | 120 | 370 | 480 | 1.1444 | 2.2888 | 3.4333 | 5.7221 | 8.5832 | 11.4442 | 92.636 | 94.348 | 94.39 | 95.352 | 95.612 | 95.088 | 95.2023 | 91.72 | 94.64 | 95.876 | 96.482 | 96.608 | 96.79 | 96.2089 | 91.818 | 95.37 | 96.352 | 96.966 | 97.104 | 97.02 | 96.6824 | 2025-08-11 | 2026-06-01 | N | Y | N | N | N | N | N | N | No Information Submitted
EcoFlow Inc. | EF-PCS-24 {240V, 24kW} | Y | Y | N | N | N | N | Y* | Y | 24 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 24.0123 | 240 | 97 | SGS | [6/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-06-18 | 2025-08-11 |  | N | N | 117.14 |  |  | 320 | 400 | 480 | 2.4012 | 4.8025 | 7.2037 | 12.0062 | 18.0092 | 24.0123 | 94.74 | 96.484 | 97.044 | 96.952 | 96.8 | 96.472 | 96.7466 | 96.168 | 97.278 | 97.586 | 97.364 | 97.03 | 96.856 | 97.1361 | 95.304 | 96.724 | 97.242 | 97.44 | 97.262 | 96.942 | 97.1758 | 2025-08-11 | 2026-06-01 | N | Y | N | N | N | N | N | N | No Information Submitted
EcoFlow Inc. | EF-PCS-24 {208V, 24kW} | Y | Y | N | N | N | N | Y* | Y | 24 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 24.2914 | 208 | 96.5 | SGS | [6/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-06-18 | 2025-08-11 |  | N | N | 117.25 |  |  | 320 | 400 | 480 | 2.4291 | 4.8583 | 7.2874 | 12.1457 | 18.2185 | 24.2914 | 94.72 | 96.05 | 96.45 | 96.43 | 96.162 | 95.75 | 96.169 | 95.394 | 96.162 | 96.556 | 96.588 | 96.37 | 96.008 | 96.3706 | 95.09 | 96.7 | 97.03 | 96.99 | 96.684 | 96.272 | 96.7062 | 2025-08-11 | 2026-06-01 | N | Y | N | N | N | N | N | N | No Information Submitted
Eco-Worthy | ECO-INV-48V12KWSR01 {208V} | Y | Y | N | N | N | N | N |  | 10.4 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.397 | 208 | 96.5 | Intertek/ETL | [8/10/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.04 | 2.079 | 3.119 | 5.199 | 7.798 | 10.397 | 95.11 | 95.71 | 96.53 | 96.55 | 96.71 | 95.27 | 96.47 | 95.33 | 96.1 | 96.62 | 96.92 | 97.48 | 95.26 | 96.99 | 95.04 | 95.77 | 96.6 | 96.55 | 96.67 | 95.19 | 96.45 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Eco-Worthy | ECO-INV-48V12KWSR01 {240V} | Y | Y | N | N | N | N | N |  | 12 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.996 | 240 | 96.5 | Intertek/ETL | [8/10/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.2 | 2.399 | 3.599 | 5.998 | 8.997 | 11.996 | 95.45 | 95.69 | 96.38 | 96.39 | 96.5 | 95.23 | 96.32 | 95.57 | 96.17 | 96.69 | 96.87 | 97.43 | 95.23 | 96.98 | 95.53 | 95.87 | 96.6 | 96.46 | 96.54 | 95.32 | 96.39 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
EG4 Electronics LLC | IV-8000-HYB-AW {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 208 Vac Grid Support Hybrid 12kPV Inverter with PCS functionality. | 7.8599 | 208 | 96.5 | Intertek | [4/10/2024] | Intertek | [4/3/2025] | [EA1.0] | 2025-06-11 | [4/3/2025] | 2025-06-11 | Intertek | 2024-02-22 | 2024-06-21 |  | N | N | 18.53 |  |  | 210 | 360 | 480 | 0.78599 | 1.572 | 2.358 | 3.93 | 5.895 | 7.8599 | 92.7458 | 94.8821 | 95.7877 | 96.2814 | 95.7548 | 95.5452 | 95.6949 | 95.3183 | 96.7852 | 96.9298 | 97.2401 | 96.7733 | 96.6331 | 96.8255 | 94.866 | 96.387 | 96.7215 | 97.1053 | 96.6941 | 96.6144 | 96.6913 | 2024-06-21 | 2025-06-11
EG4 Electronics LLC | IV-8000-HYB-AW {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac Grid Support Hybrid 12kPV Inverter with PCS functionality. | 7.8627 | 240 | 96.5 | Intertek | [4/10/2024] | Intertek | [4/3/2025] | [EA1.0] | 2025-06-11 | [4/3/2025] | 2025-06-11 | Intertek | 2024-02-22 | 2024-06-21 |  | N | N | 18.84 |  |  | 210 | 360 | 480 | 0.78627 | 1.5725 | 2.3588 | 3.9313 | 5.897 | 7.8627 | 92.9578 | 94.8899 | 95.7481 | 96.2838 | 95.9702 | 95.8604 | 95.8294 | 95.5741 | 96.5787 | 96.6854 | 97.0389 | 96.7425 | 96.7486 | 96.7433 | 94.682 | 96.1785 | 96.6318 | 96.9367 | 96.7571 | 96.7998 | 96.67 | 2024-06-21 | 2025-06-11
EG4 Electronics LLC | 18KPV-12LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.4 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter (IV-12000-HYB-AW- may be followed by 00-99) with PCS functionality. | 10.499 | 208 | 96.5 | Intertek | [4/3/2025] | Intertek | [4/3/2025] | [fA1.0] | 2025-06-02 | [4/3/2025] | 2025-06-02 | Intertek | 2022-05-27 | 2024-02-21 |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.05 | 2.1 | 3.15 | 5.25 | 7.875 | 10.499 | 93.48 | 95.27 | 95.93 | 95.85 | 95.61 | 95.29 | 95.58 | 95.07 | 96.66 | 97.03 | 97.31 | 97.1 | 96.41 | 96.99 | 94.29 | 96.71 | 97.16 | 96.95 | 96.77 | 96.47 | 96.74 | 2023-06-21 | 2025-06-02
EG4 Electronics LLC | IV-13000-HYB-AW-FX-xx {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.3 kW, 208 Vac Grid Support Utility Interactive FlexBOSS18 Inverter, where xx = 00-99. Inverter with PCS functionality. | 11.325 | 208 | 97 | Intertek | [1/23/2025] | Intertek | [3/13/2025] | [fA1.0] | 2025-05-21 | [3/13/2025] | 2025-05-21 | Intertek | 2025-04-15 | 2025-06-23 |  | N | N | 31.95 |  |  | 250 | 360 | 440 | 1.133 | 2.265 | 3.398 | 5.663 | 8.494 | 11.325 | 96.29 | 96.28 | 96.21 | 96.25 | 96.23 | 96.33 | 96.24 | 96.07 | 96.94 | 97.19 | 97.71 | 97.5 | 96.64 | 97.38 | 95.73 | 97.68 | 97.82 | 98 | 97.11 | 97.31 | 97.36 | 2025-04-01 | 2025-06-23
EG4 Electronics LLC | 18KPV-12LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter (IV-12000-HYB-AW- may be followed by 00-99) with PCS functionality. | 11.933 | 240 | 97 | Intertek | [4/3/2025] | Intertek | [4/3/2025] | [fA1.0] | 2025-06-02 | [4/3/2025] | 2025-06-02 | Intertek | 2022-05-27 | 2024-02-21 |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.193 | 2.387 | 3.58 | 5.966 | 8.949 | 11.933 | 95.02 | 96.1 | 96.54 | 96.5 | 96.13 | 95.9 | 96.2 | 96.59 | 97.19 | 97.51 | 97.34 | 97.24 | 97.1 | 97.26 | 95.82 | 97.01 | 97.42 | 97.26 | 97.14 | 97.04 | 97.13 | 2023-06-21 | 2025-06-02
EG4 Electronics LLC | IV-13000-HYB-AW-FX-xx {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12.9 kW, 240 Vac Grid Support Utility Interactive FlexBOSS18 Inverter, where xx = 00-99. Inverter with PCS functionality. | 12.997 | 240 | 96.5 | Intertek | [1/23/2025] | Intertek | [3/13/2025] | [fA1.0] | 2025-05-21 | [3/13/2025] | 2025-05-21 | Intertek | 2025-04-15 | 2025-06-23 |  | N | N | 29.57 |  |  | 250 | 360 | 440 | 1.3 | 2.599 | 3.899 | 6.499 | 9.748 | 12.997 | 95.84 | 96.15 | 95.67 | 96.57 | 96.39 | 96.14 | 96.3 | 96.62 | 97.05 | 97.3 | 98.11 | 96.99 | 96.68 | 97.24 | 96.24 | 96.52 | 96.56 | 96.51 | 96.26 | 96.12 | 96.35 | 2025-04-01 | 2025-06-23
EG4 Electronics LLC | IV-16000-HYB-AW-FX-xx {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 13.8 kW, 208 Vac Grid Support Utility Interactive FlexBOSS21 Inverter, where xx = 00-99. Inverter with PCS functionality. | 13.8987 | 208 | 96.5 | Intertek | [10/23/2024] | Intertek | [3/13/2025] | [fA1.0] | 2025-05-21 | [3/13/2025] | 2025-05-21 | Intertek | 2025-04-15 | 2025-06-23 |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.3899 | 2.7797 | 4.1696 | 6.9494 | 10.424 | 13.8987 | 95.2216 | 96.3623 | 96.3314 | 96.3567 | 96.0039 | 95.9864 | 96.103 | 95.5416 | 96.5717 | 96.9718 | 97.1706 | 97.0713 | 96.2488 | 96.9529 | 95.5994 | 96.8339 | 97.3771 | 97.1744 | 97.0907 | 96.9737 | 97.0643 | 2025-01-02 | 2025-06-23
EG4 Electronics LLC | IV-16000-HYB-AW-FX-xx {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 16 kW, 240 Vac Grid Support Utility Interactive FlexBOSS21 Inverter, where xx = 00-99. Inverter with PCS functionality. | 16.1532 | 240 | 97 | Intertek | [10/23/2024] | Intertek | [3/13/2025] | [fA1.0] | 2025-05-21 | [3/13/2025] | 2025-05-21 | Intertek | 2025-04-15 | 2025-06-23 |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.6153 | 3.2306 | 4.846 | 8.0766 | 12.1149 | 16.1532 | 95.0963 | 95.9965 | 96.3882 | 96.4022 | 96.7311 | 95.8608 | 96.4752 | 96.4687 | 97.0976 | 97.478 | 97.1222 | 97.077 | 96.941 | 97.1045 | 95.4554 | 96.9149 | 97.2473 | 97.1696 | 96.9929 | 96.8158 | 96.9863 | 2025-01-02 | 2025-06-23
Energizer Solar | Force 3.8DC {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 3.713 | 240 | 96 | CSA Group | [11/20/2023] | CSA Group | [11/20/2023] | [V1.08, V1.02] | 2024-02-01 | [11/20/2023] | 2024-02-01 | CSA Group | 2023-11-22 | 2024-02-01 |  | N | N | 27.23 |  |  | 204 | 380 | 480 | 0.3713 | 0.74261 | 1.1139 | 1.8565 | 2.7848 | 3.713 | 88.7571 | 93.1319 | 94.7403 | 95.8238 | 96.4154 | 96.5626 | 95.627 | 90.646 | 94.5568 | 95.593 | 96.5203 | 97.3128 | 97.201 | 96.5299 | 87.3378 | 93.647 | 95.4273 | 96.4142 | 97.3282 | 97.4961 | 96.3329 | 2024-02-01 | 2024-05-21
Energizer Solar | Force 5.7DC {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 5.7482 | 240 | 97 | CSA Group | [11/20/2023] | CSA Group | [11/20/2023] | [V1.08, V1.02] | 2024-02-01 | [11/20/2023] | 2024-02-01 | CSA Group | 2023-11-22 | 2024-02-01 |  | N | N | 27.23 |  |  | 204 | 380 | 480 | 0.57482 | 1.1496 | 1.7245 | 2.8741 | 4.3111 | 5.7482 | 90.8808 | 94.8098 | 95.7632 | 96.4753 | 96.7386 | 96.703 | 96.2337 | 91.5018 | 95.6465 | 97.2168 | 97.6379 | 97.868 | 97.771 | 97.371 | 89.8373 | 95.634 | 96.4644 | 97.2092 | 97.4788 | 97.595 | 96.9084 | 2024-02-01 | 2024-05-21
Energizer Solar | Force 7.6DC {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 7.7203 | 240 | 97 | CSA Group | [11/20/2023] | CSA Group | [11/20/2023] | [V1.08, V1.02] | 2024-02-01 | [11/20/2023] | 2024-02-01 | CSA Group | 2023-11-22 | 2024-02-01 |  | N | N | 27.23 |  |  | 271 | 380 | 480 | 0.77203 | 1.5441 | 2.3161 | 3.8602 | 5.7903 | 7.7203 | 93.4996 | 95.7999 | 96.5407 | 97.0482 | 97.1101 | 96.8974 | 96.8082 | 93.8722 | 96.8306 | 97.0752 | 97.4311 | 97.293 | 97.6679 | 97.1547 | 92.4126 | 96.3152 | 97.0656 | 97.6101 | 97.731 | 97.5149 | 97.3315 | 2024-02-01 | 2024-05-21
Energizer Solar | Force 9.6DC {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 9.6091 | 240 | 97 | CSA Group | [11/20/2023] | CSA Group | [11/20/2023] | [V1.08, V1.02] | 2024-02-01 | [11/20/2023] | 2024-02-01 | CSA Group | 2023-11-22 | 2024-02-01 |  | N | N | 27.23 |  |  | 257 | 380 | 480 | 0.96091 | 1.9218 | 2.8827 | 4.8046 | 7.2068 | 9.6091 | 94.0151 | 96.18 | 96.7302 | 97.0459 | 96.9854 | 96.7841 | 96.7983 | 95.6441 | 97.147 | 97.1617 | 97.4712 | 97.3224 | 97.1525 | 97.25 | 94.7056 | 96.5502 | 97.2561 | 97.5742 | 97.6405 | 97.2619 | 97.3896 | 2024-02-01 | 2024-05-21
Energizer Solar | Force 11.4DC {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 11.5119 | 240 | 97.5 | CSA Group | [11/20/2023] | CSA Group | [11/20/2023] | [V1.08, V1.02] | 2024-02-01 | [11/20/2023] | 2024-02-01 | CSA Group | 2023-11-22 | 2024-02-01 |  | N | N | 27.23 |  |  | 305 | 380 | 480 | 1.1512 | 2.3024 | 3.4536 | 5.756 | 8.6339 | 11.5119 | 95.5005 | 96.9797 | 97.2834 | 97.3603 | 97.1804 | 96.9301 | 97.1408 | 96.2352 | 97.384 | 97.7697 | 97.5626 | 97.4234 | 97.4212 | 97.4446 | 95.7811 | 97.2716 | 97.6352 | 97.6967 | 97.6385 | 97.1496 | 97.5332 | 2024-02-01 | 2024-05-21
Enphase Energy, Inc. | IQ7PD-72-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 190 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.19 | 208 | 97 | UL | [8/19/2022] | UL | [11/25/2020]; [8/19/2022] | [V04.20.04];[V04.20.03];[V04.18.02];[V04.17.01]; [V04.40.01] | 2021-03-11 | [11/25/2020]; [8/19/2022] | 2021-03-11 | UL | 2020-01-24 | 2021-03-11 |  | N | Y | 0.02 |  |  | 22 | 31 | 40 | 0.019078 | 0.038156 | 0.057235 | 0.095391 | 0.14309 | 0.19078 | 93.458 | 94.6122 | 96.5408 | 97.2243 | 97.1303 | 96.6782 | 96.7839 | 94.1892 | 95.57 | 95.9456 | 97.2425 | 97.4304 | 97.3251 | 96.9848 | 93.1764 | 94.4298 | 95.4021 | 96.9211 | 97.2222 | 97.2054 | 96.6383 | 2021-03-11 | 2023-06-01
Enphase Energy, Inc. | IQ7PD-72-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 190 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.19 | 240 | 96.5 | UL | [8/19/2022] | UL | [11/25/2020]; [8/19/2022] | [V04.20.04];[V04.20.03];[V04.18.02];[V04.17.01]; [V04.40.01] | 2021-01-11 | [11/25/2020]; [8/19/2022] | 2021-01-11 | UL | 2020-01-24 | 2021-01-11 |  | N | Y | 0.02 |  |  | 22 | 31 | 40 | 0.019148 | 0.038295 | 0.057443 | 0.095739 | 0.14361 | 0.19148 | 92.9696 | 93.86 | 96.119 | 97.0685 | 96.9972 | 96.5816 | 96.568 | 94.3225 | 95.6189 | 95.3973 | 97.2206 | 97.52 | 97.5293 | 96.9799 | 93.1596 | 94.4484 | 94.7891 | 96.8124 | 97.2752 | 97.4069 | 96.5803 | 2021-01-11 | 2023-06-01
Enphase Energy, Inc. | IQ7PD-84-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 210 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.21 | 208 | 96.5 | UL | [8/19/2022] | UL | [11/25/2020]; [8/19/2022] | [V04.20.04];[V04.20.03];[V04.18.02];[V04.17.01]; [V04.40.01] | 2021-03-11 | [11/25/2020]; [8/19/2022] | 2021-03-11 | UL | 2020-01-24 | 2021-03-11 |  | N | Y | 0.017 |  |  | 31 | 40 | 50 | 0.021144 | 0.042288 | 0.063432 | 0.10572 | 0.15858 | 0.21144 | 93.8312 | 95.0289 | 96.0923 | 97.0931 | 97.1677 | 96.9428 | 96.7714 | 93.1896 | 94.8072 | 95.5863 | 96.8088 | 96.9807 | 96.8462 | 96.5102 | 92.3854 | 93.9263 | 95.0054 | 96.5139 | 96.7794 | 96.7231 | 96.1895 | 2021-03-11 | 2023-06-01
Enphase Energy, Inc. | IQ7PD-84-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 210 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.21 | 240 | 96.5 | UL | [8/19/2022] | UL | [11/25/2020]; [8/19/2022] | [V04.20.04];[V04.20.03];[V04.18.02];[V04.17.01]; [V04.40.01] | 2021-01-11 | [11/25/2020]; [8/19/2022] | 2021-01-11 | UL | 2020-01-24 | 2021-01-11 |  | N | Y | 0.022 |  |  | 31 | 40 | 50 | 0.021137 | 0.042273 | 0.06341 | 0.10568 | 0.15853 | 0.21137 | 94.0019 | 95.0964 | 96.2205 | 97.3342 | 97.5296 | 97.4271 | 97.0636 | 93.5498 | 95.2306 | 95.6885 | 96.9745 | 97.3031 | 97.3583 | 96.7894 | 92.5204 | 94.3275 | 94.8974 | 96.6419 | 97.0503 | 97.1852 | 96.3956 | 2021-01-11 | 2023-06-01
Enphase Energy, Inc. | S230-60-LL-x {208V} | N | N | Y | Y | Y | N | N | N | 230 W, 240 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US | 0.22 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [8/14/2017] | [v00.36.01] | 2018-10-15 | [8/14/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.051 |  |  | 27 | 32 | 37 | 0.02 | 0.04 | 0.07 | 0.11 | 0.17 | 0.22 | 94.9 | 96.5 | 96.4 | 97.2 | 97.2 | 96.9 | 97 | 94.9 | 96.4 | 96.1 | 97.1 | 97.1 | 96.8 | 96.8 | 94.8 | 96.3 | 95.8 | 96.9 | 97 | 96.7 | 96.7 | 2017-10-16 | 2018-10-15
Enphase Energy, Inc. | S230-60-LL-x {240V} | N | N | Y | Y | Y | N | N | N | 230 W, 240 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US | 0.22 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [8/14/2017] | [v00.36.01] | 2018-10-15 | [8/14/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.051 |  |  | 27 | 32 | 37 | 0.02 | 0.04 | 0.07 | 0.11 | 0.17 | 0.22 | 95 | 96.4 | 96.2 | 97.4 | 97.5 | 97.4 | 97.2 | 95 | 96.5 | 95.8 | 97.2 | 97.3 | 97.2 | 97 | 94.9 | 96.4 | 95.4 | 96.9 | 97.2 | 97.2 | 96.8 | 2017-10-16 | 2018-10-15
Enphase Energy, Inc. | IQ6-60-2-US {208V} | N | N | Y | Y | Y | Y | Y* | Y | 230 W, 208 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 2 | 0.23 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 |  | N | Y | 0.02 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.1975 | 95.7125 | 96.3485 | 97.2626 | 97.2603 | 96.9175 | 96.9343 | 94.4525 | 95.865 | 96.241 | 97.1193 | 97.1982 | 96.9745 | 96.8791 | 94.1798 | 95.6904 | 96.0834 | 96.9677 | 97.0876 | 96.9175 | 96.7472 | 2017-08-01 | 2021-03-11
Enphase Energy, Inc. | IQ6-60-2-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 230 W, 240 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 2 | 0.23 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 |  | N | Y | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | 2017-08-01 | 2021-03-11
Enphase Energy, Inc. | IQ6-60-5-US {208V} | N | N | Y | Y | Y | Y | Y* | Y | 230 W, 208 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 5 | 0.23 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 |  | N | Y | 0.02 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.1975 | 95.7125 | 96.3485 | 97.2626 | 97.2603 | 96.9175 | 96.9343 | 94.4525 | 95.865 | 96.241 | 97.1193 | 97.1982 | 96.9745 | 96.8791 | 94.1798 | 95.6904 | 96.0834 | 96.9677 | 97.0876 | 96.9175 | 96.7472 | 2017-08-01 | 2021-03-11
Enphase Energy, Inc. | IQ6-60-5-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 230 W, 240 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 5 | 0.23 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 |  | N | Y | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | 2017-08-01 | 2021-03-11
Enphase Energy, Inc. | IQ6-60-ACM-US {208V} | N | N | Y | Y | Y | Y | Y* | Y | 230 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications | 0.23 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.02 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.1975 | 95.7125 | 96.3485 | 97.2626 | 97.2603 | 96.9175 | 96.9343 | 94.4525 | 95.865 | 96.241 | 97.1193 | 97.1982 | 96.9745 | 96.8791 | 94.1798 | 95.6904 | 96.0834 | 96.9677 | 97.0876 | 96.9175 | 96.7472 | 2017-08-01 | 2021-03-11
Enphase Energy, Inc. | IQ6-60-ACM-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 230W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications | 0.23 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | 2017-08-01 | 2021-03-11
Enphase Energy, Inc. | IQ7-60-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.24 | 208 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7-60-x-US-& {208V}. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.024058 | 0.048116 | 0.072174 | 0.12029 | 0.18044 | 0.24058 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4739 | 97.4153 | 97.0564 | 97.0829 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.24 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7-60-x-US-& {240V}. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.02416 | 0.04832 | 0.07248 | 0.1208 | 0.1812 | 0.2416 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-5-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.24 | 208 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7-60-x-US-& {208V}. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.024058 | 0.048116 | 0.072174 | 0.12029 | 0.18044 | 0.24058 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4739 | 97.4153 | 97.0564 | 97.0829 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-5-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.24 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7-60-x-US-& {240V}. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.02416 | 0.04832 | 0.07248 | 0.1208 | 0.1812 | 0.2416 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.24 | 208 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& {208V}. | N | Y | 0.025 | 0.025 |  | 27 | 32 | 37 | 0.024058 | 0.048116 | 0.072174 | 0.12029 | 0.18044 | 0.24058 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4739 | 97.4153 | 97.0564 | 97.0829 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.24 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& {240V}. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.02416 | 0.04832 | 0.07248 | 0.1208 | 0.1812 | 0.2416 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.24 | 208 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& {208V}. | N | Y | 0.025 | 0.025 |  | 27 | 32 | 37 | 0.024058 | 0.048116 | 0.072174 | 0.12029 | 0.18044 | 0.24058 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4739 | 97.4153 | 97.0564 | 97.0829 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.24 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& {240V}. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.02416 | 0.04832 | 0.07248 | 0.1208 | 0.1812 | 0.2416 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-E-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.24 | 208 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& {208V}. | N | Y | 0.025 | 0.025 |  | 27 | 32 | 37 | 0.024058 | 0.048116 | 0.072174 | 0.12029 | 0.18044 | 0.24058 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4739 | 97.4153 | 97.0564 | 97.0829 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-E-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.24 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& {240V}. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.02416 | 0.04832 | 0.07248 | 0.1208 | 0.1812 | 0.2416 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-E-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.24 | 208 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& {208V}. | N | Y | 0.025 | 0.025 |  | 27 | 32 | 37 | 0.024058 | 0.048116 | 0.072174 | 0.12029 | 0.18044 | 0.24058 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4739 | 97.4153 | 97.0564 | 97.0829 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-E-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.24 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7-60-x-ACM-US-y-z-& {240V}. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.02416 | 0.04832 | 0.07248 | 0.1208 | 0.1812 | 0.2416 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-E-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.24 | 208 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7-60-x-US-& {208V}. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.024058 | 0.048116 | 0.072174 | 0.12029 | 0.18044 | 0.24058 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4739 | 97.4153 | 97.0564 | 97.0829 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-E-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.24 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7-60-x-US-& {240V}. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.02416 | 0.04832 | 0.07248 | 0.1208 | 0.1812 | 0.2416 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.24 | 208 | 97 | UL | [8/19/2022] | UL | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2021-09-01 | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | 2021-09-01 | UL | 2021-08-04 | 2021-09-01 |  | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.024058 | 0.048116 | 0.072174 | 0.12029 | 0.18044 | 0.24058 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4739 | 97.4153 | 97.0564 | 97.0829 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2021-09-01 | 2023-06-01
Enphase Energy, Inc. | IQ7-60-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 240 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.24 | 240 | 97 | UL | [8/19/2022] | UL | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2021-09-01 | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | 2021-09-01 | UL | 2021-08-04 | 2021-09-01 |  | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.02416 | 0.04832 | 0.07248 | 0.1208 | 0.1812 | 0.2416 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2021-09-01 | 2023-06-01
Enphase Energy, Inc. | IQ8-60-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.24 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.24 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-05-03 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-05-03 | UL | 2021-03-17 | 2021-05-03 |  | N | Y | 0.029 |  |  | 27 | 32 | 37 | 0.024 | 0.049 | 0.073 | 0.122 | 0.182 | 0.243 | 94.28 | 95.08 | 96.59 | 97.03 | 96.6 | 95.97 | 96.49 | 94.76 | 94.77 | 96.58 | 97.3 | 97.22 | 96.85 | 96.92 | 94.95 | 94.36 | 96.44 | 97.46 | 97.52 | 97.24 | 97.11 | 2021-05-03 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8-60-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.24 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.24 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-09-13 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-09-13 | UL | 2021-08-10 | 2021-09-13 |  | N | Y | 0.023 | 0 | 0 | 27 | 32 | 37 | 0.024028 | 0.048057 | 0.072085 | 0.12014 | 0.18021 | 0.24028 | 94.5611 | 95.93 | 96.7615 | 97.2704 | 96.9296 | 96.2662 | 96.8031 | 95.1516 | 96.1237 | 96.7257 | 97.5389 | 97.4779 | 97.0937 | 97.2205 | 95.4226 | 96.5195 | 96.8923 | 97.624 | 97.742 | 97.5322 | 97.4509 | 2021-09-13 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | XACM-IQ7-LR6-60PB-300M {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 300 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: LR6-60PB-300M. Microinverter: IQ7-60-x-ACM-US-y {208V} | 0.24 | 208 | 97 | UL | [6/8/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22] | 2020-03-11 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022] | 2020-05-11 | UL | 2020-03-18 | 2020-05-11 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2020-03-11 | 2022-10-03
Enphase Energy, Inc. | XACM-IQ7-LR6-60PB-300M {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 300 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: LR6-60PB-300M. Microinverter: IQ7-60-x-ACM-US-y {240V} | 0.24 | 240 | 97 | UL | [6/8/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22] | 2020-03-11 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022] | 2020-05-11 | UL | 2020-03-18 | 2020-05-11 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2020-03-11 | 2022-10-03
Enphase Energy, Inc. | XACM-IQ7-LR6-60PB-305M {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 305 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: LR6-60PB-305M. Microinverter: IQ7-60-x-ACM-US-y {208V} | 0.24 | 208 | 97 | UL | [6/8/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22] | 2020-03-11 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022] | 2020-05-11 | UL | 2020-03-18 | 2020-05-11 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | 2020-03-11 | 2022-10-03
Enphase Energy, Inc. | XACM-IQ7-LR6-60PB-305M {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 305 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: LR6-60PB-305M. Microinverter: IQ7-60-x-ACM-US-y {240V} | 0.24 | 240 | 97 | UL | [6/8/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22] | 2020-03-11 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022] | 2020-05-11 | UL | 2020-03-18 | 2020-05-11 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | 2020-03-11 | 2022-10-03
Enphase Energy, Inc. | IQ6PLUS-ACB-LL {240V} | N | N | Y | Y | Y | N | N | N | 270 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.27 | 240 | 95.5 | No Information Submitted | No Information Submitted | UL | [12/28/2017] | [v02.12.00] | 2018-10-15 | [12/28/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.07 |  |  | 23 | 25 | 28 | 0.027 | 0.054 | 0.081 | 0.135 | 0.2025 | 0.27 | 85.8903 | 93.6164 | 95.4627 | 95.9769 | 95.5783 | 94.8032 | 95.1238 | 85.8003 | 93.4691 | 95.4058 | 96.1485 | 95.8765 | 95.2295 | 95.3213 | 85.5189 | 93.1183 | 95.1904 | 96.1928 | 96.0669 | 95.5951 | 95.3952 | 2018-05-15 | 2018-10-15
Enphase Energy, Inc. | S280-60-LL-x {208V} | N | N | Y | Y | Y | N | N | N | 270 W, 208 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4 , or 5 and may be followed by -US | 0.27 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [8/14/2017] | [v00.36.01] | 2018-10-15 | [8/14/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.051 |  |  | 27 | 32 | 37 | 0.03 | 0.05 | 0.08 | 0.14 | 0.2 | 0.27 | 95 | 96.1 | 96.5 | 96.9 | 96.7 | 96.2 | 96.6 | 95 | 96.1 | 96.1 | 96.7 | 96.6 | 96.2 | 96.5 | 94.9 | 95.7 | 95.8 | 96.6 | 96.5 | 96.1 | 96.3 | 2017-10-16 | 2018-10-15
Enphase Energy, Inc. | S280-60-LL-x {240V} | N | N | Y | Y | Y | N | N | N | 270 W, 240 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US | 0.27 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [8/14/2017] | [v00.36.01] | 2018-10-15 | [8/14/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.062 |  |  | 27 | 32 | 37 | 0.03 | 0.05 | 0.08 | 0.14 | 0.2 | 0.27 | 95.2 | 96.5 | 96.9 | 97.3 | 97.3 | 97 | 97.1 | 95.3 | 96.5 | 96.7 | 97.1 | 97.2 | 96.9 | 97 | 95.1 | 96.1 | 96 | 96.9 | 97.1 | 96.9 | 96.8 | 2017-10-16 | 2018-10-15
Enphase Energy, Inc. | IQ6PLUS-72-2-US {208V} | N | N | Y | Y | Y | Y | Y* | Y | 280 W, 208 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 2 | 0.28 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 |  | N | Y | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2021-03-11
Enphase Energy, Inc. | IQ6PLUS-72-2-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 280 W, 240 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 2 | 0.28 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 |  | N | Y | 0.03 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-01 | 2021-03-11
Enphase Energy, Inc. | IQ6PLUS-72-5-US {208V} | N | N | Y | Y | Y | Y | Y* | Y | 280 W, 208 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 5 | 0.28 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 |  | N | Y | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2021-03-11
Enphase Energy, Inc. | IQ6PLUS-72-5-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 280 W, 240 Vac Grid Support Utility Interactive Microinverter, DC Connector type = 5 | 0.28 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 |  | N | Y | 0.03 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-01 | 2021-03-11
Enphase Energy, Inc. | IQ6PLUS-72-ACM-US {208V} | N | N | Y | Y | Y | Y | Y* | Y | 280 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications | 0.28 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 | This microinverter is sold as an individual unit but is only for ACPV modules including LG Electronics Inc. LGxxxE1K-A5 and LGxxxE1C-A5, where xxx = 315, 32, 325, 33, or 335. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-15 | 2021-03-11
Enphase Energy, Inc. | IQ6PLUS-72-ACM-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 280 W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications | 0.28 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | [v01.06.03];[v02.12.00];[v02.14.02];[v02.15.00];[v02.16.05] | 2018-10-15 | [06/29/2017];[12/28/2017];[07/07/2020];[07/07/2020];[01/19/2021] | 2021-02-11 | UL | 2021-01-24 | 2021-02-11 | This microinverter is sold as an individual unit but is only for ACPV modules including LG Electronics Inc. LGxxxE1K-A5 and LGxxxE1C-A5, where xxx = 315, 32, 325, 33, or 335. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-15 | 2021-03-11
Enphase Energy, Inc. | IQ7A-72-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7A-72-x-US-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7A-72-5-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7A-72-x-US-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7A-72-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7A-72-E-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7A-72-E-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7A-72-E-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7A-72-x-US-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7A-72-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2021-09-01 | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | 2021-09-01 | UL | 2021-08-04 | 2021-09-01 |  | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-09-01 | 2023-06-01
Enphase Energy, Inc. | IQ7AS-66-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7AS-66-5-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7AS-66-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2019-03-15 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7AS-66-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2019-03-15 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7AS-66-ACM-US-RMA {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2019-03-15 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7AS-66-E-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2019-03-15 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7AS-66-E-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2019-03-15 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7AS-66-E-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& {208V}. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7PLUS-72-x-US-& {208V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029184 | 0.058368 | 0.087552 | 0.14592 | 0.21888 | 0.29184 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.29 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7PLUS-72-x-US-& {240V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029176 | 0.058352 | 0.087528 | 0.14588 | 0.21882 | 0.29176 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-5-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7PLUS-72-x-US-& {208V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029184 | 0.058368 | 0.087552 | 0.14592 | 0.21888 | 0.29184 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-5-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.29 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7PLUS-72-x-US-& {240V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029176 | 0.058352 | 0.087528 | 0.14588 | 0.21882 | 0.29176 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& {208V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029184 | 0.058368 | 0.087552 | 0.14592 | 0.21888 | 0.29184 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 240 Vac Grid Support Utility Interactive microinverter | 0.29 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& {240V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029176 | 0.058352 | 0.087528 | 0.14588 | 0.21882 | 0.29176 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& {208V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029184 | 0.058368 | 0.087552 | 0.14592 | 0.21888 | 0.29184 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 240 Vac Grid Support Utility Interactive microinverter | 0.29 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& {240V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029176 | 0.058352 | 0.087528 | 0.14588 | 0.21882 | 0.29176 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-E-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& {208V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029184 | 0.058368 | 0.087552 | 0.14592 | 0.21888 | 0.29184 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-E-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 240 Vac Grid Support Utility Interactive microinverter | 0.29 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& {240V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029176 | 0.058352 | 0.087528 | 0.14588 | 0.21882 | 0.29176 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-E-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 208 Vac Grid Support Utility Interactive microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& {208V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029184 | 0.058368 | 0.087552 | 0.14592 | 0.21888 | 0.29184 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-E-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 240 Vac Grid Support Utility Interactive microinverter | 0.29 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7PLUS-72-x-ACM-US-y-z-& {240V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029176 | 0.058352 | 0.087528 | 0.14588 | 0.21882 | 0.29176 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-E-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7PLUS-72-x-US-& {208V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029184 | 0.058368 | 0.087552 | 0.14592 | 0.21888 | 0.29184 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-E-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.29 | 240 | 97 | UL | [8/19/2022] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7PLUS-72-x-US-& {240V}. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029176 | 0.058352 | 0.087528 | 0.14588 | 0.21882 | 0.29176 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2021-06-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.29 | 208 | 96.5 | UL | [8/19/2022] | UL | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2021-09-01 | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | 2021-09-01 | UL | 2021-08-04 | 2021-09-01 |  | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029184 | 0.058368 | 0.087552 | 0.14592 | 0.21888 | 0.29184 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | 2021-09-01 | 2023-06-01
Enphase Energy, Inc. | IQ7PLUS-72-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 290 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.29 | 240 | 97 | UL | [8/19/2022] | UL | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2021-09-01 | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | 2021-09-01 | UL | 2021-08-04 | 2021-09-01 |  | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029176 | 0.058352 | 0.087528 | 0.14588 | 0.21882 | 0.29176 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2021-09-01 | 2023-06-01
Enphase Energy, Inc. | IQ7A-66-x-US-& {208V} | N | N | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive Microinverter, where x = 2, 5, E, or blank, and & = any characters or blank | 0.29291 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09] | 2019-08-01 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3795 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2019-08-01 | 2020-11-12
Enphase Energy, Inc. | IQ7A-66-x-ACM-US-y-z-& {208V} | N | N | Y | Y | Y | Y | Y* | Y | 290 W, 208 Vac Grid Support Utility Interactive microinverter, where x = 2, 5, E, or blank, y = NM or blank, z = RMA or blank, and & = any characters or blank | 0.29291 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09] | 2020-04-01 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.045 |  |  | 38 | 40.5 | 43 | 0.029291 | 0.058582 | 0.087873 | 0.14645 | 0.21968 | 0.29291 | 94.5043 | 95.6178 | 96.3794 | 96.9986 | 96.8439 | 96.3109 | 96.6391 | 94.5123 | 95.5365 | 96.2796 | 96.9698 | 96.8365 | 96.3048 | 96.6131 | 94.5015 | 95.5124 | 96.1786 | 96.9216 | 96.8005 | 96.2939 | 96.5696 | 2020-04-01 | 2020-11-12
Enphase Energy, Inc. | IQ8PLUS-72-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.295 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.295 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-05-03 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-05-03 | UL | 2021-03-17 | 2021-05-03 |  | N | Y | 0.049 |  |  | 27 | 36 | 45 | 0.029 | 0.059 | 0.088 | 0.147 | 0.221 | 0.295 | 94.38 | 95.73 | 96.83 | 97.23 | 96.78 | 96.04 | 96.7 | 94.73 | 95.15 | 96.84 | 97.57 | 97.53 | 97.17 | 97.21 | 94.69 | 94.664 | 96.51 | 97.51 | 97.65 | 97.49 | 97.21 | 2021-05-03 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8PLUS-72-M-DOM-US {240V} | N | Y | Y | Y | Y | Y | Y* |  | 0.295 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.295 | 240 | 97 | UL | [5/13/2026] | UL | [10/29/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-12-11 | 2025-10-29 | 2025-12-11 | UL | 2025-10-29 |  |  | N | Y | 0.049 |  |  | 27 | 36 | 45 | 0.029 | 0.059 | 0.088 | 0.147 | 0.221 | 0.295 | 94.38 | 95.73 | 96.83 | 97.23 | 96.78 | 96.04 | 96.7 | 94.73 | 95.15 | 96.84 | 97.57 | 97.53 | 97.17 | 97.21 | 94.69 | 94.664 | 96.51 | 97.51 | 97.65 | 97.49 | 97.21 | 2025-12-11 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8PLUS-72-M-F-US {240V} | N | Y | Y | Y | Y | Y | Y* |  | 0.295 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.295 | 240 | 97 | UL | [5/13/2026] | UL | [10/29/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-12-11 | 2025-10-29 | 2025-12-11 | UL | 2025-10-29 |  |  | N | Y | 0.049 |  |  | 27 | 36 | 45 | 0.029 | 0.059 | 0.088 | 0.147 | 0.221 | 0.295 | 94.38 | 95.73 | 96.83 | 97.23 | 96.78 | 96.04 | 96.7 | 94.73 | 95.15 | 96.84 | 97.57 | 97.53 | 97.17 | 97.21 | 94.69 | 94.664 | 96.51 | 97.51 | 97.65 | 97.49 | 97.21 | 2025-12-11 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8PLUS-72-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.295 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.295 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-09-14 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-09-14 | UL | 2021-08-10 | 2021-09-13 |  | N | Y | 0.049 | 0 | 0 | 27 | 36 | 45 | 0.029 | 0.059 | 0.088 | 0.147 | 0.221 | 0.295 | 94.38 | 95.73 | 96.89 | 97.23 | 96.78 | 96.04 | 96.7 | 94.73 | 95.15 | 96.84 | 97.57 | 97.53 | 97.17 | 97.21 | 94.69 | 94.64 | 96.51 | 97.51 | 97.65 | 97.49 | 97.21 | 2021-09-13 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ7GPLUS-72-2-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 290 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.298 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/23/2021];[04/23/2021];[04/23/2021] | [V2.19.01];[V2.22.02];[V2.23.01] | 2021-05-03 | [04/23/2021];[04/23/2021];[04/23/2021] | 2021-05-03 | UL | 2021-03-17 | 2021-05-03 |  | N | Y | 0.03 |  |  | 29 | 37 | 45 | 0.029767 | 0.059535 | 0.089302 | 0.14884 | 0.22326 | 0.29767 | 94.9075 | 94.778 | 96.6298 | 97.1774 | 96.7309 | 96.309 | 96.6209 | 95.4932 | 96.8423 | 96.4128 | 97.5518 | 97.4968 | 97.2122 | 97.2512 | 95.8204 | 96.8733 | 96.9766 | 97.5159 | 97.6552 | 97.4534 | 97.4219 | 2021-05-03
Enphase Energy, Inc. | IQ8MC-72-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.310 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.309 | 208 | 96.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.049 | 0 | 0 | 25 | 35 | 45 | 0.031 | 0.062 | 0.092999 | 0.155 | 0.2325 | 0.31 | 94.1539 | 96.1172 | 97.0897 | 97.1548 | 96.5028 | 95.6855 | 96.5561 | 94.8448 | 95.3545 | 96.6613 | 97.1052 | 96.7886 | 96.2372 | 96.6628 | 94.7352 | 94.6312 | 96.2283 | 96.8825 | 96.6611 | 96.1676 | 96.4524 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8MC-72-M-DOM-US {208V} | N | Y | Y | Y | Y | Y | Y* |  | 0.31 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.31 | 208 | 96.5 | UL | [5/13/2026] | UL | [10/29/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-12-11 | 2025-10-29 | 2025-12-11 | UL | 2025-10-29 |  |  | N | Y | 0.027 |  |  | 25 | 35 | 45 | 0.031 | 0.062 | 0.093 | 0.155 | 0.2 | 0.3 | 94.3 | 96.4 | 97.2 | 97.3 | 96.7 | 95.7 | 96.7 | 95.4 | 95.4 | 96.8 | 97.2 | 96.9 | 96.3 | 96.8 | 95.3 | 94.7 | 96.3 | 97 | 96.7 | 96.2 | 96.6 | 2025-12-11 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8MC-72-M-F-US {208V} | N | Y | Y | Y | Y | Y | Y* |  | 0.31 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.31 | 208 | 96.5 | UL | [5/13/2026] | UL | [10/29/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-12-11 | 2025-10-29 | 2025-12-11 | UL | 2025-10-29 |  |  | N | Y | 0.027 |  |  | 25 | 35 | 45 | 0.031 | 0.062 | 0.093 | 0.155 | 0.2 | 0.3 | 94.3 | 96.4 | 97.2 | 97.3 | 96.7 | 95.7 | 96.7 | 95.4 | 95.4 | 96.8 | 97.2 | 96.9 | 96.3 | 96.8 | 95.3 | 94.7 | 96.3 | 97 | 96.7 | 96.2 | 96.6 | 2025-12-11 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8MC-72-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.31 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.31 | 208 | 96.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.027 |  |  | 25 | 35 | 45 | 0.031 | 0.062 | 0.093 | 0.155 | 0.233 | 0.31 | 94.25 | 96.38 | 97.22 | 97.25 | 96.66 | 95.74 | 96.69 | 95.43 | 95.44 | 96.82 | 97.22 | 96.88 | 96.32 | 96.79 | 95.25 | 94.69 | 96.33 | 96.96 | 96.73 | 96.24 | 96.55 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ7X-96-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7X-96-x-US-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7X-96-x-US-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-5-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7X-96-x-US-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-5-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7X-96-x-US-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-E-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-E-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-E-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-E-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7X-96-x-ACM-US-y-z-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-E-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7X-96-x-US-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-E-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97 | UL | [11/21/2021] | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7X-96-x-US-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2021-09-01 | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | 2021-09-01 | UL | 2021-08-04 | 2021-09-01 |  | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-09-01 | 2023-12-21
Enphase Energy, Inc. | IQ7X-96-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [8/19/2022] | UL | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2021-09-01 | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | 2021-09-01 | UL | 2021-08-04 | 2021-09-01 |  | N | Y | 0.021 |  |  | 53 | 60 | 64 | 0.031612 | 0.063224 | 0.094836 | 0.15806 | 0.23709 | 0.31612 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | 2021-09-01 | 2023-06-01
Enphase Energy, Inc. | IQ7XS-96-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-5-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-5-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-ACM-US-RMA {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-ACM-US-RMA {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-E-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-E-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-E-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-E-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.14.05];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2018-10-15 | [08/29/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-ACM-US-y-z-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-E-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.315 | 208 | 97 | UL | [11/21/2021] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& {208V}. | N | Y | 0.021 |  |  | 45 | 54.5 | 64 | 0.032 | 0.063 | 0.095 | 0.158 | 0.236 | 0.315 | 91.13 | 95.93 | 97.15 | 97.38 | 97.04 | 96.39 | 96.8 | 90.19 | 95.49 | 96.92 | 97.37 | 97.18 | 96.73 | 96.8 | 89.38 | 95.03 | 96.65 | 97.2 | 97.09 | 96.66 | 96.63 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ7XS-96-E-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.315 | 240 | 97.5 | UL | [11/21/2021] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7XS-96-x-US-& {240V}. | N | Y | 0.027 |  |  | 45 | 54.5 | 64 | 0.031 | 0.063 | 0.094 | 0.157 | 0.236 | 0.315 | 90.45 | 95.69 | 97.11 | 97.47 | 97.25 | 96.71 | 96.9 | 89.57 | 95.2 | 96.95 | 97.59 | 97.53 | 97.21 | 97.02 | 88.79 | 94.72 | 96.64 | 97.42 | 97.49 | 97.27 | 96.87 | 2021-06-01 | 2023-12-21
Enphase Energy, Inc. | IQ8MC-72-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.32 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.32 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.033 | 0 | 0 | 25 | 35 | 45 | 0.032015 | 0.064029 | 0.096044 | 0.16007 | 0.24011 | 0.32015 | 93.5806 | 95.9248 | 97.074 | 97.1533 | 96.6635 | 95.8456 | 96.6145 | 95.6106 | 96.5963 | 96.8428 | 97.4062 | 97.2907 | 96.8624 | 97.1379 | 95.6456 | 96.4703 | 96.359 | 97.1018 | 97.1078 | 96.8281 | 96.9123 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8MC-72-M-DOM-US {240V} | N | Y | Y | Y | Y | Y | Y* |  | 0.32 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.32 | 240 | 97 | UL | [5/13/2026] | UL | [10/29/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-12-11 | 2025-10-29 | 2025-12-11 | UL | 2025-10-29 |  |  | N | Y | 0.031 |  |  | 25 | 35 | 45 | 0.032 | 0.064 | 0.096 | 0.161 | 0.2 | 0.3 | 93.8 | 95.7 | 97.1 | 97.2 | 96.7 | 95.9 | 96.7 | 95.6 | 94.9 | 96.8 | 97.5 | 97.4 | 97 | 97.1 | 95.3 | 94.5 | 96.2 | 97.2 | 97.2 | 96.9 | 96.9 | 2025-12-11 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8MC-72-M-F-US {240V} | N | Y | Y | Y | Y | Y | Y* |  | 0.32 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.32 | 240 | 97 | UL | [5/13/2026] | UL | [10/29/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-12-11 | 2025-10-29 | 2025-12-11 | UL | 2025-10-29 |  |  | N | Y | 0.031 |  |  | 25 | 35 | 45 | 0.032 | 0.064 | 0.096 | 0.161 | 0.2 | 0.3 | 93.8 | 95.7 | 97.1 | 97.2 | 96.7 | 95.9 | 96.7 | 95.6 | 94.9 | 96.8 | 97.5 | 97.4 | 97 | 97.1 | 95.3 | 94.5 | 96.2 | 97.2 | 97.2 | 96.9 | 96.9 | 2025-12-11 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8MC-72-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.32 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.32 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.031 |  |  | 25 | 35 | 45 | 0.032 | 0.064 | 0.096 | 0.161 | 0.241 | 0.321 | 93.76 | 95.72 | 97.12 | 97.23 | 96.7 | 95.89 | 96.66 | 95.62 | 94.89 | 96.84 | 97.49 | 97.36 | 96.98 | 97.11 | 95.34 | 94.49 | 96.2 | 97.19 | 97.19 | 96.93 | 96.85 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8M-72-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.325 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.325 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-05-03 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-05-03 | UL | 2021-03-17 | 2021-05-03 |  | N | Y | 0.033 |  |  | 30 | 37.5 | 45 | 0.033 | 0.065 | 0.098 | 0.164 | 0.245 | 0.327 | 95.32 | 96.43 | 97.22 | 97.13 | 96.46 | 95.43 | 96.59 | 95.52 | 96.15 | 97.32 | 97.64 | 97.31 | 96.85 | 97.23 | 95.62 | 95.7 | 97 | 97.7 | 97.55 | 97.21 | 97.33 | 2021-05-03 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8M-72-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.325 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.325 | 240 | 97.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-09-15 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-09-15 | UL | 2021-08-10 | 2021-09-13 |  | N | Y | 0.021 | 0 | 0 | 30 | 37.5 | 45 | 0.032516 | 0.065033 | 0.097549 | 0.16258 | 0.24387 | 0.32516 | 95.2961 | 96.3793 | 97.3135 | 97.4261 | 96.8321 | 96.0448 | 96.8911 | 95.7064 | 96.7863 | 97.3264 | 97.7646 | 97.5773 | 97.1243 | 97.4495 | 95.847 | 96.873 | 97.2053 | 97.7786 | 97.7463 | 97.4648 | 97.5544 | 2021-09-13 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8AC-72-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.345 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.344 | 208 | 96.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.022 | 0 | 0 | 28 | 36.5 | 45 | 0.034475 | 0.068949 | 0.10342 | 0.17237 | 0.25856 | 0.34475 | 94.2854 | 96.3057 | 97.1478 | 97.1589 | 96.5519 | 95.8333 | 96.612 | 95.5554 | 96.3242 | 96.8095 | 96.9994 | 96.6324 | 95.9151 | 96.6364 | 95.2518 | 96.0362 | 96.4134 | 96.82 | 96.4362 | 95.8272 | 96.4162 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8AC-72-M-DOM-US {208V} | N | Y | Y | Y | Y | Y | Y* |  | 0.345 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.345 | 208 | 96.5 | UL | [5/13/2026] | UL | [10/29/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-12-11 | 2025-10-29 | 2025-12-11 | UL | 2025-10-29 |  |  | N | Y | 0.028 |  |  | 28 | 36.5 | 45 | 0.0345 | 0.0689 | 0.1034 | 0.1723 | 0.3 | 0.3 | 94.3 | 96.4 | 97.2 | 97.2 | 96.7 | 95.7 | 96.7 | 95.4 | 95.8 | 96.9 | 97.1 | 96.7 | 96.1 | 96.7 | 95.1 | 95.1 | 96.5 | 96.9 | 96.6 | 96 | 96.5 | 2025-12-11 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8AC-72-M-F-US {208V} | N | Y | Y | Y | Y | Y | Y* |  | 0.345 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.345 | 208 | 96.5 | UL | [5/13/2026] | UL | [10/29/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-12-11 | 2025-10-29 | 2025-12-11 | UL | 2025-10-29 |  |  | N | Y | 0.028 |  |  | 28 | 36.5 | 45 | 0.0345 | 0.0689 | 0.1034 | 0.1723 | 0.3 | 0.3 | 94.3 | 96.4 | 97.2 | 97.2 | 96.7 | 95.7 | 96.7 | 95.4 | 95.8 | 96.9 | 97.1 | 96.7 | 96.1 | 96.7 | 95.1 | 95.1 | 96.5 | 96.9 | 96.6 | 96 | 96.5 | 2025-12-11 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8AC-72-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.345 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.345 | 208 | 96.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.345 |  |  | 28 | 36.5 | 45 | 0.0345 | 0.0689 | 0.1034 | 0.1723 | 0.2584 | 0.3445 | 94.331 | 96.357 | 97.202 | 97.245 | 96.672 | 95.742 | 96.7 | 95.393 | 95.791 | 96.865 | 97.126 | 96.656 | 96.063 | 96.656 | 95.098 | 95.073 | 96.493 | 96.94 | 96.563 | 96.027 | 96.474 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ7A-66-x-US-& {240V} | N | N | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter, where x = 2, 5, E, or blank, and & = any characters or blank | 0.3487 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09] | 2019-08-01 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2019-08-01 | 2020-11-12
Enphase Energy, Inc. | IQ7A-66-x-ACM-US-y-z-& {240V} | N | N | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive microinverter, where x = 2, 5, E, or blank, y = NM or blank, z = RMA or blank, and & = any characters or blank | 0.349 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09] | 2020-04-01 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2020-04-01 | 2020-11-12
Enphase Energy, Inc. | IQ7A-72-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7A-72-x-US-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7A-72-5-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7A-72-x-US-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7A-72-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7A-72-E-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7A-72-E-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to ACPV modules and is not available as an individual unit. Formerly IQ7A-72-x-ACM-US-y-z-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7A-72-E-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-04-01 | [02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | Formerly IQ7A-72-x-US-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7A-72-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.14.05];[V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2021-09-01 | [07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[07/12/2021];[06/08/2022]; [8/19/2022] | 2021-09-01 | UL | 2021-08-04 | 2021-09-01 |  | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-09-01 | 2022-11-01
Enphase Energy, Inc. | IQ7AS-66-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7AS-66-5-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7AS-66-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2019-03-15 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7AS-66-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2019-03-15 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7AS-66-ACM-US-RMA {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2019-03-15 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7AS-66-E-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2019-03-15 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7AS-66-E-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.17.01];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2019-03-15 | [01/09/2019];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-04-01 | UL | 2020-03-18 | 2020-04-01 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-ACM-US-y-z-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ7AS-66-E-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.349 | 240 | 97 | UL | [8/19/2022] | UL | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | [V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07];[V04.30.22]; [V04.40.01] | 2020-10-12 | [07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021];[06/08/2022]; [8/19/2022] | 2020-10-12 | UL | 2020-01-24 | 2020-10-12 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7AS-66-x-US-& {240V}. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2021-06-01 | 2022-11-01
Enphase Energy, Inc. | IQ8A-72-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.349 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.349 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-05-03 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-05-03 | UL | 2021-03-17 | 2021-05-03 |  | N | Y | 0.017 |  |  | 32 | 38.5 | 45 | 0.035 | 0.07 | 0.105 | 0.175 | 0.263 | 0.35 | 95.44 | 96.52 | 97.25 | 97.2 | 96.57 | 95.42 | 96.68 | 95.65 | 96.09 | 97.29 | 97.55 | 97.18 | 96.54 | 97.13 | 95.58 | 95.67 | 97.13 | 97.56 | 97.39 | 96.99 | 97.21 | 2021-05-03 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8A-72-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.349 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.349 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-09-16 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-09-16 | UL | 2021-08-10 | 2021-09-13 |  | N | Y | 0.022 | 0 | 0 | 32 | 38.5 | 45 | 0.034961 | 0.069922 | 0.10488 | 0.1748 | 0.26221 | 0.34961 | 95.6582 | 96.4443 | 97.2964 | 97.3871 | 96.8006 | 95.9864 | 96.8791 | 95.973 | 96.7099 | 97.2844 | 97.6574 | 97.408 | 96.8777 | 97.3267 | 95.9891 | 96.7714 | 97.0801 | 97.6542 | 97.5743 | 97.2005 | 97.4095 | 2021-09-13 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8AC-72-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.349 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.349 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.03 | 0 | 0 | 28 | 36.5 | 45 | 0.034933 | 0.069866 | 0.1048 | 0.17467 | 0.262 | 0.34933 | 93.7649 | 95.8429 | 97.1841 | 97.2902 | 96.7901 | 96.1442 | 96.7418 | 95.5755 | 96.588 | 96.8803 | 97.3193 | 97.1173 | 96.6092 | 97.0178 | 95.5631 | 96.4069 | 96.4821 | 97.1093 | 96.9762 | 96.6142 | 96.8417 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8AC-72-M-DOM-US {240V} | N | Y | Y | Y | Y | Y | Y* |  | 0.349 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.349 | 240 | 97 | UL | [5/13/2026] | UL | [10/29/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-12-11 | 2025-10-29 | 2025-12-11 | UL | 2025-10-29 |  |  | N | Y | 0.031 |  |  | 28 | 36.5 | 45 | 0.035 | 0.07 | 0.105 | 0.175 | 0.3 | 0.3 | 93.9 | 96.1 | 97.2 | 97.4 | 96.9 | 96.1 | 96.8 | 95.5 | 95.1 | 96.9 | 97.4 | 97.2 | 96.8 | 97 | 95.4 | 94.6 | 96.5 | 97.2 | 97.1 | 96.7 | 96.8 | 2025-12-11 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8AC-72-M-F-US {240V} | N | Y | Y | Y | Y | Y | Y* |  | 0.349 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.349 | 240 | 97 | UL | [5/13/2026] | UL | [10/29/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-12-11 | 2025-10-29 | 2025-12-11 | UL | 2025-10-29 |  |  | N | Y | 0.031 |  |  | 28 | 36.5 | 45 | 0.035 | 0.07 | 0.105 | 0.175 | 0.3 | 0.3 | 93.9 | 96.1 | 97.2 | 97.4 | 96.9 | 96.1 | 96.8 | 95.5 | 95.1 | 96.9 | 97.4 | 97.2 | 96.8 | 97 | 95.4 | 94.6 | 96.5 | 97.2 | 97.1 | 96.7 | 96.8 | 2025-12-11 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8AC-72-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.349 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.349 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.036 |  |  | 28 | 36.5 | 45 | 0.035 | 0.07 | 0.105 | 0.175 | 0.262 | 0.349 | 93.85 | 96.09 | 97.21 | 97.36 | 96.88 | 96.1 | 96.82 | 95.5 | 95.11 | 96.9 | 97.42 | 97.19 | 96.77 | 97.01 | 95.41 | 94.58 | 96.5 | 97.22 | 97.08 | 96.71 | 96.83 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8HC-72-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.36 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.359 | 208 | 96.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.026 | 0 | 0 | 29.5 | 37 | 45 | 0.035979 | 0.071957 | 0.10794 | 0.17989 | 0.26984 | 0.35979 | 95.048 | 96.5449 | 97.1408 | 97.2099 | 96.5647 | 95.7592 | 96.6674 | 95.5113 | 96.4292 | 96.8397 | 97.0465 | 96.5817 | 95.72 | 96.6167 | 95.6329 | 96.0499 | 96.3127 | 96.8532 | 96.4706 | 95.6508 | 96.4365 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8X-80-E-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.36 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.359 | 208 | 96.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-11-21 | [9/27/2023];[5/14/2025] | 2023-11-21 | UL | 2023-09-18 | 2023-11-21 |  | N | Y | 0.012 | 0 | 0 | 43 | 51.5 | 60 | 0.035984 | 0.071968 | 0.10795 | 0.17992 | 0.26988 | 0.35984 | 90.6675 | 95.6618 | 96.7968 | 97.0063 | 96.6115 | 95.9505 | 96.3983 | 89.8243 | 95.3866 | 96.5721 | 96.8872 | 96.5378 | 95.9831 | 96.2615 | 88.8191 | 94.7418 | 96.2543 | 96.7308 | 96.5094 | 95.9298 | 96.1003 | 2023-11-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8X-80-M-DOM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.36 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.359 | 208 | 96.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2024-10-01 | [8/19/2024];[5/14/2025] | 2024-10-01 | UL | 2024-09-18 | 2024-10-01 |  | N | Y | 0.012 | 0 | 0 | 43 | 51.5 | 60 | 0.035984 | 0.071968 | 0.10795 | 0.17992 | 0.26988 | 0.35984 | 90.6675 | 95.6618 | 96.7968 | 97.0063 | 96.6115 | 95.9505 | 96.3983 | 89.8243 | 95.3866 | 96.5721 | 96.8872 | 96.5378 | 95.9831 | 96.2615 | 88.8191 | 94.7418 | 96.2543 | 96.7308 | 96.5094 | 95.9298 | 96.1003 | 2024-10-01 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8H-208-72-2-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.36 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.36 | 208 | 96.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-05-03 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-05-03 | UL | 2021-03-17 | 2021-05-03 |  | N | Y | 0.014 |  |  | 36 | 40.5 | 45 | 0.036 | 0.072 | 0.108 | 0.181 | 0.271 | 0.361 | 95.41 | 96.37 | 97.12 | 97.13 | 96.41 | 95.45 | 96.56 | 95.24 | 96.29 | 97.04 | 97.16 | 96.57 | 95.87 | 96.65 | 95.16 | 95.98 | 96.82 | 97.13 | 96.62 | 95.92 | 96.63 | 2021-05-03 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8H-208-72-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.360 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.36 | 208 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-09-18 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-09-18 | UL | 2021-08-10 | 2021-09-13 |  | N | Y | 0.015 | 0 | 0 | 36 | 40.5 | 45 | 0.035978 | 0.071955 | 0.10793 | 0.17989 | 0.26983 | 0.35978 | 95.4252 | 96.507 | 97.3264 | 97.4865 | 97.0403 | 96.3654 | 97.0433 | 95.1007 | 96.289 | 97.193 | 97.481 | 97.1596 | 96.6187 | 97.0782 | 95.0595 | 96.0776 | 97.051 | 97.4154 | 97.1243 | 96.6108 | 97.016 | 2021-09-13 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8HC-72-M-DOM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.36 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.36 | 208 | 96.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2025-02-21 | [8/19/2024];[5/14/2025] | 2025-02-21 | UL | 2025-01-30 | 2025-02-21 |  | N | Y | 0.081 | 0 | 0 | 29.5 | 37 | 45 | 0.036064 | 0.072128 | 0.10819 | 0.18032 | 0.27048 | 0.36064 | 91.6415 | 96.6112 | 97.302 | 97.2775 | 96.6654 | 95.7434 | 96.6206 | 91.1334 | 96.175 | 97.0431 | 97.1901 | 96.7084 | 95.9343 | 96.5614 | 89.9918 | 95.6878 | 96.7186 | 97.0373 | 96.6353 | 95.9028 | 96.38 | 2025-02-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8HC-72-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.36 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.36 | 208 | 96.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.019 |  |  | 29.5 | 37 | 45 | 0.036 | 0.072 | 0.108 | 0.18 | 0.27 | 0.36 | 94.38 | 96.26 | 97.17 | 97.19 | 96.6 | 95.64 | 96.64 | 95.52 | 95.73 | 96.9 | 97.07 | 96.63 | 95.84 | 96.62 | 95.4 | 95.18 | 96.52 | 96.9 | 96.53 | 95.81 | 96.46 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8X-80-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.36 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.36 | 208 | 96.5 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-11-21 | [9/27/2023];[5/14/2025] | 2023-11-21 | UL | 2023-09-18 | 2023-11-21 |  | N | Y | 0.012 |  |  | 43 | 51.5 | 60 | 0.036 | 0.072 | 0.108 | 0.181 | 0.271 | 0.361 | 95.23 | 96.01 | 96.86 | 97.08 | 96.64 | 96 | 96.64 | 94.89 | 95.48 | 96.61 | 96.95 | 96.68 | 96.01 | 96.56 | 95.04 | 94.96 | 96.27 | 96.76 | 96.6 | 96.08 | 96.42 | 2023-11-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ7HS-66-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 369 VA, 208 Vac Grid Support Utility Interactive microinverter | 0.367 | 208 | 97 | UL | [6/8/2022] | UL | [01/19/2021];[01/19/2021] | [V04.19.06];[V04.21.04] | 2021-02-11 | [01/19/2021];[01/19/2021] | 2021-02-11 | UL | 2020-01-24 | 2021-02-11 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y {208V}. | N | Y | 0.05 |  |  | 38 | 40.5 | 43 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 96.9774 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 97.0161 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185 | 96.9879 | 2021-07-12 | 2022-09-12
Enphase Energy, Inc. | IQ7HS-66-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 369 VA, 208 Vac Grid Support Utility Interactive microinverter | 0.367 | 208 | 97 | UL | [8/19/2022] | UL | [01/19/2021];[01/19/2021]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2021-02-11 | [01/19/2021];[01/19/2021]; [8/19/2022] | 2021-02-11 | UL | 2020-01-24 | 2021-02-11 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y {208V}. | N | Y | 0.05 |  |  | 38 | 40.5 | 43 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 96.9774 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 97.0161 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185 | 96.9879 | 2021-07-12 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-E-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 369 VA, 208 Vac Grid Support Utility Interactive microinverter | 0.367 | 208 | 97 | UL | [8/19/2022] | UL | [01/19/2021];[01/19/2021]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2021-02-11 | [01/19/2021];[01/19/2021]; [8/19/2022] | 2021-02-11 | UL | 2020-01-24 | 2021-02-11 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y {208V}. | N | Y | 0.05 |  |  | 38 | 40.5 | 43 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 96.9774 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 97.0161 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185 | 96.9879 | 2021-07-12 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-E-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 369 VA, 208 Vac Grid Support Utility Interactive microinverter | 0.367 | 208 | 97 | UL | [8/19/2022] | UL | [01/19/2021];[01/19/2021]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2021-02-11 | [01/19/2021];[01/19/2021]; [8/19/2022] | 2021-02-11 | UL | 2020-01-24 | 2021-02-11 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y {208V}. | N | Y | 0.05 |  |  | 38 | 40.5 | 43 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 96.9774 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 97.0161 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185 | 96.9879 | 2021-07-12 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-M-ACM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 369 VA, 208 Vac Grid Support Utility Interactive Inverter | 0.367 | 208 | 97 | UL | [8/19/2022] | UL | [3/30/2022]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2022-05-23 | [3/30/2022]; [8/19/2022] | 2022-05-23 | UL | 2021-08-04 | 2022-05-23 | This component is specific to SunPower ACPV modules and is not available as an individual unit. | N | Y | 0.05 |  |  | 38 | 40.5 | 43 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 96.9774 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 97.0161 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185 | 96.9879 | 2022-05-23 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-M-ACM-US-NM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 369 VA, 208 Vac Grid Support Utility Interactive Inverter | 0.367 | 208 | 97 | UL | [8/19/2022] | UL | [3/30/2022]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2022-05-23 | [3/30/2022]; [8/19/2022] | 2022-05-23 | UL | 2021-08-04 | 2022-05-23 | This component is specific to SunPower ACPV modules and is not available as an individual unit. | N | Y | 0.05 |  |  | 38 | 40.5 | 43 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 96.9774 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 97.0161 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185 | 96.9879 | 2022-05-23 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-M-ACM-US-RMA {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 369 VA, 208 Vac Grid Support Utility Interactive microinverter | 0.367 | 208 | 97 | UL | [8/19/2022] | UL | [03/30/2022]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2022-05-23 | [03/30/2022]; [8/19/2022] | 2022-05-23 | UL | 2021-08-04 | 2022-05-23 | This component is specific to SunPower ACPV modules and is not available as an individual unit. | N | Y | 0.05 |  |  | 38 | 40.5 | 43 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 96.9774 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 97.0161 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185 | 96.9879 | 2022-05-23 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 369 VA, 208 Vac Grid Support Utility Interactive Inverter | 0.367 | 208 | 97 | UL | [8/19/2022] | UL | [3/30/2022]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2022-06-21 | [3/30/2022]; [8/19/2022] | 2022-06-21 | UL | 2021-09-04 | 2022-06-21 | This component is specific to SunPower ACPV modules and is not available as an individual unit. | N | Y | 0.05 |  |  | 38 | 40.5 | 43 | 0.036703 | 0.073405 | 0.11011 | 0.18351 | 0.27527 | 0.36703 | 95.4311 | 96.2155 | 97.2705 | 97.4157 | 96.9796 | 96.4093 | 96.9774 | 95.4912 | 96.2222 | 97.215 | 97.431 | 97.0437 | 96.5177 | 97.0161 | 95.4773 | 96.2339 | 97.1236 | 97.3849 | 97.0292 | 96.5185 | 96.9879 | 2022-06-21 | 2022-11-01
Enphase Energy, Inc. | IQ8H-240-72-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.38 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.38 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-05-03 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-05-03 | UL | 2021-03-17 | 2021-05-03 |  | N | Y | 0.03 |  |  | 36 | 40.5 | 45 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 95.35 | 96.61 | 97.36 | 97.41 | 96.93 | 96.15 | 96.97 | 95.53 | 96.31 | 97.39 | 97.59 | 97.19 | 96.59 | 97.16 | 95.46 | 96.08 | 97.28 | 97.6 | 97.38 | 96.94 | 97.25 | 2021-05-03 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8H-240-72-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.38 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.38 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2021-09-17 | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[5/14/2025] | 2021-09-17 | UL | 2021-08-10 | 2021-09-13 |  | N | Y | 0.022 | 0 | 0 | 36 | 40.5 | 45 | 0.03803 | 0.076061 | 0.11409 | 0.19015 | 0.28523 | 0.3803 | 95.8426 | 96.705 | 97.3296 | 97.4708 | 96.9541 | 96.1562 | 97.0109 | 96.1029 | 96.7737 | 97.2891 | 97.5985 | 97.2794 | 96.674 | 97.245 | 96.0883 | 96.7957 | 97.0427 | 97.5781 | 97.3859 | 96.8918 | 97.2789 | 2021-09-13 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8H-3P-72-E-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.380 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 0.38 | 208 | 97 | UL | [5/13/2026] | UL | [5/22/2024];[6/13/2025];{5/13/2026] | [2.58.05];[8.14.02];{10.31.01] | 2024-06-21 | [6/13/2025] | 2024-06-21 | UL | 2023-09-27 | 2023-11-21 |  | N | Y | 0.052 |  |  | 28.5 | 37 | 45 | 0.038 | 0.076 | 0.115 | 0.191 | 0.287 | 0.382 | 95.22 | 95.95 | 97.09 | 97.28 | 96.75 | 96.01 | 96.76 | 95.49 | 95.43 | 97.02 | 97.79 | 97.72 | 97.34 | 97.43 | 96.16 | 95.04 | 96.76 | 97.77 | 97.96 | 97.8 | 97.55 | 2023-11-21 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8H-3P-72-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.380 kW, 208 Vac Grid Support Utility Interactive Inverter | 0.38 | 208 | 97 | UL | [5/13/2026] | UL | [5/22/2024];[6/13/2025];{5/13/2026] | [2.58.05];[8.14.02];{10.31.01] | 2024-06-21 | [6/13/2025] | 2024-06-21 | UL | 2023-09-27 | 2023-11-21 |  | N | Y | 0.052 |  |  | 28.5 | 37 | 45 | 0.038 | 0.076 | 0.115 | 0.191 | 0.287 | 0.382 | 95.22 | 95.95 | 97.09 | 97.28 | 96.75 | 96.01 | 96.76 | 95.49 | 95.43 | 97.02 | 97.79 | 97.72 | 97.34 | 97.43 | 96.16 | 95.04 | 96.76 | 97.77 | 97.96 | 97.8 | 97.55 | 2023-11-21 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ7HS-66-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 384 VA, 240 Vac Grid Support Utility Interactive microinverter | 0.384 | 240 | 97 | UL | [6/8/2022] | UL | [01/19/2021];[01/19/2021] | [V04.19.06];[V04.21.04] | 2021-02-11 | [01/19/2021];[01/19/2021] | 2021-02-11 | UL | 2020-01-24 | 2021-02-11 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y {240V}. | N | Y | 0.06 |  |  | 38 | 40.5 | 43 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 97.1217 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 97.2345 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854 | 97.2867 | 2021-07-12 | 2022-09-12
Enphase Energy, Inc. | IQ7HS-66-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 384 VA, 240 Vac Grid Support Utility Interactive microinverter | 0.384 | 240 | 97 | UL | [8/19/2022] | UL | [01/19/2021];[01/19/2021]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2021-02-11 | [01/19/2021];[01/19/2021]; [8/19/2022] | 2021-02-11 | UL | 2020-01-24 | 2021-02-11 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y {240V}. | N | Y | 0.06 |  |  | 38 | 40.5 | 43 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 97.1217 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 97.2345 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854 | 97.2867 | 2021-07-12 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-E-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 384 VA, 240 Vac Grid Support Utility Interactive microinverter | 0.384 | 240 | 97 | UL | [8/19/2022] | UL | [01/19/2021];[01/19/2021]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2021-02-11 | [01/19/2021];[01/19/2021]; [8/19/2022] | 2021-02-11 | UL | 2020-01-24 | 2021-02-11 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y {240V}. | N | Y | 0.06 |  |  | 38 | 40.5 | 43 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 97.1217 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 97.2345 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854 | 97.2867 | 2021-07-12 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-E-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 384 VA, 240 Vac Grid Support Utility Interactive microinverter | 0.384 | 240 | 97 | UL | [8/19/2022] | UL | [01/19/2021];[01/19/2021]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2021-02-11 | [01/19/2021];[01/19/2021]; [8/19/2022] | 2021-02-11 | UL | 2020-01-24 | 2021-02-11 | This component is specific to SunPower ACPV modules and is not available as an individual unit. Formerly IQ7HS-66-x-ACM-US-y {240V}. | N | Y | 0.06 |  |  | 38 | 40.5 | 43 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 97.1217 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 97.2345 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854 | 97.2867 | 2021-07-12 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-M-ACM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 384 VA, 240 Vac Grid Support Utility Interactive Inverter | 0.384 | 240 | 97 | UL | [8/19/2022] | UL | [3/30/2022]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2022-05-23 | [3/30/2022]; [8/19/2022] | 2022-05-23 | UL | 2021-08-04 | 2022-05-23 | This component is specific to SunPower ACPV modules and is not available as an individual unit. | N | Y | 0.06 |  |  | 38 | 40.5 | 43 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 97.1217 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 97.2345 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854 | 97.2867 | 2022-05-23 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-M-ACM-US-NM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 384 VA, 240 Vac Grid Support Utility Interactive Inverter | 0.384 | 240 | 97 | UL | [8/19/2022] | UL | [3/30/2022]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2022-05-23 | [3/30/2022]; [8/19/2022] | 2022-05-23 | UL | 2021-08-04 | 2022-05-23 | This component is specific to SunPower ACPV modules and is not available as an individual unit. | N | Y | 0.06 |  |  | 38 | 40.5 | 43 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 97.1217 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 97.2345 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854 | 97.2867 | 2022-05-23 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-M-ACM-US-RMA {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 384 VA, 240 Vac Grid Support Utility Interactive microinverter | 0.384 | 240 | 97 | UL | [8/19/2022] | UL | [03/30/2022]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2022-05-23 | [03/30/2022]; [8/19/2022] | 2022-05-23 | UL | 2021-08-04 | 2022-05-23 | This component is specific to SunPower ACPV modules and is not available as an individual unit. | N | Y | 0.06 |  |  | 38 | 40.5 | 43 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 97.1217 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 97.2345 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854 | 97.2867 | 2022-05-23 | 2022-11-01
Enphase Energy, Inc. | IQ7HS-66-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 384 VA, 240 Vac Grid Support Utility Interactive Inverter | 0.384 | 240 | 97 | UL | [8/19/2022] | UL | [3/30/2022]; [8/19/2022] | [V04.19.06];[V04.21.04]; [V04.40.01] | 2022-06-21 | [3/30/2022]; [8/19/2022] | 2022-06-21 | UL | 2021-09-04 | 2022-06-21 | This component is specific to SunPower ACPV modules and is not available as an individual unit. | N | Y | 0.06 |  |  | 38 | 40.5 | 43 | 0.03838 | 0.07676 | 0.11514 | 0.1919 | 0.28785 | 0.3838 | 95.5882 | 96.3483 | 97.2836 | 97.5309 | 97.15 | 96.7136 | 97.1217 | 95.603 | 96.2346 | 97.2829 | 97.5917 | 97.3229 | 96.9867 | 97.2345 | 95.7337 | 96.3525 | 97.1679 | 97.6271 | 97.4031 | 97.0854 | 97.2867 | 2022-06-21 | 2022-11-01
Enphase Energy, Inc. | IQ8HC-72-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.384 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.384 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.022 | 0 | 0 | 29.5 | 37 | 45 | 0.038 | 0.077 | 0.115 | 0.192 | 0.288 | 0.384 | 94.59 | 96.25 | 97.25 | 97.37 | 96.81 | 96.06 | 96.83 | 95.16 | 95.71 | 97 | 97.35 | 97 | 96.45 | 96.91 | 95 | 95.19 | 96.62 | 97.17 | 96.9 | 96.37 | 96.73 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8HC-72-M-DOM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.384 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.384 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2024-10-01 | [8/19/2024];[5/14/2025] | 2024-10-01 | UL | 2024-09-09 | 2024-10-01 |  | N | Y | 0.053 | 0 | 0 | 29.5 | 37 | 45 | 0.038 | 0.077 | 0.115 | 0.192 | 0.288 | 0.384 | 94.59 | 96.25 | 97.25 | 97.37 | 96.81 | 96.06 | 96.83 | 95.16 | 95.71 | 97 | 97.35 | 97 | 96.45 | 96.91 | 95 | 95.19 | 96.62 | 97.17 | 96.9 | 96.37 | 96.73 | 2024-10-01 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8HC-72-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.384 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.384 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-07-21 | [5/22/2023];[8/25/2023];[5/14/2025] | 2023-07-21 | UL | 2023-04-25 | 2023-07-21 |  | N | Y | 0.053 |  |  | 29.5 | 37 | 45 | 0.038 | 0.077 | 0.115 | 0.192 | 0.288 | 0.384 | 94.59 | 96.25 | 97.25 | 97.37 | 96.81 | 96.06 | 96.83 | 95.16 | 95.71 | 97 | 97.35 | 97 | 96.45 | 96.91 | 95 | 95.19 | 96.62 | 97.17 | 96.9 | 96.37 | 96.73 | 2023-07-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8X-80-E-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.384 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.384 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-11-21 | [9/27/2023];[5/14/2025] | 2023-11-21 | UL | 2023-09-18 | 2023-11-21 |  | N | Y | 0.026 | 0 | 0 | 43 | 51.5 | 60 | 0.038 | 0.077 | 0.115 | 0.192 | 0.288 | 0.384 | 93.57 | 95.86 | 97.16 | 97.68 | 97.51 | 97.07 | 97.24 | 95.1 | 95.45 | 96.87 | 97.53 | 97.47 | 97.14 | 97.2 | 94.75 | 95.01 | 96.57 | 97.36 | 97.37 | 97.08 | 97.03 | 2023-11-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8X-80-M-DOM-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.384 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.384 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2024-10-01 | [8/19/2024];[5/14/2025] | 2024-10-01 | UL | 2024-09-18 | 2024-10-01 |  | N | Y | 0.026 | 0 | 0 | 43 | 51.5 | 60 | 0.038 | 0.077 | 0.115 | 0.192 | 0.288 | 0.384 | 93.57 | 95.86 | 97.16 | 97.68 | 97.51 | 97.07 | 97.24 | 95.1 | 95.45 | 96.87 | 97.53 | 97.47 | 97.14 | 97.2 | 94.75 | 95.01 | 96.57 | 97.36 | 97.37 | 97.08 | 97.03 | 2024-10-01 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8X-80-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.384 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.384 | 240 | 97 | UL | [5/13/2026] | UL | [04/23/2021];[04/23/2021];[04/23/2021];[06/25/2021];[09/17/2021];[11/09/2021];[02/23/2022];[04/22/2022];[9/17/2022];[9/17/2022];[3/22/2023];[8/25/2023];[2/23/2024];[5/14/2025];{5/13/2026] | [V2.19.01];[V2.22.02];[V2.23.01];[V2.27.02];[V2.38.02];[V2.38.03];[V2.39.01];[V2.42.02];[2.48.01];[V2.45.04];[V2.45.02];[V2.51.01];[V2.56.01];[V2.61.01];[V2.63.01];[V8.14.02];[V10.31.01] | 2023-11-21 | [9/27/2023];[5/14/2025] | 2023-11-21 | UL | 2023-09-18 | 2023-11-21 |  | N | Y | 0.051 |  |  | 43 | 51.5 | 60 | 0.038 | 0.077 | 0.115 | 0.192 | 0.288 | 0.384 | 93.57 | 95.86 | 97.16 | 97.68 | 97.51 | 97.07 | 97.24 | 95.1 | 95.45 | 96.87 | 97.53 | 97.47 | 97.14 | 97.2 | 94.75 | 95.01 | 96.57 | 97.36 | 97.37 | 97.08 | 97.03 | 2023-11-21 | 2026-08-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ9N-A-DOM-US {208V} | N | Y | Y | Y | Y | Y | Y* |  | 0.405 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.405 | 208 | 97.5 | Intertek | [12/12/2025] | Intertek | [12/5/2025]; [12/12/2025] | [10.24.02, 10.26.06]; [10.31.01] | 2026-01-12 | [12/5/2025] | 2026-01-12 | Intertek | 2025-10-22 |  |  | N | Y | 0.063 |  |  | 28 | 36.5 | 45 | 0.040596 | 0.081192 | 0.12179 | 0.20298 | 0.30447 | 0.40596 | 96.308 | 97.3276 | 97.7982 | 97.7429 | 97.1765 | 96.3609 | 97.3021 | 96.5492 | 97.0145 | 97.6006 | 97.6667 | 97.2466 | 96.7499 | 97.313 | 96.2466 | 96.512 | 97.2952 | 97.5359 | 97.1272 | 96.6325 | 97.1424 | 2025-11-21 | 2026-06-22 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ9N-A-US {208V} | N | Y | Y | Y | Y | Y | Y* |  | 0.405 kW, 208 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.405 | 208 | 97.5 | Intertek | [12/12/2025] | Intertek | [12/5/2025]; [12/12/2025] | [10.24.02, 10.26.06]; [10.31.01] | 2026-01-12 | [12/5/2025] | 2026-01-12 | Intertek | 2025-10-22 |  |  | N | Y | 0.063 |  |  | 28 | 36.5 | 45 | 0.040596 | 0.081192 | 0.12179 | 0.20298 | 0.30447 | 0.40596 | 96.308 | 97.3276 | 97.7982 | 97.7429 | 97.1765 | 96.3609 | 97.3021 | 96.5492 | 97.0145 | 97.6006 | 97.6667 | 97.2466 | 96.7499 | 97.313 | 96.2466 | 96.512 | 97.2952 | 97.5359 | 97.1272 | 96.6325 | 97.1424 | 2025-11-21 | 2026-06-22 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ9N-A-DOM-US-HPB {208V} | N | Y | Y | Y | Y | Y | Y* |  | 0.415 kW, 208 Grid Support Utility Interactive Microinverter with PCS functionality | 0.415 | 208 | 97 | Intertek | [12/12/2025] | Intertek | [2/14/2025]; [12/12/2025] | [10.24.02, 10.26.06]; [10.31.01] | 2026-01-21 | [2/14/2025] | 2026-01-21 | Intertek | 2025-12-13 |  |  | N | Y | 0.051 |  |  | 30 | 37 | 45 | 0.042 | 0.083 | 0.125 | 0.208 | 0.311 | 0.415 | 96.14 | 97.08 | 97.74 | 97.75 | 97.3 | 96.64 | 97.36 | 96.13 | 96.69 | 97.46 | 97.6 | 97.24 | 96.59 | 97.24 | 96.42 | 96.32 | 97.12 | 97.41 | 97.07 | 96.45 | 97.05 | 2026-01-21 | 2026-06-22 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ9N-3P-277-A-DOM-US {277V} | N | Y | Y | Y | Y | Y | Y* |  | 0.427 kW, 277 Vac Grid Support Utility Interactive Microinverter with PCS functionality. | 0.427 | 277 | 97.5 | Intertek | [11/18/2025] | Intertek | [11/18/2025] | [10.24.02, 10.26.06] | 2025-12-22 | [11/18/2025] | 2025-12-22 | Intertek | 2025-11-18 |  |  | N | Y | 0.2 |  |  | 28 | 36.5 | 45 | 0.043 | 0.085 | 0.128 | 0.213 | 0.32 | 0.427 | 95.17 | 96.8 | 97.61 | 97.82 | 97.43 | 96.88 | 97.39 | 96.02 | 96.21 | 97.28 | 97.98 | 97.85 | 97.63 | 97.64 | 96.25 | 95.52 | 96.82 | 97.69 | 97.73 | 97.5 | 97.43 | 2025-12-22 | 2026-03-02
Enphase Energy, Inc. | IQ9N-3P-277-A-US {277V} | N | Y | Y | Y | Y | Y | Y* |  | 0.427 kW, 277 Vac Grid Support Utility Interactive Microinverter with PCS functionality. | 0.427 | 277 | 97.5 | Intertek | [11/18/2025] | Intertek | [11/18/2025] | [10.24.02, 10.26.06] | 2025-12-22 | [11/18/2025] | 2025-12-22 | Intertek | 2025-11-18 |  |  | N | Y | 0.2 |  |  | 28 | 36.5 | 45 | 0.043 | 0.085 | 0.128 | 0.213 | 0.32 | 0.427 | 95.17 | 96.8 | 97.61 | 97.82 | 97.43 | 96.88 | 97.39 | 96.02 | 96.21 | 97.28 | 97.98 | 97.85 | 97.63 | 97.64 | 96.25 | 95.52 | 96.82 | 97.69 | 97.73 | 97.5 | 97.43 | 2025-12-22 | 2026-03-02
Enphase Energy, Inc. | IQ9N-A-DOM-US {240V} | N | Y | Y | Y | Y | Y | Y* |  | 0.427 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.427 | 240 | 97.5 | Intertek | [12/12/2025] | Intertek | [12/5/2025]; [12/12/2025] | [10.24.02, 10.26.06]; [10.31.01] | 2026-01-12 | [12/5/2025] | 2026-01-12 | Intertek | 2025-10-22 |  |  | N | Y | 0.054 |  |  | 28 | 36.5 | 45 | 0.043 | 0.085 | 0.128 | 0.214 | 0.32 | 0.427 | 96.31 | 97.16 | 97.67 | 97.6 | 97.06 | 96.23 | 97.18 | 96.52 | 96.86 | 97.61 | 97.79 | 97.51 | 97.03 | 97.48 | 96.42 | 96.3 | 97.34 | 97.65 | 97.47 | 97.09 | 97.37 | 2025-11-21 | 2026-06-22 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ9N-A-US {240V} | N | Y | Y | Y | Y | Y | Y* |  | 0.427 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality | 0.427 | 240 | 97.5 | Intertek | [12/12/2025] | Intertek | [12/5/2025]; [12/12/2025] | [10.24.02, 10.26.06]; [10.31.01] | 2026-01-12 | [12/5/2025] | 2026-01-12 | Intertek | 2025-10-22 |  |  | N | Y | 0.054 |  |  | 28 | 36.5 | 45 | 0.043 | 0.085 | 0.128 | 0.214 | 0.32 | 0.427 | 96.31 | 97.16 | 97.67 | 97.6 | 97.06 | 96.23 | 97.18 | 96.52 | 96.86 | 97.61 | 97.79 | 97.51 | 97.03 | 97.48 | 96.42 | 96.3 | 97.34 | 97.65 | 97.47 | 97.09 | 97.37 | 2025-11-21 | 2026-06-22 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ9N-A-DOM-US-HPB {240V} | N | Y | Y | Y | Y | Y | Y* |  | 0.44 kW, 240 Grid Support Utility Interactive Microinverter with PCS functionality | 0.44 | 240 | 97.5 | Intertek | [12/12/2025] | Intertek | [2/14/2025]; [12/12/2025] | [10.24.02, 10.26.06]; [10.31.01] | 2026-01-21 | [2/14/2025] | 2026-01-21 | Intertek | 2025-12-13 |  |  | N | Y | 0.069 |  |  | 30 | 37 | 45 | 0.044 | 0.088 | 0.132 | 0.22 | 0.33 | 0.44 | 95.89 | 97.14 | 97.68 | 97.8 | 97.4 | 96.82 | 97.42 | 96.07 | 96.72 | 97.55 | 97.81 | 97.57 | 97.15 | 97.5 | 96.03 | 95.87 | 97.15 | 97.6 | 97.42 | 97.05 | 97.28 | 2026-01-21 | 2026-06-22 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8P-3P-72-E-DOM-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.475 kW, 208 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 0.475 | 208 | 97.5 | UL | [5/13/2026] | UL | [8/19/2024];[6/13/2025];{5/13/2026] | [2.57.03, 2.58.05];[8.14.02];{10.31.01] | 2024-10-01 | [6/13/2025] | 2024-10-01 | UL | 2024-09-26 | 2024-10-01 |  | N | Y | 0.056 |  |  | 35.5 | 45 | 53 | 0.048 | 0.096 | 0.143 | 0.239 | 0.358 | 0.478 | 95.79 | 96.67 | 97.5 | 97.67 | 97.25 | 96.49 | 97.24 | 96.14 | 96.13 | 97.37 | 97.9 | 97.77 | 97.42 | 97.59 | 96.14 | 95.53 | 97.11 | 97.81 | 97.78 | 97.5 | 97.51 | 2024-10-01 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8P-3P-72-E-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.475 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 0.475 | 208 | 97.5 | UL | [5/13/2026] | UL | [5/22/2024];[6/13/2025];{5/13/2026] | [2.57.03, 2.58.05];[8.14.02];{10.31.01] | 2024-06-21 | [6/13/2025] | 2024-06-21 | UL | 2023-09-27 | 2023-11-21 |  | N | Y | 0.056 |  |  | 35.5 | 45 | 53 | 0.048 | 0.096 | 0.143 | 0.239 | 0.358 | 0.478 | 95.79 | 96.67 | 97.5 | 97.67 | 97.25 | 96.49 | 97.24 | 96.14 | 96.13 | 97.37 | 97.9 | 97.77 | 97.42 | 97.59 | 96.14 | 95.53 | 97.11 | 97.81 | 97.78 | 97.5 | 97.51 | 2023-11-21 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8P-3P-72-M-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.475 kW, 208 Vac Grid Support Utility Interactive Inverter | 0.475 | 208 | 97.5 | UL | [5/13/2026] | UL | [5/22/2024];[6/13/2025];{5/13/2026] | [2.57.03, 2.58.05];[8.14.02];{10.31.01] | 2024-06-21 | [6/13/2025] | 2024-06-21 | UL | 2023-09-27 | 2023-11-21 |  | N | Y | 0.056 |  |  | 35.5 | 45 | 53 | 0.048 | 0.096 | 0.143 | 0.239 | 0.358 | 0.478 | 95.79 | 96.67 | 97.5 | 97.67 | 97.25 | 96.49 | 97.24 | 96.14 | 96.13 | 97.37 | 97.9 | 97.77 | 97.42 | 97.59 | 96.14 | 95.53 | 97.11 | 97.81 | 97.78 | 97.5 | 97.51 | 2023-11-21 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8P-72-2-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 475 VA, 240 Vac Grid Support Utility Interactive Inverter Microinverter | 0.475 | 240 | 97.5 | UL | [5/13/2026] | UL | [5/30/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-07-14 | [5/30/2025] | 2025-07-14 | UL | 2025-05-07 | 2025-07-14 |  | N | Y | 0.063 |  |  | 36 | 45.5 | 55 | 0.047544 | 0.095087 | 0.14263 | 0.23772 | 0.35658 | 0.47544 | 95.2787 | 95.6643 | 97.1046 | 97.4097 | 97.0208 | 96.2884 | 96.9384 | 96.162 | 95.2058 | 97.0719 | 97.7098 | 97.6733 | 97.3305 | 97.4078 | 96.0679 | 94.9954 | 96.7635 | 97.7275 | 97.8185 | 97.6721 | 97.4543 | 2024-02-01 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8P-72-M-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 475 VA, 240 Vac Grid Support Utility Interactive Inverter Microinverter | 0.475 | 240 | 97.5 | UL | [5/13/2026] | UL | [5/30/2025];{5/13/2026] | [V8.14.02];{10.31.01] | 2025-07-14 | [5/30/2025] | 2025-07-14 | UL | 2025-05-07 | 2025-07-14 |  | N | Y | 0.063 |  |  | 36 | 45.5 | 55 | 0.047544 | 0.095087 | 0.14263 | 0.23772 | 0.35658 | 0.47544 | 95.2787 | 95.6643 | 97.1046 | 97.4097 | 97.0208 | 96.2884 | 96.9384 | 96.162 | 95.2058 | 97.0719 | 97.7098 | 97.6733 | 97.3305 | 97.4078 | 96.0679 | 94.9954 | 96.7635 | 97.7275 | 97.8185 | 97.6721 | 97.4543 | 2025-07-11 | 2026-07-01 | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ9S-3P-277-B-DOM-US {277V} | N | Y | Y | Y | Y | Y | Y* |  | 0.548 kW, 277 Vac Grid Support Utility Interactive Microinverter | 0.548 | 277 | 97.5 | Intertek | [5/15/2026] | Intertek | [5/15/2026] | [10.24.02, 10.26.06, 10.32.02] | 2026-06-22 | [5/15/2026] | 2026-06-22 | Intertek | 2026-05-15 |  |  | N | Y | 0.22 |  |  | 32 | 43.5 | 55 | 0.055 | 0.11 | 0.164 | 0.274 | 0.411 | 0.548 | 94.63 | 96.11 | 97.42 | 97.86 | 97.69 | 97.25 | 97.47 | 96.19 | 95.19 | 97.02 | 97.78 | 97.82 | 97.6 | 97.51 | 95.38 | 94.34 | 96.35 | 97.48 | 97.61 | 97.42 | 97.17 | 2026-06-22 |  | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ9S-3P-277-B-US {277V} | N | Y | Y | Y | Y | Y | Y* |  | 0.548 kW, 277 Vac Grid Support Utility Interactive Microinverter | 0.548 | 277 | 97.5 | Intertek | [5/15/2026] | Intertek | [5/15/2026] | [10.24.02, 10.26.06, 10.32.02] | 2026-06-22 | [5/15/2026] | 2026-06-22 | Intertek | 2026-05-15 |  |  | N | Y | 0.22 |  |  | 32 | 43.5 | 55 | 0.055 | 0.11 | 0.164 | 0.274 | 0.411 | 0.548 | 94.63 | 96.11 | 97.42 | 97.86 | 97.69 | 97.25 | 97.47 | 96.19 | 95.19 | 97.02 | 97.78 | 97.82 | 97.6 | 97.51 | 95.38 | 94.34 | 96.35 | 97.48 | 97.61 | 97.42 | 97.17 | 2026-06-22 |  | Y | N | N | N | N | N | N | N | No Information Submitted
Enphase Energy, Inc. | IQ8D-72-E-US {208V} | N | N | Y | Y | Y | Y | Y* | Y | 633 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.64 | 208 | 97.5 | No Information Submitted | No Information Submitted | UL | [6/7/2021];[01/14/2022] | [v2.27.03];[v2.40.01] | 2022-01-03 | [6/7/2021];[01/14/2022] | 2022-01-03 | UL | 2021-09-24 | 2022-01-03 |  | N | Y | 0.04265 |  |  | 60 | 77.5 | 95 | 0.064042 | 0.12808 | 0.19213 | 0.32021 | 0.48031 | 0.64042 | 96.3423 | 96.6805 | 97.7456 | 97.9048 | 97.4033 | 96.7427 | 97.4381 | 96.4393 | 97.1473 | 97.546 | 97.9638 | 97.735 | 97.2609 | 97.6554 | 96.2972 | 96.9607 | 97.1235 | 97.7774 | 97.6043 | 97.174 | 97.477 | 2022-01-03 | 2022-08-01
EPC Power Corp. | HY LC12/6-7 {480V} | Y | N | Y | Y | Y | N | N | N | 220 kVA, 480 Vac, 3 phase Grid Support Utility Interactive Hybrid Inverter with PV MPPT and DC input | 220.033 | 480 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [09/25/2018] | [042C314] | 2019-01-15 | [09/25/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 19.2 |  |  | 455 | 475 | 600 | 22.0033 | 44.0067 | 66.01 | 110.0167 | 165.025 | 220.0333 | 95.0157 | 96.16 | 96.4114 | 96.3571 | 96.0943 | 95.7657 | 96.1313 | 93.9614 | 95.3957 | 95.6729 | 95.7343 | 95.5243 | 95.18 | 95.5001 | 94.3386 | 95.8 | 96.0971 | 96.1657 | 96.0143 | 95.7186 | 95.9635 | 2019-01-15
EPC Power Corp. | 50-100181 {480V} | Y | Y | Y | Y | Y | Y | Y* | N | 1043 kVA, 480Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 1044.2 | 480 | 98 | TUV Rheinland | [3/4/2024] | TUV Rheinland of North America | [04/14/2021] | [fe924e5] | 2022-01-03 | [04/14/2021] | 2022-01-03 | TUV Rheinland | 2022-01-24 | No Information Submitted |  | N | N | 291.17 |  |  | 720 | 1110 | 1500 | 104.42 | 208.84 | 313.26 | 522.1 | 783.15 | 1044.2 | 97.9098 | 98.5852 | 98.6358 | 98.4572 | 98.0884 | 97.6996 | 98.2298 | 97.9854 | 98.6056 | 98.5864 | 98.3194 | 97.897 | 97.4388 | 98.0845 | 95.7674 | 97.4938 | 97.8344 | 97.9364 | 97.6856 | 97.3356 | 97.6523 | 2024-09-03
EPC Power Corp. | 50-100181 {600V} | Y | Y | Y | Y | Y | Y | Y* | N | 1300 kVA, 600Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 1304.151 | 600 | 98.5 | TUV Rheinland | [3/4/2024] | TUV Rheinland of North America | [04/14/2021] | [fe924e5] | 2022-01-03 | [04/14/2021] | 2022-01-03 | TUV Rheinland | 2022-01-24 | No Information Submitted |  | N | N | 248 |  |  | 925 | 1225 | 1500 | 130.4151 | 260.8303 | 391.2454 | 652.0756 | 978.1135 | 1304.1513 | 98.0532 | 98.725 | 98.788 | 98.674 | 98.3996 | 98.0802 | 98.4903 | 97.3176 | 98.4686 | 98.6054 | 98.5492 | 98.2394 | 97.8678 | 98.3044 | 97.389 | 98.2938 | 98.479 | 98.4228 | 98.1552 | 97.8514 | 98.2113 | 2024-09-03
EPC Power Corp. | 50-100181 {690V} | Y | Y | Y | Y | Y | Y | Y* | N | 1500 kVA, 690Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 1504.9 | 690 | 98.5 | TUV Rheinland | [3/4/2024] | TUV Rheinland of North America | [04/14/2021] | [fe924e5] | 2022-01-03 | [04/14/2021] | 2022-01-03 | TUV Rheinland | 2022-01-24 | No Information Submitted |  | N | N | 250.08 |  |  | 1100 | 1330 | 1500 | 150.49 | 300.98 | 451.47 | 752.45 | 1128.675 | 1504.9 | 98.0852 | 98.4231 | 98.6012 | 98.6169 | 98.4248 | 98.1524 | 98.459 | 97.9106 | 98.3437 | 98.5608 | 98.5504 | 98.3682 | 98.0579 | 98.3945 | 97.5318 | 98.1167 | 98.3924 | 98.4846 | 98.3078 | 98.0463 | 98.3014 | 2024-09-03
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {240V} | Y | Y | N | N | N | N | Y* |  | 11.5 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 11.349 | 240 | 96 | TUV Rheinland of North America | [09/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-09-30 |  |  | N | N | 14.23 |  |  | 250 | 375 | 480 | 1.135 | 2.27 | 3.405 | 5.675 | 8.512 | 11.349 | 94.73 | 96.12 | 96.22 | 96.17 | 95.69 | 95.04 | 95.81 | 95.27 | 96.65 | 96.8 | 96.78 | 96.32 | 95.6 | 96.41 | 94.61 | 96.12 | 96.41 | 96.41 | 96.04 | 95.54 | 96.08 | 2025-12-11 | 2026-01-12
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {240V} | Y | Y | N | N | N | N | Y* |  | 11.5 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 11.349 | 240 | 96 | TUV Rheinland of North America | [09/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-09-30 |  |  | N | N | 14.23 |  |  | 250 | 375 | 480 | 1.135 | 2.27 | 3.405 | 5.675 | 8.512 | 11.349 | 94.73 | 96.12 | 96.22 | 96.17 | 95.69 | 95.04 | 95.81 | 95.27 | 96.65 | 96.8 | 96.78 | 96.32 | 95.6 | 96.41 | 94.61 | 96.12 | 96.41 | 96.41 | 96.04 | 95.54 | 96.08 | 2025-12-11 | 2026-01-12
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {208V, 5.0kW} | Y | Y | N | N | N | N | Y* |  | 5.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.0315 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.50315 | 1.0063 | 1.5094 | 2.5158 | 3.7736 | 5.0315 | 90.6481 | 94.2205 | 95.2844 | 95.818 | 95.719 | 95.6238 | 95.4051 | 91.4714 | 94.6072 | 95.6642 | 96.2334 | 96.1263 | 96.1763 | 95.8337 | 91.2682 | 94.5047 | 95.3835 | 95.9362 | 95.9699 | 95.8838 | 95.6268 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {208V, 5.0kW} | Y | Y | N | N | N | N | Y* |  | 5.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.0315 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.50315 | 1.0063 | 1.5094 | 2.5158 | 3.7736 | 5.0315 | 90.6481 | 94.2205 | 95.2844 | 95.818 | 95.719 | 95.6238 | 95.4051 | 91.4714 | 94.6072 | 95.6642 | 96.2334 | 96.1263 | 96.1763 | 95.8337 | 91.2682 | 94.5047 | 95.3835 | 95.9362 | 95.9699 | 95.8838 | 95.6268 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {208V, 5.0kW} | Y | Y | N | N | N | N | Y* |  | 5.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.0315 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.50315 | 1.0063 | 1.5094 | 2.5158 | 3.7736 | 5.0315 | 90.6481 | 94.2205 | 95.2844 | 95.818 | 95.719 | 95.6238 | 95.4051 | 91.4714 | 94.6072 | 95.6642 | 96.2334 | 96.1263 | 96.1763 | 95.8337 | 91.2682 | 94.5047 | 95.3835 | 95.9362 | 95.9699 | 95.8838 | 95.6268 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {240V, 5.8kW} | Y | Y | N | N | N | N | Y* |  | 5.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.8122 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.58122 | 1.1624 | 1.7437 | 2.9061 | 4.3591 | 5.8122 | 91.6915 | 94.9083 | 95.8501 | 96.1662 | 96.2831 | 96.1082 | 95.9454 | 92.4874 | 95.3794 | 96.2015 | 96.7833 | 96.8356 | 96.7084 | 96.4954 | 92.0025 | 94.966 | 95.8275 | 96.5099 | 96.4855 | 96.4554 | 96.1548 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {240V, 5.8kW} | Y | Y | N | N | N | N | Y* |  | 5.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.8122 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.58122 | 1.1624 | 1.7437 | 2.9061 | 4.3591 | 5.8122 | 91.6915 | 94.9083 | 95.8501 | 96.1662 | 96.2831 | 96.1082 | 95.9454 | 92.4874 | 95.3794 | 96.2015 | 96.7833 | 96.8356 | 96.7084 | 96.4954 | 92.0025 | 94.966 | 95.8275 | 96.5099 | 96.4855 | 96.4554 | 96.1548 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {240V, 5.8kW} | Y | Y | N | N | N | N | Y* |  | 5.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.8122 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.58122 | 1.1624 | 1.7437 | 2.9061 | 4.3591 | 5.8122 | 91.6915 | 94.9083 | 95.8501 | 96.1662 | 96.2831 | 96.1082 | 95.9454 | 92.4874 | 95.3794 | 96.2015 | 96.7833 | 96.8356 | 96.7084 | 96.4954 | 92.0025 | 94.966 | 95.8275 | 96.5099 | 96.4855 | 96.4554 | 96.1548 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {208V, 6.6kW} | Y | Y | N | N | N | N | Y* |  | 6.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.68 | 208 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.6682 | 1.3364 | 2.0046 | 3.341 | 5.0115 | 6.682 | 92.4875 | 95.2327 | 95.7798 | 95.8418 | 95.7669 | 95.3992 | 95.6079 | 92.8564 | 95.463 | 96.1177 | 96.1376 | 96.3349 | 96.0108 | 96.0685 | 92.4878 | 95.063 | 95.7129 | 96.0218 | 95.909 | 95.7447 | 95.7218 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {208V, 6.6kW} | Y | Y | N | N | N | N | Y* |  | 6.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.68 | 208 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.6682 | 1.3364 | 2.0046 | 3.341 | 5.0115 | 6.682 | 92.4875 | 95.2327 | 95.7798 | 95.8418 | 95.7669 | 95.3992 | 95.6079 | 92.8564 | 95.463 | 96.1177 | 96.1376 | 96.3349 | 96.0108 | 96.0685 | 92.4878 | 95.063 | 95.7129 | 96.0218 | 95.909 | 95.7447 | 95.7218 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {208V, 6.6kW} | Y | Y | N | N | N | N | Y* |  | 6.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.68 | 208 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.6682 | 1.3364 | 2.0046 | 3.341 | 5.0115 | 6.682 | 92.4875 | 95.2327 | 95.7798 | 95.8418 | 95.7669 | 95.3992 | 95.6079 | 92.8564 | 95.463 | 96.1177 | 96.1376 | 96.3349 | 96.0108 | 96.0685 | 92.4878 | 95.063 | 95.7129 | 96.0218 | 95.909 | 95.7447 | 95.7218 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {240V, 7.6kW} | Y | Y | N | N | N | N | Y* |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6 | 240 | 96.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.76013 | 1.5203 | 2.2804 | 3.8007 | 5.701 | 7.6013 | 93.2739 | 95.6475 | 96.2084 | 96.2358 | 96.0886 | 95.7839 | 95.984 | 93.6997 | 95.9983 | 96.6393 | 96.8057 | 96.6768 | 96.4222 | 96.5336 | 93.4787 | 95.6119 | 96.2598 | 96.5683 | 96.4535 | 96.187 | 96.28 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {240V, 7.6kW} | Y | Y | N | N | N | N | Y* |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6 | 240 | 96.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.76013 | 1.5203 | 2.2804 | 3.8007 | 5.701 | 7.6013 | 93.2739 | 95.6475 | 96.2084 | 96.2358 | 96.0886 | 95.7839 | 95.984 | 93.6997 | 95.9983 | 96.6393 | 96.8057 | 96.6768 | 96.4222 | 96.5336 | 93.4787 | 95.6119 | 96.2598 | 96.5683 | 96.4535 | 96.187 | 96.28 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {240V, 7.6kW} | Y | Y | N | N | N | N | Y* |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6 | 240 | 96.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.76013 | 1.5203 | 2.2804 | 3.8007 | 5.701 | 7.6013 | 93.2739 | 95.6475 | 96.2084 | 96.2358 | 96.0886 | 95.7839 | 95.984 | 93.6997 | 95.9983 | 96.6393 | 96.8057 | 96.6768 | 96.4222 | 96.5336 | 93.4787 | 95.6119 | 96.2598 | 96.5683 | 96.4535 | 96.187 | 96.28 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {240V, 9.6kW} | Y | Y | N | N | N | N | Y* |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.63 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.963 | 1.926 | 2.889 | 4.815 | 7.2225 | 9.63 | 94.1685 | 95.9701 | 96.256 | 96.1966 | 95.8452 | 95.4484 | 95.8876 | 94.6628 | 96.3268 | 96.7267 | 96.772 | 96.422 | 95.9912 | 96.4354 | 94.1688 | 95.9942 | 96.4864 | 96.5372 | 96.2844 | 95.7755 | 96.2371 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {240V, 9.6kW} | Y | Y | N | N | N | N | Y* |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.63 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.963 | 1.926 | 2.889 | 4.815 | 7.2225 | 9.63 | 94.1685 | 95.9701 | 96.256 | 96.1966 | 95.8452 | 95.4484 | 95.8876 | 94.6628 | 96.3268 | 96.7267 | 96.772 | 96.422 | 95.9912 | 96.4354 | 94.1688 | 95.9942 | 96.4864 | 96.5372 | 96.2844 | 95.7755 | 96.2371 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {240V, 9.6kW} | Y | Y | N | N | N | N | Y* |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.63 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.963 | 1.926 | 2.889 | 4.815 | 7.2225 | 9.63 | 94.1685 | 95.9701 | 96.256 | 96.1966 | 95.8452 | 95.4484 | 95.8876 | 94.6628 | 96.3268 | 96.7267 | 96.772 | 96.422 | 95.9912 | 96.4354 | 94.1688 | 95.9942 | 96.4864 | 96.5372 | 96.2844 | 95.7755 | 96.2371 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {208V, 9.9kW} | Y | Y | N | N | N | N | Y* |  | 9.9 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.9 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.99008 | 1.9802 | 2.9702 | 4.9504 | 7.4256 | 9.9008 | 94.0773 | 95.7729 | 95.5128 | 95.2461 | 95.2174 | 94.5651 | 95.2084 | 94.6946 | 96.18 | 96.3538 | 96.3192 | 95.6452 | 95.1092 | 95.8337 | 94.0239 | 95.6448 | 95.9748 | 95.8924 | 95.5 | 94.9997 | 95.5626 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {208V, 9.9kW} | Y | Y | N | N | N | N | Y* |  | 9.9 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.9 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.99008 | 1.9802 | 2.9702 | 4.9504 | 7.4256 | 9.9008 | 94.0773 | 95.7729 | 95.5128 | 95.2461 | 95.2174 | 94.5651 | 95.2084 | 94.6946 | 96.18 | 96.3538 | 96.3192 | 95.6452 | 95.1092 | 95.8337 | 94.0239 | 95.6448 | 95.9748 | 95.8924 | 95.5 | 94.9997 | 95.5626 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {208V, 9.9kW} | Y | Y | N | N | N | N | Y* |  | 9.9 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.9 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.99008 | 1.9802 | 2.9702 | 4.9504 | 7.4256 | 9.9008 | 94.0773 | 95.7729 | 95.5128 | 95.2461 | 95.2174 | 94.5651 | 95.2084 | 94.6946 | 96.18 | 96.3538 | 96.3192 | 95.6452 | 95.1092 | 95.8337 | 94.0239 | 95.6448 | 95.9748 | 95.8924 | 95.5 | 94.9997 | 95.5626 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {240V, 11.5kW} | Y | Y | N | N | N | N | Y* |  | 11.5 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.3494 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 14.23 |  |  | 250 | 375 | 480 | 1.1349 | 2.2699 | 3.4048 | 5.6747 | 8.512 | 11.3494 | 94.727 | 96.1155 | 96.2152 | 96.1709 | 95.6922 | 95.0392 | 95.8054 | 95.2658 | 96.6478 | 96.8035 | 96.7768 | 96.3178 | 95.6015 | 96.4111 | 94.6132 | 96.1217 | 96.4059 | 96.407 | 96.0399 | 95.5409 | 96.083 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Expert Computer Int'l Inc. | ExpertPower 10KW Hybrid Inverter {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.0186 | 240 | 95.5 | Intertek | [3/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.8 | 9 | 91.6 | 92.9 | 94.6 | 95.8 | 95.4 | 95.6 | 95.4 | 92.1 | 93.3 | 95 | 96.2 | 96.4 | 96.1 | 95.8 | 89.3 | 92.1 | 93.6 | 95.2 | 96 | 95.7 | 95 | 2026-01-12
Fengfan Co., Ltd. Power Supply Branch | SPT-OMOBFP1-A-6KW {120V} | Y | Y | N | N | N | N | N | N | 6 kW, 120 Vac Split Phase, Transformerless Grid Support Utility Interactive Inverter | 6.0177 | 120 | 93.5 | Intertek | [1/17/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 43 |  |  | 250 | 370 | 500 | 0.60177 | 1.2035 | 1.8053 | 3.0088 | 4.5132 | 6.0177 | 84.5 | 90.4 | 92.4 | 93.9 | 94.5 | 94.4 | 93.5 | 83.8 | 90.3 | 92.5 | 94.1 | 94.9 | 94.9 | 93.7 | 80.8 | 88.9 | 91 | 93.4 | 94.1 | 94.3 | 92.8 | 2024-05-13
Fortress Power LLC | Avalon HV PC50 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.0017 | 240 | 96.5 | CSA Group | [9/8/2023] | CSA Group | [9/8/2023] | [A2] | 2024-08-01 | [9/8/2023] | 2024-08-01 | CSA Group | 2024-01-05 | 2024-08-01 |  | N | N | 18.83 |  |  | 140 | 370 | 450 | 0.50017 | 1.0003 | 1.5005 | 2.5008 | 3.7512 | 5.0017 | 94.2264 | 95.2572 | 96.6079 | 96.5986 | 96.7891 | 96.6855 | 96.5431 | 95.3984 | 95.7768 | 96.5277 | 96.5548 | 96.8363 | 96.978 | 96.6367 | 95.1057 | 95.5303 | 96.4585 | 96.5737 | 96.7108 | 96.7105 | 96.5285 | 2024-08-01
Fortress Power LLC | EdgeOn Duo 7.5 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 5 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 5.02 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 92.68 | 95.266 | 95.93 | 96.35 | 96.16 | 95.992 | 95.98 | 93.568 | 95.856 | 96.53 | 97.03 | 97.08 | 96.97 | 96.7963 | 93.73 | 95.934 | 96.5 | 96.81 | 96.9 | 96.81 | 96.6535 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 7.5 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 5 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 5.04 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.504 | 1.008 | 1.512 | 2.52 | 3.78 | 5.04 | 92.994 | 95.51 | 96.13 | 96.56 | 96.34 | 96.22 | 96.1797 | 93.67 | 95.992 | 96.75 | 97.31 | 97.43 | 97.378 | 97.0983 | 93.79 | 96.142 | 96.614 | 96.98 | 97.24 | 97.24 | 96.9174 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 9 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 6 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 6.1237 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 19.2 |  |  | 200 | 360 | 480 | 0.61237 | 1.2247 | 1.8371 | 3.0618 | 4.5927 | 6.1237 | 91.5057 | 94.3751 | 95.4429 | 96.1451 | 96.2033 | 96.0221 | 95.8115 | 93.6071 | 95.9507 | 96.6981 | 97.1632 | 97.1394 | 97.0155 | 96.8845 | 93.0132 | 95.454 | 96.3177 | 96.9016 | 96.9299 | 96.7629 | 96.6117 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 9 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 6 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 6.1493 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 19.2 |  |  | 200 | 360 | 480 | 0.61493 | 1.2299 | 1.8448 | 3.0747 | 4.612 | 6.1493 | 91.5991 | 94.4496 | 95.4631 | 96.2597 | 96.4111 | 96.355 | 95.9722 | 93.875 | 96.1389 | 96.881 | 97.3815 | 97.4928 | 97.4245 | 97.1802 | 92.6866 | 95.4464 | 96.4097 | 97.0954 | 97.2951 | 97.2686 | 96.8688 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | Avalon HV PC76 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6043 | 240 | 97 | CSA Group | [9/8/2023] | CSA Group | [9/8/2023] | [A2] | 2024-08-01 | [9/8/2023] | 2024-08-01 | CSA Group | 2024-01-05 | 2024-08-01 |  | N | N | 16.33 |  |  | 175 | 380 | 450 | 0.76043 | 1.5209 | 2.2813 | 3.8022 | 5.7032 | 7.6043 | 95.7781 | 96.5695 | 97.1423 | 97.1163 | 97.2718 | 97.3248 | 97.1314 | 95.0243 | 96.1104 | 97.1692 | 97.2619 | 97.2861 | 97.6278 | 97.1348 | 94.7344 | 96.1352 | 96.951 | 97.088 | 97.1471 | 97.3269 | 96.973 | 2024-08-01
Fortress Power LLC | EdgeOn Duo 12 Lite {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 7.6 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 7.6472 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.76472 | 1.5294 | 2.2942 | 3.8236 | 5.7354 | 7.6472 | 92.9526 | 95.5516 | 96.215 | 96.6536 | 96.4528 | 96.189 | 96.2682 | 89.7494 | 96.0782 | 96.7932 | 97.1622 | 96.9742 | 96.771 | 96.648 | 94.0664 | 96.2374 | 96.769 | 97.1184 | 96.9078 | 96.7056 | 96.7781 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 12 Lite {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 7.6 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 7.648 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.736 | 7.648 | 92.946 | 95.544 | 96.21 | 96.648 | 96.448 | 96.186 | 96.2631 | 93.74 | 96.074 | 96.788 | 97.158 | 96.97 | 96.766 | 96.8034 | 94.064 | 96.234 | 96.766 | 97.116 | 96.906 | 96.704 | 96.7759 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-ENVY-8K {208V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 7.8599 | 208 | 96.5 | Intertek | [3/21/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-04-03 |  | N | N | 18.53 |  |  | 210 | 360 | 480 | 0.78599 | 1.572 | 2.358 | 3.93 | 5.895 | 7.8599 | 92.7458 | 94.8821 | 95.7877 | 96.2814 | 95.7548 | 95.5452 | 95.6949 | 95.3183 | 96.7852 | 96.9298 | 97.2401 | 96.7733 | 96.6331 | 96.8255 | 94.866 | 96.387 | 96.7215 | 97.1053 | 96.6941 | 96.6144 | 96.6913 | 2023-04-03 | 2025-05-12
Fortress Power LLC | FP-ENVY-8K {240V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 7.8627 | 240 | 96.5 | Intertek | [3/21/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-04-03 |  | N | N | 18.84 |  |  | 210 | 360 | 480 | 0.78627 | 1.5725 | 2.3588 | 3.9313 | 5.897 | 7.8627 | 92.9578 | 94.8899 | 95.7481 | 96.2838 | 95.9702 | 95.8604 | 95.8294 | 95.5741 | 96.5787 | 96.6854 | 97.0389 | 96.7425 | 96.7486 | 96.7433 | 94.682 | 96.1785 | 96.6318 | 96.9367 | 96.7571 | 96.7998 | 96.67 | 2023-04-03 | 2025-05-12
Fortress Power LLC | EdgeOn Duo 12 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 8.0472 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.80472 | 1.6094 | 2.4142 | 4.0236 | 6.0354 | 8.0472 | 92.9526 | 95.5528 | 96.2152 | 96.6546 | 96.452 | 96.1892 | 96.2681 | 93.7514 | 96.077 | 96.7964 | 97.1666 | 96.974 | 96.7728 | 96.8093 | 94.0688 | 96.2392 | 96.77 | 97.1224 | 96.9124 | 96.6488 | 96.7788 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 12 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 8 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 8.06 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.806 | 1.612 | 2.418 | 4.03 | 6.045 | 8.06 | 92.852 | 95.4494 | 96.1102 | 96.5538 | 96.3506 | 96.0918 | 96.1665 | 93.649 | 95.9818 | 96.693 | 97.0644 | 96.8732 | 96.6702 | 96.708 | 93.969 | 96.1426 | 96.6718 | 97.023 | 96.8134 | 96.5544 | 96.6802 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-ENVY-10K {208V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 9.7577 | 208 | 96.5 | Intertek | [3/21/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-04-03 |  | N | N | 14.8 |  |  | 210 | 360 | 480 | 0.97577 | 1.9515 | 2.9273 | 4.8789 | 7.3183 | 9.7577 | 92.7092 | 94.8879 | 95.3456 | 95.9721 | 95.5079 | 95.3565 | 95.4354 | 96.1203 | 96.8726 | 97.0518 | 97.3038 | 96.7285 | 96.5437 | 96.8618 | 95.0454 | 96.5267 | 96.8926 | 97.167 | 96.5064 | 96.4285 | 96.6301 | 2023-04-03 | 2025-05-12
Fortress Power LLC | FP-ENVY-10K {240V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 9.7586 | 240 | 96.5 | Intertek | [3/21/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-04-03 |  | N | N | 14.3 |  |  | 210 | 360 | 480 | 0.97586 | 1.9517 | 2.9276 | 4.8793 | 7.3189 | 9.7586 | 93.035 | 95.0464 | 95.7433 | 96.0352 | 95.4309 | 95.34 | 95.4757 | 95.1061 | 96.6509 | 97.0749 | 97.2195 | 96.6243 | 96.5263 | 96.7391 | 94.2113 | 96.1002 | 96.6822 | 96.9911 | 96.5706 | 96.5369 | 96.5527 | 2023-04-03 | 2025-05-12
Fortress Power LLC | Avalon HV PC100 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.0007 | 240 | 97 | CSA Group | [9/8/2023] | CSA Group | [9/8/2023] | [A2] | 2024-08-01 | [9/8/2023] | 2024-08-01 | CSA Group | 2024-01-05 | 2024-08-01 |  | N | N | 16.38 |  |  | 230 | 380 | 450 | 1.0001 | 2.0001 | 3.0002 | 5.0003 | 7.5005 | 10.0007 | 93.5666 | 96.1068 | 97.393 | 97.2724 | 97.3298 | 97.2051 | 97.1074 | 93.5201 | 95.7429 | 97.2657 | 97.3249 | 97.2118 | 97.3903 | 97.0298 | 92.7828 | 95.4556 | 97.3767 | 97.3334 | 97.2796 | 97.6002 | 97.0475 | 2024-08-01
Fortress Power LLC | EdgeOn Duo 15 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 10.1396 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 16.94 |  |  | 200 | 360 | 480 | 1.014 | 2.0279 | 3.0419 | 5.0698 | 7.6047 | 10.1396 | 93.0477 | 95.5809 | 96.2415 | 96.6629 | 96.4516 | 96.2021 | 96.2786 | 93.7158 | 96.0665 | 96.8163 | 97.1487 | 96.9642 | 96.7822 | 96.8013 | 94.0472 | 96.2511 | 96.7916 | 97.1155 | 96.9244 | 96.6588 | 96.7866 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 15 Lite {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 10.1472 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 18 |  |  | 200 | 360 | 480 | 1.0147 | 2.0294 | 3.0442 | 5.0736 | 7.6104 | 10.1472 | 92.9963 | 95.5759 | 96.2237 | 96.6613 | 96.4562 | 96.1983 | 96.2761 | 93.7907 | 96.1027 | 96.8102 | 97.1618 | 96.9743 | 96.7739 | 96.8131 | 94.1119 | 96.2672 | 96.7835 | 97.1258 | 96.9159 | 96.6586 | 96.7866 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 15 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 10.1858 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 16.94 |  |  | 200 | 360 | 480 | 1.0186 | 2.0372 | 3.0557 | 5.0929 | 7.6393 | 10.1858 | 92.9095 | 95.4795 | 96.1203 | 96.5624 | 96.3577 | 96.1012 | 96.1775 | 93.6611 | 96.0245 | 96.7245 | 97.0669 | 96.879 | 96.6799 | 96.7185 | 94.0672 | 96.1747 | 96.6706 | 96.9939 | 96.8177 | 96.5602 | 96.682 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 15 Lite {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 10.1858 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 18 |  |  | 200 | 360 | 480 | 1.0186 | 2.0372 | 3.0557 | 5.0929 | 7.6393 | 10.1858 | 92.8933 | 95.4787 | 96.1281 | 96.5592 | 96.3579 | 96.0975 | 96.177 | 93.6955 | 96.0051 | 96.7063 | 97.0717 | 96.8789 | 96.675 | 96.7174 | 94.0173 | 96.1625 | 96.6817 | 96.9927 | 96.8158 | 96.5601 | 96.6795 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-ENVY-12K {208V} | Y | Y | N | N | N | N | Y* | Y | 12 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 10.4994 | 208 | 96.5 | Intertek | [3/22/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-03-13 |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.0499 | 2.0999 | 3.1498 | 5.2497 | 7.8745 | 10.4994 | 93.4773 | 95.2677 | 95.9298 | 95.8461 | 95.6083 | 95.2856 | 95.5784 | 95.0713 | 96.6555 | 97.0252 | 97.3102 | 97.0957 | 96.4058 | 96.9948 | 94.2867 | 96.7139 | 97.1633 | 96.953 | 96.7744 | 96.4653 | 96.7406 | 2023-03-13 | 2025-02-11
Fortress Power LLC | Avalon HV PC114 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.406 | 240 | 97 | CSA Group | [9/8/2023] | CSA Group | [9/8/2023] | [A2] | 2024-08-01 | [9/8/2023] | 2024-08-01 | CSA Group | 2024-01-05 | 2024-08-01 |  | N | N | 15.36 |  |  | 245 | 380 | 450 | 1.1406 | 2.2812 | 3.4218 | 5.703 | 8.5545 | 11.406 | 94.7721 | 96.19 | 97.0866 | 97.3773 | 97.2555 | 97.2709 | 97.109 | 95.985 | 96.8789 | 96.8812 | 97.034 | 97.2274 | 97.345 | 97.084 | 95.5491 | 96.6497 | 97.0462 | 97.1786 | 97.2181 | 97.5716 | 97.1117 | 2024-08-01
Fortress Power LLC | EdgeOn Duo 15 Pro {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.4 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 11.5669 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 19 |  |  | 200 | 360 | 480 | 1.1567 | 2.3134 | 3.4701 | 5.7834 | 8.6752 | 11.5669 | 93.0675 | 95.5749 | 96.2997 | 96.6409 | 96.4392 | 96.2088 | 96.2752 | 93.6781 | 96.0439 | 96.7972 | 97.1353 | 96.9536 | 96.7793 | 96.7878 | 94.0465 | 96.3229 | 96.8228 | 97.1182 | 96.9286 | 96.6545 | 96.7965 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 15 Pro {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.4 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 11.6088 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 19 |  |  | 200 | 360 | 480 | 1.1609 | 2.3218 | 3.4827 | 5.8044 | 8.7066 | 11.6088 | 92.8881 | 95.4935 | 96.1138 | 96.5693 | 96.353 | 96.1025 | 96.1756 | 93.6426 | 96.0296 | 96.7159 | 97.0645 | 96.8809 | 96.677 | 96.7174 | 94.0961 | 96.1711 | 96.6734 | 96.9968 | 96.8241 | 96.5565 | 96.6871 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-ENVY-12K {240V} | Y | Y | N | N | N | N | Y* | Y | 12 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 11.9326 | 240 | 97 | Intertek | [3/22/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-03-13 |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.1933 | 2.3865 | 3.5798 | 5.9663 | 8.9494 | 11.9326 | 95.0246 | 96.0981 | 96.5396 | 96.4958 | 96.126 | 95.9005 | 96.1965 | 96.5925 | 97.1942 | 97.5102 | 97.3417 | 97.2365 | 97.1037 | 97.2569 | 95.8173 | 97.0077 | 97.4221 | 97.2641 | 97.1385 | 97.0353 | 97.1344 | 2023-03-13 | 2025-02-11
Fortress Power LLC | FP-Envy 15K {208V} | Y | Y | Y | Y | Y | Y | Y |  | 12.9 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 13.899 | 208 | 96.5 | Intertek | [9/1/2025] | Intertek | [9/1/2025] | [fA1.0] | 2025-11-21 | [8/1/2025] | 2025-11-21 | Intertek | 2025-10-28 |  |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.39 | 2.78 | 4.17 | 6.949 | 10.424 | 13.899 | 95.22 | 96.36 | 96.33 | 96.36 | 96 | 95.99 | 96.1 | 95.54 | 96.57 | 96.97 | 97.17 | 97.07 | 96.25 | 96.95 | 95.6 | 96.83 | 97.38 | 97.17 | 97.09 | 96.97 | 97.06 | 2025-11-21 | 2026-01-12
Fortress Power LLC | FP-Envy Duo 21 {208V} | Y | Y | Y | Y | Y | Y | Y |  | 13.8 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 13.899 | 208 | 96.5 | Intertek | [9/1/2025] | Intertek | [9/1/2025] | [fA1.0] | 2025-11-21 | [8/1/2025] | 2025-11-21 | Intertek | 2025-10-28 |  |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.39 | 2.78 | 4.17 | 6.949 | 10.424 | 13.899 | 95.22 | 96.36 | 96.33 | 96.36 | 96 | 95.99 | 96.1 | 95.54 | 96.57 | 96.97 | 97.17 | 97.07 | 96.25 | 96.95 | 95.6 | 96.83 | 97.38 | 97.17 | 97.09 | 96.97 | 97.06 | 2025-11-21 | 2026-01-12
Fortress Power LLC | FP-Envy 15K {240V} | Y | Y | Y | Y | Y | Y | Y |  | 15 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 16.153 | 240 | 97 | Intertek | [9/1/2025] | Intertek | [9/1/2025] | [fA1.0] | 2025-11-21 | [8/1/2025] | 2025-11-21 | Intertek | 2025-10-28 |  |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.615 | 3.231 | 4.846 | 8.077 | 12.115 | 16.153 | 95.1 | 96 | 96.39 | 96.4 | 96.73 | 95.86 | 96.48 | 96.47 | 97.1 | 97.48 | 97.12 | 97.08 | 96.94 | 97.1 | 95.46 | 96.91 | 97.25 | 97.17 | 96.99 | 96.82 | 96.99 | 2025-11-21 | 2026-01-12
Fortress Power LLC | FP-Envy Duo 21 {240V} | Y | Y | Y | Y | Y | Y | Y |  | 16 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 16.153 | 240 | 97 | Intertek | [9/1/2025] | Intertek | [9/1/2025] | [fA1.0] | 2025-11-21 | [8/1/2025] | 2025-11-21 | Intertek | 2025-10-28 |  |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.615 | 3.231 | 4.846 | 8.077 | 12.115 | 16.153 | 95.1 | 96 | 96.39 | 96.4 | 96.73 | 95.86 | 96.48 | 96.47 | 97.1 | 97.48 | 97.12 | 97.08 | 96.94 | 97.1 | 95.46 | 96.91 | 97.25 | 97.17 | 96.99 | 96.82 | 96.99 | 2025-11-21 | 2026-01-12
Fortress Power LLC | FP-Nano-30k-L {208V} | Y | Y | N | N | N | N | Y |  | 25.883548 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality | 25.8835 | 208 | 97 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 57.3 |  |  | 500 | 675 | 850 | 2.5884 | 5.1767 | 7.7651 | 12.9418 | 19.4127 | 25.8835 | 93.9922 | 95.7952 | 96.926 | 96.8916 | 97.1284 | 97.2124 | 96.8665 | 95.8284 | 95.9332 | 96.6126 | 96.9374 | 97.4868 | 97.2454 | 97.1104 | 89.5538 | 94.454 | 95.935 | 96.8496 | 97.2484 | 97.382 | 96.5662 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-30k-L {220V} | Y | Y | N | N | N | N | Y |  | 27.379 kW, 220 Vac Grid Support Utility Interactive Inverter with PCS functionality | 27.379 | 220 | 97 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 67.5 |  |  | 500 | 675 | 850 | 2.7378 | 5.4756 | 8.2134 | 13.689 | 20.5336 | 27.3781 | 94.062 | 95.658 | 95.876 | 96.926 | 97.104 | 97.23 | 96.7316 | 95.828 | 95.938 | 96.636 | 96.904 | 97.512 | 97.416 | 97.1283 | 89.634 | 95.716 | 96.816 | 97.218 | 97.562 | 97.588 | 96.9921 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-30k-L {240V} | Y | Y | N | N | N | N | Y |  | 29.834174 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality | 29.8342 | 240 | 97 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 70.7 |  |  | 500 | 675 | 850 | 2.9834 | 5.9668 | 8.9503 | 14.9171 | 22.3756 | 29.8342 | 94.1056 | 95.74 | 95.9364 | 96.9676 | 97.0914 | 97.208 | 96.7456 | 95.8062 | 95.9614 | 96.708 | 96.93 | 97.4686 | 97.4116 | 97.1195 | 89.631 | 95.7398 | 96.8554 | 97.2412 | 97.5684 | 97.5508 | 97.0043 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-30k-N {480V} | Y | Y | N | N | N | N | Y |  | 29.884702 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 29.8847 | 480 | 97 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 54.5 |  |  | 500 | 675 | 850 | 2.9885 | 5.9769 | 8.9654 | 14.9424 | 22.4135 | 29.8847 | 94.0686 | 95.8068 | 96.0994 | 97.282 | 97.2044 | 97.2516 | 96.8951 | 95.8456 | 96.0126 | 96.686 | 97.236 | 97.5746 | 97.4406 | 97.2429 | 89.6642 | 95.7374 | 96.8292 | 97.2394 | 97.57 | 97.6 | 97.0053 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-40k-N {480V} | Y | Y | N | N | N | N | Y |  | 39.844002 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 39.844 | 480 | 97 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 70 |  |  | 500 | 675 | 850 | 3.9844 | 7.9688 | 11.9532 | 19.922 | 29.883 | 39.844 | 94.1092 | 95.8522 | 97.0008 | 97.3276 | 97.3346 | 97.4462 | 97.0955 | 96.0928 | 96.5924 | 96.914 | 97.447 | 97.4484 | 97.357 | 97.2824 | 94.472 | 96.3238 | 97.1636 | 97.5694 | 97.6026 | 97.3274 | 97.34 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-50k-N {480V} | Y | Y | N | N | N | N | Y |  | 49.80341867 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 49.8034 | 480 | 97.5 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 76 |  |  | 600 | 725 | 850 | 4.9803 | 9.9607 | 14.941 | 24.9017 | 37.3526 | 49.8034 | 94.4062 | 96.4892 | 97.322 | 97.4496 | 97.3804 | 97.2358 | 97.2172 | 94.4798 | 96.4874 | 97.138 | 97.616 | 97.5676 | 97.5136 | 97.346 | 95.4054 | 96.9518 | 97.2974 | 97.5806 | 97.5812 | 97.4988 | 97.4244 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-60k-N {480V} | Y | Y | N | N | N | N | Y |  | 59.763 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 59.763 | 480 | 97.5 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 76 |  |  | 600 | 725 | 850 | 5.976 | 11.953 | 17.929 | 29.882 | 44.822 | 59.763 | 96.01 | 97.2 | 97.59 | 97.54 | 97.42 | 97.28 | 97.39 | 95.84 | 96.83 | 97.37 | 97.65 | 97.49 | 97.31 | 97.4 | 95.74 | 97.17 | 97.55 | 97.61 | 97.51 | 97.39 | 97.44 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
FOXESS CO., LTD. | M1-600-NA {208V} | N | Y | N | N | N | N | N |  | 600 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.607 | 208 | 95 | CSA Group | [11/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | Y | 0.312 |  |  | 35 | 42 | 50 | 0.061 | 0.121 | 0.182 | 0.304 | 0.456 | 0.607 | 91.24 | 94.89 | 95.23 | 95.63 | 95.45 | 95.45 | 95.27 | 91.37 | 94.95 | 95.41 | 95.58 | 95.53 | 95.53 | 95.33 | 90.89 | 94.28 | 95.11 | 95.05 | 95 | 95.15 | 94.83 | 2026-05-01 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
FOXESS CO., LTD. | M1-800-NA {208V} | N | Y | N | N | N | N | N |  | 800 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.814 | 208 | 95.5 | CSA Group | [11/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | Y | 0.312 |  |  | 35 | 42 | 50 | 0.081 | 0.163 | 0.244 | 0.407 | 0.61 | 0.814 | 92.58 | 95.02 | 95.87 | 95.98 | 95.67 | 95.58 | 95.6 | 92.19 | 95.31 | 95.54 | 95.48 | 95.6 | 95.44 | 95.41 | 90.21 | 94.96 | 95.21 | 95.3 | 95.98 | 95.4 | 95.43 | 2026-05-01 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
FOXESS CO., LTD. | M1-800-NA {240V} | N | Y | N | N | N | N | N |  | 800 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.814 | 240 | 95.5 | CSA Group | [11/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | Y | 0.416 |  |  | 35 | 42 | 50 | 0.081 | 0.163 | 0.244 | 0.407 | 0.61 | 0.814 | 92.34 | 94.7 | 96.03 | 95.45 | 95.66 | 95.69 | 95.48 | 90.54 | 94.7 | 95.81 | 95.81 | 95.35 | 95.52 | 95.29 | 90.33 | 94.52 | 95.14 | 95.38 | 95.18 | 95.3 | 95 | 2026-05-01 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
FOXESS CO., LTD. | M1-1000-NA {208V} | N | Y | N | N | N | N | N |  | 1000 W, 208 Vac Grid Support Utility Interactive Microinverter | 1.004 | 208 | 95.5 | CSA Group | [11/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | Y | 0.312 |  |  | 35 | 42 | 50 | 0.1 | 0.201 | 0.301 | 0.502 | 0.753 | 1.004 | 92.2 | 95.11 | 96.04 | 95.92 | 95.62 | 94.81 | 95.53 | 91.75 | 95.02 | 95.82 | 95.74 | 95.37 | 94.67 | 95.31 | 90.81 | 95.89 | 95.4 | 95.48 | 95.14 | 94.64 | 95.08 | 2026-05-01 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
FOXESS CO., LTD. | M1-1000-NA {240V} | N | Y | N | N | N | N | N |  | 1000 W, 240 Vac Grid Support Utility Interactive Microinverter | 1.005 | 240 | 95.5 | CSA Group | [11/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | Y | 0.415 |  |  | 35 | 42 | 50 | 0.1 | 0.201 | 0.301 | 0.502 | 0.754 | 1.005 | 92.24 | 95.41 | 96.02 | 96.04 | 95.59 | 94.98 | 95.56 | 91.58 | 95.02 | 95.84 | 95.63 | 95.64 | 95.32 | 95.45 | 91.49 | 94.98 | 95.36 | 95.29 | 95.23 | 95.16 | 95.09 | 2026-05-01 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
FOXESS CO., LTD. | M1-1200-NA {240V} | N | Y | N | N | N | N | N |  | 1200 W, 240 Vac Grid Support Utility Interactive Microinverter | 1.201 | 240 | 95.5 | CSA Group | [11/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | Y | 0.416 |  |  | 35 | 42 | 50 | 0.12 | 0.24 | 0.36 | 0.6 | 0.901 | 1.201 | 92.61 | 95.73 | 96.14 | 95.67 | 95.3 | 95.33 | 95.39 | 92.28 | 95.46 | 95.94 | 95.78 | 95.28 | 95.23 | 95.35 | 91.4 | 95.33 | 95.54 | 95.26 | 95.09 | 94.64 | 95.02 | 2026-05-01 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
FOXESS CO., LTD. | H1-3.8-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 3.713 | 240 | 96 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 204 | 380 | 480 | 0.3713 | 0.74261 | 1.1139 | 1.8565 | 2.7848 | 3.713 | 88.7571 | 93.1319 | 94.7403 | 95.8238 | 96.4154 | 96.5626 | 95.627 | 90.646 | 94.5568 | 95.593 | 96.5203 | 97.3128 | 97.201 | 96.5299 | 87.3378 | 93.647 | 95.4273 | 96.4142 | 97.3282 | 97.4961 | 96.3329 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | AIO-H1-3.8-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 3.7972 | 240 | 96 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 204 | 380 | 500 | 0.37972 | 0.75944 | 1.1392 | 1.8986 | 2.8479 | 3.7972 | 89.6627 | 93.2292 | 94.5681 | 95.9692 | 96.4301 | 96.5483 | 95.685 | 91.725 | 94.6987 | 95.7083 | 96.7501 | 96.9842 | 97.1693 | 96.4665 | 88.9624 | 93.5492 | 95.5387 | 97.0122 | 97.3598 | 97.5206 | 96.5499 | 2025-07-01
FOXESS CO., LTD. | AIO-H1-5.7-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.7 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 5.6866 | 240 | 97 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 204 | 380 | 500 | 0.56866 | 1.1373 | 1.706 | 2.8433 | 4.265 | 5.6866 | 90.9696 | 94.7434 | 95.8003 | 96.4201 | 96.6721 | 96.5359 | 96.1832 | 91.1194 | 95.495 | 96.9717 | 97.7104 | 97.7396 | 97.8212 | 97.2684 | 91.0574 | 96.0199 | 96.4362 | 96.7768 | 97.6862 | 97.512 | 96.9881 | 2025-07-01
FOXESS CO., LTD. | H1-5.7-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 5.7482 | 240 | 97 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 204 | 380 | 480 | 0.57482 | 1.1496 | 1.7245 | 2.8741 | 4.3111 | 5.7482 | 90.8808 | 94.8098 | 95.7632 | 96.4753 | 96.7386 | 96.703 | 96.2337 | 91.5018 | 95.6465 | 97.2168 | 97.6379 | 97.868 | 97.771 | 97.371 | 89.8373 | 95.634 | 96.4644 | 97.2092 | 97.4788 | 97.595 | 96.9084 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | AIO-H1-7.6-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.5857 | 240 | 97.5 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 271 | 380 | 500 | 0.75857 | 1.5171 | 2.2757 | 3.7928 | 5.6893 | 7.5857 | 95.214 | 96.6078 | 97.1112 | 97.4349 | 97.5337 | 97.4987 | 97.3214 | 95.8601 | 97.1947 | 97.6786 | 97.8404 | 97.7797 | 97.7298 | 97.6718 | 95.0767 | 96.615 | 97.41 | 97.5037 | 97.6476 | 97.3909 | 97.4216 | 2025-07-01
FOXESS CO., LTD. | H1-7.6-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 7.7203 | 240 | 97 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 271 | 380 | 480 | 0.77203 | 1.5441 | 2.3161 | 3.8602 | 5.7903 | 7.7203 | 93.4996 | 95.7999 | 96.5407 | 97.0482 | 97.1101 | 96.8974 | 96.8082 | 93.8722 | 96.8306 | 97.0752 | 97.4311 | 97.293 | 97.6679 | 97.1547 | 92.4126 | 96.3152 | 97.0656 | 97.6101 | 97.731 | 97.5149 | 97.3315 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | AIO-H1-9.6-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.5752 | 240 | 97.5 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 257 | 380 | 500 | 0.95752 | 1.915 | 2.8726 | 4.7876 | 7.1814 | 9.5752 | 95.5716 | 96.9652 | 97.2989 | 97.5667 | 97.3513 | 97.0646 | 97.2854 | 96.4655 | 97.5565 | 97.7877 | 97.8147 | 97.7869 | 97.5106 | 97.7147 | 95.5032 | 96.9894 | 97.3765 | 97.569 | 97.4942 | 97.2838 | 97.3804 | 2025-07-01
FOXESS CO., LTD. | H1-9.6-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 9.6091 | 240 | 97 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 257 | 380 | 480 | 0.96091 | 1.9218 | 2.8827 | 4.8046 | 7.2068 | 9.6091 | 94.0151 | 96.18 | 96.7302 | 97.0459 | 96.9854 | 96.7841 | 96.7983 | 95.6441 | 97.147 | 97.1617 | 97.4712 | 97.3224 | 97.1525 | 97.25 | 94.7056 | 96.5502 | 97.2561 | 97.5742 | 97.6405 | 97.2619 | 97.3896 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | AIO-H1-11.4-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.3612 | 240 | 97.5 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 257 | 380 | 500 | 1.1361 | 2.2722 | 3.4084 | 5.6806 | 8.5209 | 11.3612 | 95.4936 | 97.0984 | 97.3469 | 97.5337 | 97.2494 | 96.9259 | 97.2268 | 96.3704 | 97.3767 | 97.7788 | 97.5807 | 97.5045 | 97.4531 | 97.4991 | 95.4259 | 97.3169 | 97.5648 | 97.6753 | 97.5094 | 97.1914 | 97.442 | 2025-07-01
FOXESS CO., LTD. | H1-11.4-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 11.5119 | 240 | 97.5 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 305 | 380 | 480 | 1.1512 | 2.3024 | 3.4536 | 5.756 | 8.6339 | 11.5119 | 95.5005 | 96.9797 | 97.2834 | 97.3603 | 97.1804 | 96.9301 | 97.1408 | 96.2352 | 97.384 | 97.7697 | 97.5626 | 97.4234 | 97.4212 | 97.4446 | 95.7811 | 97.2716 | 97.6352 | 97.6967 | 97.6385 | 97.1496 | 97.5332 | 2022-10-21 | 2024-02-12
FOXESS CO., LTD. | H3-70-Plus-US-L {208V} | Y | Y | N | N | N | N | Y* |  | 70 kW, 208 Vac Transformerless Grid Support Utility Interactive Inverter | 69.35 | 208 | 96 | CSA Group | [6/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-06-18 |  |  | N | N | 32.2 |  |  | 240 | 400 | 700 | 6.935 | 13.87 | 20.805 | 34.675 | 52.012 | 69.35 | 94.95 | 96.31 | 96.49 | 96.31 | 95.76 | 94.41 | 95.89 | 95.42 | 96.58 | 96.83 | 96.75 | 96.38 | 95.92 | 96.46 | 93.65 | 95.64 | 96.05 | 96.08 | 95.75 | 95.28 | 95.74 | 2026-09-01 |  | Y | Y | Y | Y | N | Y | Y | N | No Information Submitted
FOXESS CO., LTD. | H3-150-Plus-US-H {480V} | Y | Y | N | N | N | N | Y* |  | 150 kW, 480 Vac Transformerless Grid Support Utility Interactive Inverter | 149.243 | 480 | 97.5 | CSA Group | [6/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-06-18 |  |  | N | N | 26.4 |  |  | 540 | 700 | 850 | 14.924 | 29.849 | 44.773 | 74.621 | 111.932 | 149.243 | 95.84 | 97.1 | 97.46 | 97.61 | 97.38 | 97.14 | 97.35 | 96.26 | 97.54 | 97.86 | 97.96 | 97.8 | 97.25 | 97.74 | 96.63 | 97.84 | 98.11 | 98.18 | 98.07 | 97.32 | 97.99 | 2026-09-01 |  | Y | Y | Y | Y | N | Y | Y | N | No Information Submitted
FranklinWH Energy Storage Inc. | aPower Syyy {240V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.7764 | 240 | 97.5 | CSA Group | [12/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-04-14 | 2025-05-01 |  | N | N | 59.3 |  |  | 250 | 400 | 480 | 0.97764 | 1.9553 | 2.9329 | 4.8882 | 7.3323 | 9.7764 | 94.0563 | 95.7656 | 96.7667 | 97.3048 | 97.3507 | 97.1855 | 97.0517 | 94.9793 | 97.4217 | 97.9049 | 98.0486 | 98.0031 | 97.8209 | 97.8418 | 94.3301 | 96.2484 | 97.1181 | 97.719 | 97.7563 | 97.6438 | 97.4538 | 2025-05-12
FranklinWH Energy Storage Inc. | aPower Syyy {208V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.7851 | 208 | 97.5 | CSA Group | [12/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-04-14 | 2025-05-01 |  | N | N | 58.7 |  |  | 250 | 400 | 480 | 0.97851 | 1.957 | 2.9355 | 4.8925 | 7.3388 | 9.7851 | 93.9597 | 95.7448 | 96.7603 | 97.2398 | 97.2409 | 97.0309 | 96.9665 | 94.9498 | 97.5429 | 98.0023 | 98.105 | 97.9495 | 97.7095 | 97.8362 | 94.1974 | 96.2048 | 97.1199 | 97.544 | 97.6082 | 97.4664 | 97.3224 | 2025-05-12
FranklinWH Energy Storage Inc. | aPower Syyy {208V, 10kW} | Y | Y | N | N | N | N | Y* |  | 10 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.016 | 208 | 95.5 | CSA Group | [4/22/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 45761 |  |  | N | N | 64.1 |  |  | 49.4 | 51.2 | 54.4 | 1.002 | 2.003 | 3.005 | 5.008 | 7.512 | 10.016 | 93.23 | 95.74 | 96.3 | 96.27 | 95.44 | 94.26 | 95.58 | 93.13 | 95.66 | 96.28 | 96.34 | 95.51 | 94.48 | 95.64 | 92.86 | 95.5 | 96.23 | 96.43 | 95.74 | 94.77 | 95.77 | 2026-08-11 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
FranklinWH Energy Storage Inc. | aPower Syyy {240V, 10kW} | Y | Y | N | N | N | N | Y* |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.076 | 240 | 96 | CSA Group | [4/22/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 45761 |  |  | N | N | 58 |  |  | 49.4 | 51.2 | 54.4 | 1.008 | 2.015 | 3.023 | 5.038 | 7.557 | 10.076 | 93.38 | 95.86 | 96.41 | 96.34 | 95.61 | 94.56 | 95.73 | 93.18 | 95.81 | 96.43 | 96.39 | 95.64 | 94.6 | 95.75 | 93.01 | 95.69 | 96.4 | 96.47 | 95.81 | 94.91 | 95.86 | 2026-08-11 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
FranklinWH Energy Storage Inc. | aPower Syyy {240V, 11.5kW} | Y | Y | N | N | N | N | Y* |  | 11.5 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.554 | 240 | 97.5 | CSA Group | [4/22/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 45761 |  |  | N | N | 32 |  |  | 250 | 400 | 480 | 1.155 | 2.311 | 3.466 | 5.777 | 8.666 | 11.554 | 94.75 | 95.98 | 96.79 | 97.2 | 97.05 | 96.81 | 96.89 | 94.82 | 96.47 | 97.5 | 97.96 | 97.86 | 97.6 | 97.63 | 93.46 | 95.73 | 96.81 | 97.68 | 97.57 | 97.4 | 97.24 | 2026-08-11 | 2026-08-21 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
FranklinWH Energy Storage Inc. | aPower Syyy {208V, 11.5kW} | Y | Y | N | N | N | N | Y* |  | 11.5 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.577 | 208 | 97 | CSA Group | [4/22/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 45761 |  |  | N | N | 68 |  |  | 250 | 400 | 480 | 1.158 | 2.315 | 3.473 | 5.788 | 8.683 | 11.577 | 93.72 | 95.86 | 96.71 | 97.08 | 96.97 | 96.59 | 96.76 | 94.34 | 96.26 | 97.45 | 97.77 | 97.66 | 97.41 | 97.44 | 93.4 | 95.31 | 96.83 | 97.38 | 97.41 | 97.19 | 97.06 | 2026-08-11 | 2026-08-21 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
Fronius International GmbH | Primo GEN24 3.8 208-240 Plus SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.8 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 3.7999 | 240 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.63 |  |  | 190 | 385 | 480 | 0.38 | 0.75999 | 1.14 | 1.9 | 2.85 | 3.7999 | 91.0973 | 94.7379 | 95.9993 | 96.4629 | 96.7029 | 96.7741 | 96.2491 | 92.6834 | 95.9716 | 96.7951 | 97.4158 | 97.5866 | 97.6284 | 97.181 | 90.9224 | 95.0813 | 96.174 | 97.0187 | 97.2843 | 97.3607 | 96.7345 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 3.8 208-240 SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.8 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 3.7999 | 240 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.63 |  |  | 190 | 385 | 480 | 0.38 | 0.75999 | 1.14 | 1.9 | 2.85 | 3.7999 | 91.0973 | 94.7379 | 95.9993 | 96.4629 | 96.7029 | 96.7741 | 96.2491 | 92.6834 | 95.9716 | 96.7951 | 97.4158 | 97.5866 | 97.6284 | 97.181 | 90.9224 | 95.0813 | 96.174 | 97.0187 | 97.2843 | 97.3607 | 96.7345 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Fronius Primo 3.8-1 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 3.8 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 3.8 | 208 | 96 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0] | 2018-10-15 | [7/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.41 |  |  | 100 | 650 | 800 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 87.3 | 92.4 | 93.9 | 95.2 | 95.6 | 95.7 | 94.8 | 90.7 | 95.2 | 96.4 | 97.2 | 97.5 | 97.6 | 96.9 | 85.7 | 93.4 | 95.2 | 96.6 | 97.1 | 97.3 | 96.1 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Primo 3.8-1 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 3.8 | 240 | 95.5 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0] | 2018-10-15 | [7/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.55 |  |  | 100 | 650 | 800 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 85.5 | 91.5 | 93.3 | 94.8 | 95.4 | 95.6 | 94.4 | 87.2 | 93.4 | 95 | 96.4 | 96.9 | 97.2 | 96 | 87 | 93.7 | 95.5 | 96.9 | 97.4 | 97.6 | 96.5 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Primo GEN24 3.8 208-240 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 3.802 | 240 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.3 |  |  | 200 | 400 | 480 | 0.38018 | 0.76036 | 1.1405 | 1.9009 | 2.8514 | 3.8018 | 89.0285 | 93.9929 | 95.2684 | 96.142 | 96.561 | 96.6724 | 95.8938 | 93.396 | 96.2696 | 97.0028 | 97.4707 | 97.6461 | 97.6553 | 97.2937 | 91.8008 | 95.685 | 96.5943 | 97.2177 | 97.4303 | 97.467 | 96.9747 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 3.8 208-240 Plus {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 3.802 | 240 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.3 |  |  | 200 | 400 | 480 | 0.38018 | 0.76036 | 1.1405 | 1.9009 | 2.8514 | 3.8018 | 89.0285 | 93.9929 | 95.2684 | 96.142 | 96.561 | 96.6724 | 95.8938 | 93.396 | 96.2696 | 97.0028 | 97.4707 | 97.6461 | 97.6553 | 97.2937 | 91.8008 | 95.685 | 96.5943 | 97.2177 | 97.4303 | 97.467 | 96.9747 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 3.8 208-240 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 3.805 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.4 |  |  | 200 | 360 | 480 | 0.381 | 0.761 | 1.142 | 1.903 | 2.854 | 3.805 | 90.04 | 94.42 | 95.58 | 96.37 | 96.51 | 96.51 | 96.01 | 93.84 | 96.3 | 96.91 | 97.34 | 97.41 | 97.37 | 97.14 | 91.74 | 95.59 | 96.36 | 96.93 | 97.1 | 97.08 | 96.68 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 3.8 208-240 Plus {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 3.805 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.4 |  |  | 200 | 360 | 480 | 0.381 | 0.761 | 1.142 | 1.903 | 2.854 | 3.805 | 90.04 | 94.42 | 95.58 | 96.37 | 96.51 | 96.51 | 96.01 | 93.84 | 96.3 | 96.91 | 97.34 | 97.41 | 97.37 | 97.14 | 91.74 | 95.59 | 96.36 | 96.93 | 97.1 | 97.08 | 96.68 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 3.8 208-240 Plus SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.8 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 3.8147 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.74 |  |  | 190 | 365 | 480 | 0.38147 | 0.76293 | 1.1444 | 1.9073 | 2.861 | 3.8147 | 90.972 | 94.5295 | 95.784 | 96.188 | 96.388 | 96.4566 | 95.9674 | 92.9078 | 95.953 | 96.6908 | 97.2113 | 97.3462 | 97.3313 | 96.9913 | 90.9984 | 94.9841 | 96.0279 | 96.7766 | 96.9891 | 97.005 | 96.4901 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 3.8 208-240 SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.8 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 3.8147 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.74 |  |  | 190 | 365 | 480 | 0.38147 | 0.76293 | 1.1444 | 1.9073 | 2.861 | 3.8147 | 90.972 | 94.5295 | 95.784 | 96.188 | 96.388 | 96.4566 | 95.9674 | 92.9078 | 95.953 | 96.6908 | 97.2113 | 97.3462 | 97.3313 | 96.9913 | 90.9984 | 94.9841 | 96.0279 | 96.7766 | 96.9891 | 97.005 | 96.4901 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Fronius Primo 5.0-1 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 5 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 5 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0] | 2018-10-15 | [7/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.41 |  |  | 100 | 650 | 800 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89.4 | 93.8 | 94.8 | 95.8 | 96 | 96 | 95.4 | 92.5 | 96 | 96.8 | 97.5 | 97.6 | 97.6 | 97.2 | 89.3 | 94.6 | 96 | 97 | 97.3 | 97.4 | 96.6 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Primo 5.0-1 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 5 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0] | 2018-10-15 | [7/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.55 |  |  | 100 | 660 | 800 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89 | 93.2 | 94.6 | 95.6 | 95.9 | 96 | 95.3 | 91.6 | 95.4 | 96.4 | 97.1 | 97.4 | 97.4 | 96.9 | 92.3 | 96 | 97 | 97.7 | 97.9 | 97.9 | 97.4 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Primo GEN24 5.0 208-240 Plus SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.0 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.0002 | 240 | 97 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.62 |  |  | 190 | 385 | 480 | 0.50002 | 1 | 1.5 | 2.5001 | 3.7501 | 5.0002 | 93.5288 | 95.5677 | 96.175 | 96.6246 | 96.7651 | 96.7308 | 96.4738 | 94.159 | 96.6219 | 97.2055 | 97.5096 | 97.624 | 97.6078 | 97.3602 | 92.7932 | 95.9577 | 96.7372 | 97.2239 | 97.3573 | 97.3834 | 97.0037 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 5.0 208-240 SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.0 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.0002 | 240 | 97 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.62 |  |  | 190 | 385 | 480 | 0.50002 | 1 | 1.5 | 2.5001 | 3.7501 | 5.0002 | 93.5288 | 95.5677 | 96.175 | 96.6246 | 96.7651 | 96.7308 | 96.4738 | 94.159 | 96.6219 | 97.2055 | 97.5096 | 97.624 | 97.6078 | 97.3602 | 92.7932 | 95.9577 | 96.7372 | 97.2239 | 97.3573 | 97.3834 | 97.0037 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 5.0 208-240 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.006 | 208 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.2 |  |  | 230 | 360 | 480 | 0.50064 | 1.0013 | 1.5019 | 2.5032 | 3.7548 | 5.0064 | 92.1068 | 95.559 | 96.333 | 96.7491 | 96.7615 | 96.6907 | 96.4576 | 94.9627 | 96.8248 | 97.2401 | 97.4415 | 97.3926 | 97.3272 | 97.2557 | 93.458 | 96.166 | 96.7617 | 97.1167 | 97.1328 | 96.9747 | 96.8816 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 5.0 208-240 Plus {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.006 | 208 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.2 |  |  | 230 | 360 | 480 | 0.50064 | 1.0013 | 1.5019 | 2.5032 | 3.7548 | 5.0064 | 92.1068 | 95.559 | 96.333 | 96.7491 | 96.7615 | 96.6907 | 96.4576 | 94.9627 | 96.8248 | 97.2401 | 97.4415 | 97.3926 | 97.3272 | 97.2557 | 93.458 | 96.166 | 96.7617 | 97.1167 | 97.1328 | 96.9747 | 96.8816 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 5.0 208-240 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.007 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.3 |  |  | 230 | 400 | 480 | 0.50072 | 1.0014 | 1.5022 | 2.5036 | 3.7554 | 5.0072 | 91.4981 | 95.117 | 95.9981 | 96.4863 | 96.8457 | 96.8711 | 96.3695 | 94.7183 | 96.7822 | 97.2832 | 97.6405 | 97.635 | 97.5893 | 97.4323 | 93.5556 | 96.3003 | 96.9674 | 97.3974 | 97.4608 | 97.4163 | 97.1718 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 5.0 208-240 Plus {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.007 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.3 |  |  | 230 | 400 | 480 | 0.50072 | 1.0014 | 1.5022 | 2.5036 | 3.7554 | 5.0072 | 91.4981 | 95.117 | 95.9981 | 96.4863 | 96.8457 | 96.8711 | 96.3695 | 94.7183 | 96.7822 | 97.2832 | 97.6405 | 97.635 | 97.5893 | 97.4323 | 93.5556 | 96.3003 | 96.9674 | 97.3974 | 97.4608 | 97.4163 | 97.1718 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 5.0 208-240 Plus SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.0 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.0224 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.6 |  |  | 190 | 365 | 480 | 0.50224 | 1.0045 | 1.5067 | 2.5112 | 3.7668 | 5.0224 | 93.399 | 95.8084 | 95.8707 | 96.3153 | 96.4507 | 96.3548 | 96.1937 | 94.2612 | 96.5214 | 97.0429 | 97.316 | 97.2855 | 97.2571 | 97.1022 | 92.8231 | 95.8202 | 96.5218 | 96.8849 | 97.0206 | 96.9716 | 96.7019 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 5.0 208-240 SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.0 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.0224 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.6 |  |  | 190 | 365 | 480 | 0.50224 | 1.0045 | 1.5067 | 2.5112 | 3.7668 | 5.0224 | 93.399 | 95.8084 | 95.8707 | 96.3153 | 96.4507 | 96.3548 | 96.1937 | 94.2612 | 96.5214 | 97.0429 | 97.316 | 97.2855 | 97.2571 | 97.1022 | 92.8231 | 95.8202 | 96.5218 | 96.8849 | 97.0206 | 96.9716 | 96.7019 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 6.0 208-240 Plus SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.0 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.7316 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.53 |  |  | 190 | 365 | 480 | 0.57316 | 1.1463 | 1.7195 | 2.8658 | 4.2987 | 5.7316 | 93.2421 | 95.7581 | 96.0497 | 96.3978 | 96.4338 | 96.2511 | 96.2095 | 94.7764 | 96.713 | 97.141 | 97.3368 | 97.3123 | 97.176 | 97.1587 | 93.4162 | 96.0496 | 96.6594 | 96.9506 | 97.0021 | 96.8982 | 96.7539 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 6.0 208-240 SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.0 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.7316 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.53 |  |  | 190 | 365 | 480 | 0.57316 | 1.1463 | 1.7195 | 2.8658 | 4.2987 | 5.7316 | 93.2421 | 95.7581 | 96.0497 | 96.3978 | 96.4338 | 96.2511 | 96.2095 | 94.7764 | 96.713 | 97.141 | 97.3368 | 97.3123 | 97.176 | 97.1587 | 93.4162 | 96.0496 | 96.6594 | 96.9506 | 97.0021 | 96.8982 | 96.7539 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 6.0 208-240 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.743 | 208 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.4 |  |  | 230 | 360 | 480 | 0.5743 | 1.1486 | 1.7229 | 2.8715 | 4.3072 | 5.743 | 93.0718 | 95.8262 | 96.3687 | 96.6826 | 96.6192 | 96.475 | 96.4137 | 95.3477 | 96.9249 | 97.2393 | 97.3708 | 97.3163 | 97.133 | 97.211 | 94.177 | 96.3803 | 96.8316 | 97.0907 | 97.0319 | 96.7863 | 96.8611 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 6.0 208-240 Plus {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.743 | 208 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.4 |  |  | 230 | 360 | 480 | 0.5743 | 1.1486 | 1.7229 | 2.8715 | 4.3072 | 5.743 | 93.0718 | 95.8262 | 96.3687 | 96.6826 | 96.6192 | 96.475 | 96.4137 | 95.3477 | 96.9249 | 97.2393 | 97.3708 | 97.3163 | 97.133 | 97.211 | 94.177 | 96.3803 | 96.8316 | 97.0907 | 97.0319 | 96.7863 | 96.8611 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Fronius Primo 6.0-1 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 6 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0] | 2018-10-15 | [7/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.41 |  |  | 100 | 660 | 800 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 90.7 | 94.4 | 95.2 | 95.9 | 96 | 95.9 | 95.6 | 93.5 | 96.5 | 97.1 | 97.6 | 97.6 | 97.6 | 97.3 | 91 | 95.4 | 96.4 | 97.2 | 97.3 | 97.4 | 96.8 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Primo 6.0-1 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0] | 2018-10-15 | [7/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.55 |  |  | 100 | 660 | 800 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 89.8 | 93.6 | 94.9 | 95.8 | 96 | 96 | 95.4 | 91.4 | 95.3 | 96.3 | 97 | 97.3 | 97.3 | 96.8 | 91.7 | 95.7 | 96.7 | 97.5 | 97.7 | 97.7 | 97.2 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Primo GEN24 6.0 208-240 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 6.004 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.3 |  |  | 230 | 400 | 480 | 0.60044 | 1.2009 | 1.8013 | 3.0022 | 4.5033 | 6.0044 | 92.6588 | 95.6182 | 96.2204 | 96.7281 | 96.8629 | 96.79 | 96.5234 | 95.3651 | 97.0418 | 97.4249 | 97.6296 | 97.6221 | 97.5002 | 97.4746 | 94.4545 | 96.64 | 97.127 | 97.4435 | 97.436 | 97.2966 | 97.2344 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 6.0 208-240 Plus {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 6.004 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.3 |  |  | 230 | 400 | 480 | 0.60044 | 1.2009 | 1.8013 | 3.0022 | 4.5033 | 6.0044 | 92.6588 | 95.6182 | 96.2204 | 96.7281 | 96.8629 | 96.79 | 96.5234 | 95.3651 | 97.0418 | 97.4249 | 97.6296 | 97.6221 | 97.5002 | 97.4746 | 94.4545 | 96.64 | 97.127 | 97.4435 | 97.436 | 97.2966 | 97.2344 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 6.0 208-240 Plus SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.0 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 6.0047 | 240 | 97 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.53 |  |  | 190 | 385 | 480 | 0.60047 | 1.2009 | 1.8014 | 3.0023 | 4.5035 | 6.0047 | 93.4643 | 96.0718 | 96.3559 | 96.7017 | 96.7527 | 96.5931 | 96.5208 | 94.8709 | 96.8847 | 97.3598 | 97.6019 | 97.6102 | 97.5386 | 97.429 | 93.6473 | 96.3114 | 96.955 | 97.3069 | 97.3654 | 97.321 | 97.1002 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 6.0 208-240 SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.0 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 6.0047 | 240 | 97 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.53 |  |  | 190 | 385 | 480 | 0.60047 | 1.2009 | 1.8014 | 3.0023 | 4.5035 | 6.0047 | 93.4643 | 96.0718 | 96.3559 | 96.7017 | 96.7527 | 96.5931 | 96.5208 | 94.8709 | 96.8847 | 97.3598 | 97.6019 | 97.6102 | 97.5386 | 97.429 | 93.6473 | 96.3114 | 96.955 | 97.3069 | 97.3654 | 97.321 | 97.1002 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Fronius Primo 7.6-1 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 7.6 | 208 | 97 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0] | 2018-10-15 | [7/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.41 |  |  | 100 | 660 | 800 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.7 | 95.1 | 95.8 | 96.1 | 96.1 | 95.8 | 95.8 | 96 | 97.4 | 97.7 | 97.8 | 97.7 | 97.6 | 97.7 | 94.1 | 96.7 | 97.3 | 97.6 | 97.5 | 97.4 | 97.3 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Primo 7.6-1 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 7.6 | 240 | 97 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0] | 2018-10-15 | [7/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.55 |  |  | 100 | 660 | 800 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 91.6 | 94.8 | 95.5 | 96 | 96.1 | 95.9 | 95.7 | 94 | 96.4 | 97 | 97.4 | 97.5 | 97.4 | 97.2 | 94.6 | 97 | 97.6 | 97.9 | 97.9 | 97.8 | 97.7 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Primo GEN24 7.7 208-240 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.7 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 7.686 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 9.2 |  |  | 260 | 385 | 480 | 0.769 | 1.537 | 2.306 | 3.843 | 5.765 | 7.686 | 94.05 | 96.37 | 96.88 | 97.11 | 97.04 | 96.88 | 96.87 | 94.83 | 96.86 | 97.22 | 97.48 | 97.44 | 97.32 | 97.28 | 93.09 | 96.01 | 96.73 | 97.08 | 97.11 | 97.06 | 96.84 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 7.7 208-240 Plus {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.7 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 7.686 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 9.2 |  |  | 260 | 385 | 480 | 0.769 | 1.537 | 2.306 | 3.843 | 5.765 | 7.686 | 94.05 | 96.37 | 96.88 | 97.11 | 97.04 | 96.88 | 96.87 | 94.83 | 96.86 | 97.22 | 97.48 | 97.44 | 97.32 | 97.28 | 93.09 | 96.01 | 96.73 | 97.08 | 97.11 | 97.06 | 96.84 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 7.7 208-240 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.7 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 7.689 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 9.2 |  |  | 260 | 365 | 480 | 0.769 | 1.538 | 2.307 | 3.845 | 5.767 | 7.689 | 93.81 | 96.07 | 96.53 | 96.72 | 96.67 | 96.46 | 96.51 | 94.89 | 96.66 | 97.09 | 97.14 | 97.09 | 96.88 | 96.98 | 92.99 | 95.77 | 96.38 | 96.7 | 96.7 | 96.57 | 96.46 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 7.7 208-240 Plus {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.7 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 7.689 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 9.2 |  |  | 260 | 365 | 480 | 0.769 | 1.538 | 2.307 | 3.845 | 5.767 | 7.689 | 93.81 | 96.07 | 96.53 | 96.72 | 96.67 | 96.46 | 96.51 | 94.89 | 96.66 | 97.09 | 97.14 | 97.09 | 96.88 | 96.98 | 92.99 | 95.77 | 96.38 | 96.7 | 96.7 | 96.57 | 96.46 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Fronius Primo 8.2-1 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 8.2 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 7.9 | 208 | 97 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0] | 2018-10-15 | [7/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.41 |  |  | 100 | 660 | 800 | 0.79 | 1.58 | 2.37 | 3.95 | 5.93 | 7.9 | 93 | 95.3 | 95.9 | 96.2 | 96.2 | 95.9 | 96 | 95.8 | 97.3 | 97.7 | 97.8 | 97.8 | 97.5 | 97.7 | 94 | 96.7 | 97.3 | 97.6 | 97.6 | 97.4 | 97.3 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Primo 8.2-1 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 8.2 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 8.2 | 240 | 97 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.7, Roach V0.26.9.10, Guard V0.10.9.0] | 2018-10-15 | [7/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.55 |  |  | 100 | 660 | 800 | 0.82 | 1.64 | 2.46 | 4.1 | 6.15 | 8.2 | 92.1 | 94.9 | 95.7 | 96.2 | 96.2 | 96.1 | 95.9 | 94.2 | 96.6 | 97.1 | 97.4 | 97.4 | 97.4 | 97.2 | 94.7 | 97.1 | 97.6 | 97.9 | 97.9 | 97.8 | 97.7 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Primo GEN24 10.0 208-240 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.0 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 9.454 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.4 |  |  | 260 | 365 | 480 | 0.945 | 1.891 | 2.836 | 4.727 | 7.091 | 9.454 | 94.64 | 96.41 | 96.65 | 96.71 | 96.56 | 96.19 | 96.5 | 95.55 | 96.97 | 97.15 | 97.16 | 96.98 | 96.68 | 96.97 | 93.99 | 96.24 | 96.6 | 96.73 | 96.61 | 96.37 | 96.5 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 10.0 208-240 Plus {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.0 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 9.454 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.4 |  |  | 260 | 365 | 480 | 0.945 | 1.891 | 2.836 | 4.727 | 7.091 | 9.454 | 94.64 | 96.41 | 96.65 | 96.71 | 96.56 | 96.19 | 96.5 | 95.55 | 96.97 | 97.15 | 97.16 | 96.98 | 96.68 | 96.97 | 93.99 | 96.24 | 96.6 | 96.73 | 96.61 | 96.37 | 96.5 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Fronius Primo 10.0-1 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 10 kW, 208 Vac, Grid Support Utility Interactive Inverter with arc detector and meter | 9.995 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.9.0] | 2018-10-15 | [9/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Model number formerly listed as Fronius Primo 1.-1 {28V}. | Y | N | 0.24 |  |  | 100 | 660 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 92 | 94.7 | 95.1 | 95.6 | 95.6 | 95.5 | 95.3 | 94.5 | 97.4 | 96.8 | 97.3 | 97.3 | 97.4 | 97.1 | 93.3 | 97.1 | 96.5 | 97 | 97.3 | 97.3 | 97 | 2017-11-01 | 2019-03-01
Fronius International GmbH | Fronius Primo 10.0-1 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 10 kW, 240 Vac, Grid Support Utility Interactive Inverter with arc detector and meter | 9.995 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.9.0] | 2018-10-15 | [9/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Model number formerly listed as Fronius Primo 1.-1 {24V}. | Y | N | 0.32 |  |  | 100 | 655 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 91.4 | 94.3 | 94.8 | 95.4 | 95.6 | 95.6 | 95.2 | 93.5 | 95.8 | 96.3 | 96.9 | 97.1 | 97 | 96.7 | 95.6 | 97 | 97.2 | 97.6 | 97.7 | 97.5 | 97.5 | 2017-11-01 | 2019-03-01
Fronius International GmbH | Fronius Symo 10.0-3 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 10 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 9.995 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [10/16/2017];[03/28/2018] | [ReCerbo V0.3.14.8 Roach V0.26.18.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8, Roach V0.26.25.0 Guard V0.10.9.0] | 2018-10-15 | [10/16/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.81 |  |  | 100 | 370 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 96.1 | 95.4 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 97 | 94.8 | 96.4 | 96.7 | 96.9 | 96.9 | 96.7 | 96.7 | 2017-12-01 | 2019-03-01
Fronius International GmbH | Fronius Symo 10.0-3 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 10 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 9.995 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [10/16/2017];[03/28/2018] | [ReCerbo V0.3.14.8 Roach V0.26.18.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8, Roach V0.26.25.0 Guard V0.10.9.0] | 2018-10-15 | [10/16/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.8 |  |  | 100 | 370 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 96.1 | 95.4 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 97 | 94.8 | 96.4 | 96.7 | 96.9 | 96.9 | 96.7 | 96.7 | 2017-12-01 | 2019-03-01
Fronius International GmbH | Fronius Symo 10.0-3 480 {480V} | N | N | Y | Y | Y | N | N | N | 10 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 9.995 | 480 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [7/27/2017];[03/28/2018] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0] | 2018-10-15 | [7/27/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.86 |  |  | 100 | 670 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 89.6 | 93.7 | 94.8 | 95.3 | 96 | 96.2 | 95.3 | 91.8 | 95.2 | 96.1 | 96.7 | 97.2 | 97.3 | 96.6 | 92.9 | 96.1 | 96.9 | 97.3 | 97.7 | 97.8 | 97.2 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 10.0-3 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 10 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 10.011 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2019-02-15 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.6 |  |  | 300 | 355 | 480 | 1.0011 | 2.0021 | 3.0032 | 5.0053 | 7.508 | 10.0106 | 94.519 | 95.8999 | 96.162 | 96.1988 | 96.0327 | 95.7143 | 96 | 95.4147 | 96.5747 | 96.7816 | 96.8004 | 96.661 | 96.3996 | 96.6375 | 94.3618 | 95.9714 | 96.3244 | 96.445 | 96.0917 | 96.1777 | 96.1229 | 2019-02-15 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 10.0-3 208-240 Lite {208V} | N | N | Y | Y | Y | N | N | N | 10 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 10.011 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2020-05-11 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.6 |  |  | 300 | 355 | 480 | 1.0011 | 2.0021 | 3.0032 | 5.0053 | 7.508 | 10.0106 | 94.519 | 95.8999 | 96.162 | 96.1988 | 96.0327 | 95.7143 | 96 | 95.4147 | 96.5747 | 96.7816 | 96.8004 | 96.661 | 96.3996 | 96.6375 | 94.3618 | 95.9714 | 96.3244 | 96.445 | 96.0917 | 96.1777 | 96.1229 | 2020-05-11
Fronius International GmbH | Primo GEN24 10.0 208-240 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.0 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 10.019 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.5 |  |  | 260 | 385 | 480 | 1.002 | 2.004 | 3.006 | 5.009 | 7.514 | 10.019 | 95.2 | 96.68 | 96.99 | 97.03 | 96.91 | 96.62 | 96.85 | 95.79 | 97.19 | 97.38 | 97.45 | 97.37 | 97.13 | 97.3 | 94.38 | 96.58 | 96.93 | 97.11 | 97.08 | 96.87 | 96.93 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 10.0 208-240 Plus {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.0 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 10.019 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.5 |  |  | 260 | 385 | 480 | 1.002 | 2.004 | 3.006 | 5.009 | 7.514 | 10.019 | 95.2 | 96.68 | 96.99 | 97.03 | 96.91 | 96.62 | 96.85 | 95.79 | 97.19 | 97.38 | 97.45 | 97.37 | 97.13 | 97.3 | 94.38 | 96.58 | 96.93 | 97.11 | 97.08 | 96.87 | 96.93 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Fronius Symo Advanced 10.0-3 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 10 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 10.062 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2019-02-15 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.8 |  |  | 300 | 370 | 480 | 1.0062 | 2.0123 | 3.0185 | 5.0308 | 7.5462 | 10.0616 | 94.0092 | 95.6298 | 96.0803 | 96.2486 | 96.2138 | 96.0334 | 96.0787 | 95.4049 | 96.7635 | 97.0499 | 97.1293 | 97.0789 | 96.9476 | 96.9967 | 94.7759 | 96.3625 | 96.7198 | 96.8607 | 96.8774 | 96.7291 | 96.7377 | 2019-02-15 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 10.0-3 208-240 Lite {240V} | N | N | Y | Y | Y | N | N | N | 10 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 10.062 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2020-05-11 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.8 |  |  | 300 | 370 | 480 | 1.0062 | 2.0123 | 3.0185 | 5.0308 | 7.5462 | 10.0616 | 94.0092 | 95.6298 | 96.0803 | 96.2486 | 96.2138 | 96.0334 | 96.0787 | 95.4049 | 96.7635 | 97.0499 | 97.1293 | 97.0789 | 96.9476 | 96.9967 | 94.7759 | 96.3625 | 96.7198 | 96.8607 | 96.8774 | 96.7291 | 96.7377 | 2020-05-11
Fronius International GmbH | Fronius Primo 11.4-1 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 11.4 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.9.0] | 2018-10-15 | [9/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Model number formerly listed as Fronius Primo 11.4-1 {28V}. | Y | N | 0.24 |  |  | 240 | 660 | 800 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 93 | 94.9 | 95.4 | 95.8 | 95.8 | 95.7 | 95.6 | 95.4 | 97 | 97.3 | 97.4 | 97.4 | 97.4 | 97.3 | 94.5 | 96.4 | 96.9 | 97.2 | 97.2 | 97.3 | 97.1 | 2017-11-01 | 2019-03-01
Fronius International GmbH | Fronius Primo 11.4-1 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 11.4 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.9.0] | 2018-10-15 | [9/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Model number formerly listed as Fronius Primo 11.4-1 {24V}. | Y | N | 0.32 |  |  | 240 | 660 | 800 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 92.1 | 94.8 | 95.3 | 95.8 | 95.9 | 95.8 | 95.6 | 93.7 | 96.1 | 96.6 | 97 | 97.1 | 97.1 | 96.9 | 94.8 | 96.9 | 97.4 | 97.6 | 97.6 | 97.6 | 97.4 | 2017-11-01 | 2019-03-01
Fronius International GmbH | Fronius Symo 12.0-3 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 12 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 12 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [10/16/2017];[03/28/2018] | [ReCerbo V0.3.14.8 Roach V0.26.18.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8, Roach V0.26.25.0 Guard V0.10.9.0] | 2018-10-15 | [10/16/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.61 |  |  | 300 | 350 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 95.4 | 96.2 | 96.3 | 96.2 | 95.9 | 95.4 | 95.9 | 96.3 | 96.9 | 96.9 | 96.8 | 96.5 | 96.2 | 96.6 | 94.7 | 96.1 | 96.4 | 96.4 | 96.3 | 96 | 96.2 | 2017-12-01 | 2019-03-01
Fronius International GmbH | Fronius Symo 12.0-3 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 12 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 12 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [10/16/2017];[03/28/2018] | [ReCerbo V0.3.14.8 Roach V0.26.18.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8, Roach V0.26.25.0 Guard V0.10.9.0] | 2018-10-15 | [10/16/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.81 |  |  | 300 | 370 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.4 | 95.9 | 96.2 | 96.3 | 96.1 | 95.8 | 96.1 | 96 | 96.9 | 97.1 | 97.1 | 97 | 96.8 | 97 | 95.2 | 96.6 | 96.8 | 96.9 | 96.8 | 96.6 | 96.7 | 2017-12-01 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 12.0-3 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 12 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 12.09 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2019-02-15 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.8 |  |  | 300 | 370 | 480 | 1.209 | 2.418 | 3.6271 | 6.0451 | 9.0677 | 12.0902 | 94.3681 | 95.8926 | 96.1836 | 96.2592 | 96.1128 | 95.8185 | 96.0565 | 95.9688 | 96.9444 | 97.0969 | 97.1128 | 97.001 | 96.8186 | 96.9828 | 95.2352 | 96.577 | 96.7993 | 96.8786 | 96.7889 | 96.5969 | 96.7266 | 2019-02-15 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 12.0-3 208-240 Lite {240V} | N | N | Y | Y | Y | N | N | N | 12 kW, 240 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 12.09 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2020-05-11 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.8 |  |  | 300 | 370 | 480 | 1.209 | 2.418 | 3.6271 | 6.0451 | 9.0677 | 12.0902 | 94.3681 | 95.8926 | 96.1836 | 96.2592 | 96.1128 | 95.8185 | 96.0565 | 95.9688 | 96.9444 | 97.0969 | 97.1128 | 97.001 | 96.8186 | 96.9828 | 95.2352 | 96.577 | 96.7993 | 96.8786 | 96.7889 | 96.5969 | 96.7266 | 2020-05-11
Fronius International GmbH | Fronius Symo Advanced 12.0-3 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 12 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 12.341 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2019-02-15 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.61 |  |  | 300 | 350 | 480 | 1.2341 | 2.4682 | 3.7022 | 6.1704 | 9.2556 | 12.3408 | 95.3587 | 96.1848 | 96.2739 | 96.1814 | 95.8555 | 95.4107 | 95.9485 | 96.2658 | 96.8639 | 96.9037 | 96.8162 | 96.5262 | 96.1647 | 96.6208 | 94.7302 | 96.1208 | 96.3848 | 96.4459 | 96.2846 | 96.0009 | 96.2459 | 2019-02-15 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 12.0-3 208-240 Lite {208V} | N | N | Y | Y | Y | N | N | N | 12 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 12.341 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2020-05-11 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.61 |  |  | 300 | 350 | 480 | 1.2341 | 2.4682 | 3.7022 | 6.1704 | 9.2556 | 12.3408 | 95.3587 | 96.1848 | 96.2739 | 96.1814 | 95.8555 | 95.4107 | 95.9485 | 96.2658 | 96.8639 | 96.9037 | 96.8162 | 96.5262 | 96.1647 | 96.6208 | 94.7302 | 96.1208 | 96.3848 | 96.4459 | 96.2846 | 96.0009 | 96.2459 | 2020-05-11
Fronius International GmbH | Fronius Primo 12.5-1 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 12.5 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 12.5 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.9.0] | 2018-10-15 | [9/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Model number formerly listed as Fronius Primo 12.5-1 {28V}. | Y | N | 0.24 |  |  | 260 | 665 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.38 | 12.5 | 92.5 | 95.1 | 95.5 | 95.9 | 95.9 | 95.6 | 95.6 | 95.3 | 96.9 | 97.3 | 97.5 | 97.3 | 97.3 | 97.2 | 94.5 | 96.6 | 97 | 97.2 | 97.1 | 97.2 | 97 | 2017-11-01 | 2019-03-01
Fronius International GmbH | Fronius Primo 12.5-1 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 12.5 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 12.5 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.9.0] | 2018-10-15 | [9/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Model number formerly listed as Fronius Primo 12.5-1 {24V}. | Y | N | 0.32 |  |  | 260 | 660 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.38 | 12.5 | 92.1 | 95 | 95.4 | 95.9 | 95.9 | 95.8 | 95.6 | 93.7 | 96.2 | 96.6 | 97 | 97.1 | 97.1 | 96.8 | 95.4 | 97.2 | 97.3 | 97.5 | 97.6 | 97.7 | 97.5 | 2017-11-01 | 2019-03-01
Fronius International GmbH | Fronius Symo 12.5-3 480 {480V} | N | N | Y | Y | Y | N | N | N | 12.5 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 12.5 | 480 | 97 | No Information Submitted | No Information Submitted | CSA Group | [7/27/2017];[03/28/2018] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0] | 2018-10-15 | [7/27/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.94 |  |  | 350 | 685 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.37 | 12.5 | 92.5 | 94.9 | 95.6 | 96 | 96.4 | 96.5 | 96 | 94.4 | 96.5 | 97 | 97.3 | 97.5 | 97.5 | 97.2 | 95.6 | 97.3 | 97.7 | 97.9 | 98 | 98 | 97.8 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Primo 15.0-1 208-240 {208V} | N | N | Y | Y | Y | N | N | N | 15 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 13.75 | 208 | 97 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.9.0] | 2018-10-15 | [9/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Model number formerly listed as Fronius Primo 15.-1 {28V}. | Y | N | 0.24 |  |  | 320 | 680 | 800 | 1.38 | 2.75 | 4.13 | 6.88 | 10.31 | 13.75 | 93.3 | 95.7 | 96 | 96.3 | 96.2 | 96 | 96 | 95.9 | 97.1 | 97.4 | 97.4 | 97.4 | 97.2 | 97.3 | 95.1 | 96.8 | 97.1 | 97.2 | 97.2 | 97.1 | 97.1 | 2017-11-01 | 2019-03-01
Fronius International GmbH | Fronius Primo 15.0-1 208-240 {240V} | N | N | Y | Y | Y | N | N | N | 15 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 15 | 240 | 97 | No Information Submitted | No Information Submitted | CSA Group | [7/7/2017];[12/21/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0];[ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.9.0] | 2018-10-15 | [9/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Model number formerly listed as Fronius Primo 15.-1 {24V}. | Y | N | 0.32 |  |  | 320 | 680 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.5 | 95.5 | 96 | 96.3 | 96.3 | 96.1 | 96.1 | 94.5 | 96.5 | 96.9 | 97.2 | 97.2 | 97 | 97 | 95.7 | 97.2 | 97.5 | 97.6 | 97.6 | 97.4 | 97.5 | 2017-11-01 | 2019-03-01
Fronius International GmbH | Fronius Symo 15.0-3 208 {208V} | N | N | Y | Y | Y | N | N | N | 15 kW, 208 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 15 | 208 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [9/27/2017] | [ReCerbo V0.3.14.8, Roach V0.26.14.0, Guard V0.10.9.0] | 2018-10-15 | [9/27/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Model number formerly listed as Fronius Symo 15.-3 {28V}. | Y | N | 0.43 |  |  | 325 | 445 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 96.1 | 97 | 97.1 | 97.1 | 96.9 | 96.7 | 96.9 | 95.3 | 96.4 | 96.6 | 96.7 | 96.5 | 96.2 | 96.5 | 92.7 | 94.9 | 95.4 | 95.6 | 95.5 | 95.3 | 95.4 | 2017-11-01 | 2019-03-01
Fronius International GmbH | Fronius Symo 15.0-3 480 {480V} | N | N | Y | Y | Y | N | N | N | 15 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 15 | 480 | 97 | No Information Submitted | No Information Submitted | CSA Group | [7/27/2017];[03/28/2018] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0] | 2018-10-15 | [7/27/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.03 |  |  | 350 | 685 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 92 | 94.9 | 95.6 | 96.2 | 96.5 | 96.4 | 96.1 | 93.5 | 96 | 96.7 | 97.2 | 97.4 | 97.4 | 97.1 | 94.6 | 96.8 | 97.4 | 97.8 | 97.9 | 97.9 | 97.6 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 15.0-3 480 {480V} | N | N | Y | Y | Y | N | N | N | 15 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 15.197 | 480 | 97 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2019-02-15 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1 |  |  | 350 | 685 | 800 | 1.5197 | 3.0394 | 4.559 | 7.5984 | 11.3976 | 15.1968 | 92.0416 | 94.9196 | 95.6245 | 96.2374 | 96.4854 | 96.3871 | 96.0691 | 93.544 | 95.9984 | 96.6963 | 97.2403 | 97.4077 | 97.4379 | 97.0637 | 94.623 | 96.8127 | 97.3656 | 97.7693 | 97.8886 | 97.8973 | 97.6168 | 2019-02-15 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 15.0-3 480 Lite {480V} | N | N | Y | Y | Y | N | N | N | 15 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 15.197 | 480 | 97 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2020-05-11 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1 |  |  | 350 | 685 | 800 | 1.5197 | 3.0394 | 4.559 | 7.5984 | 11.3976 | 15.1968 | 92.0416 | 94.9196 | 95.6245 | 96.2374 | 96.4854 | 96.3871 | 96.0691 | 93.544 | 95.9984 | 96.6963 | 97.2403 | 97.4077 | 97.4379 | 97.0637 | 94.623 | 96.8127 | 97.3656 | 97.7693 | 97.8886 | 97.8973 | 97.6168 | 2020-05-11
Fronius International GmbH | Fronius Symo 17.5-3 480 {480V} | N | N | Y | Y | Y | N | N | N | 17.5 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 17.5 | 480 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [7/27/2017];[03/28/2018] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0] | 2018-10-15 | [7/27/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.03 |  |  | 400 | 700 | 800 | 1.75 | 3.5 | 5.25 | 8.75 | 13.12 | 17.5 | 92.7 | 95.3 | 95.8 | 96.5 | 96.6 | 96.7 | 96.3 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 98.2 | 98 | 94.8 | 96.9 | 97.4 | 97.7 | 97.8 | 97.8 | 97.6 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Symo 20.0-3 480 {480V} | N | N | Y | Y | Y | N | N | N | 20 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [7/27/2017];[03/28/2018] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0] | 2018-10-15 | [7/27/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.04 |  |  | 450 | 712 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.7 | 95.6 | 96.3 | 96.7 | 96.8 | 96.8 | 96.5 | 96 | 97.2 | 97.7 | 98 | 98 | 98 | 97.9 | 95.7 | 97 | 97.5 | 97.7 | 97.8 | 97.8 | 97.6 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 20.0-3 480 {480V} | N | N | Y | Y | Y | N | N | N | 20 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 20.227 | 480 | 97 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2019-02-15 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1 |  |  | 450 | 710 | 800 | 2.0227 | 4.0454 | 6.0681 | 10.1136 | 15.1704 | 20.2271 | 93.0613 | 95.4939 | 96.1422 | 96.7009 | 96.7849 | 96.8065 | 96.4777 | 95.0962 | 97.0421 | 97.5307 | 97.8635 | 97.9715 | 98.0044 | 97.7361 | 94.4625 | 96.6871 | 97.2645 | 97.6594 | 97.7318 | 97.7681 | 97.4793 | 2019-02-15 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 20.0-3 480 Lite {480V} | N | N | Y | Y | Y | N | N | N | 20 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 20.227 | 480 | 97 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2020-05-11 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1 |  |  | 450 | 710 | 800 | 2.0227 | 4.0454 | 6.0681 | 10.1136 | 15.1704 | 20.2271 | 93.0613 | 95.4939 | 96.1422 | 96.7009 | 96.7849 | 96.8065 | 96.4777 | 95.0962 | 97.0421 | 97.5307 | 97.8635 | 97.9715 | 98.0044 | 97.7361 | 94.4625 | 96.6871 | 97.2645 | 97.6594 | 97.7318 | 97.7681 | 97.4793 | 2020-05-11
Fronius International GmbH | Fronius Symo 22.7-3 480 {480V} | N | N | Y | Y | Y | N | N | N | 22.7 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 22.73 | 480 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [7/27/2017];[03/28/2018] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0] | 2018-10-15 | [7/27/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.03 |  |  | 500 | 720 | 800 | 2.27 | 4.55 | 6.82 | 11.36 | 17.05 | 22.73 | 94.3 | 96.2 | 96.7 | 97 | 97 | 96.9 | 96.8 | 96.4 | 97.6 | 97.8 | 98 | 98 | 98 | 97.9 | 95.9 | 97.3 | 97.7 | 97.8 | 97.9 | 97.8 | 97.7 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 22.7-3 480 {480V} | N | N | Y | Y | Y | N | N | N | 22.7 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 22.876 | 480 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2019-02-15 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1 |  |  | 500 | 722 | 800 | 2.2876 | 4.5752 | 6.8627 | 11.4379 | 17.1568 | 22.8758 | 94.3192 | 96.1631 | 96.6618 | 96.9515 | 96.9908 | 96.9484 | 96.7927 | 96.3886 | 97.5518 | 97.8068 | 97.9996 | 98.0209 | 97.9813 | 97.9 | 95.9441 | 97.3371 | 97.6666 | 97.8392 | 97.8629 | 97.8067 | 97.7285 | 2019-02-15 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 22.7-3 480 Lite {480V} | N | N | Y | Y | Y | N | N | N | 22.7 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 22.876 | 480 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2020-05-11 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1 |  |  | 500 | 722 | 800 | 2.2876 | 4.5752 | 6.8627 | 11.4379 | 17.1568 | 22.8758 | 94.3192 | 96.1631 | 96.6618 | 96.9515 | 96.9908 | 96.9484 | 96.7927 | 96.3886 | 97.5518 | 97.8068 | 97.9996 | 98.0209 | 97.9813 | 97.9 | 95.9441 | 97.3371 | 97.6666 | 97.8392 | 97.8629 | 97.8067 | 97.7285 | 2020-05-11
Fronius International GmbH | Fronius Symo 24.0-3 480 {480V} | N | N | Y | Y | Y | N | N | N | 24 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 24 | 480 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [7/27/2017];[03/28/2018] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10];[ReCerbo V0.3.14.8, Roach V0.26.25.0, Guard V0.10.9.0] | 2018-10-15 | [7/27/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.03 |  |  | 500 | 725 | 800 | 2.4 | 4.8 | 7.2 | 12 | 18 | 24 | 94.3 | 96.1 | 96.6 | 97 | 97 | 97 | 96.8 | 96.2 | 97.5 | 97.8 | 98 | 98 | 97.9 | 97.9 | 95.8 | 97.2 | 97.6 | 97.8 | 97.8 | 97.7 | 97.7 | 2017-08-01 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 24.0-3 480 {480V} | N | N | Y | Y | Y | N | N | N | 24 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 24.142 | 480 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2019-02-15 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1 |  |  | 500 | 722 | 800 | 2.4142 | 4.8284 | 7.2425 | 12.0709 | 18.1063 | 24.1418 | 94.2986 | 96.1383 | 96.5889 | 96.9511 | 96.9529 | 96.9541 | 96.762 | 96.245 | 97.4769 | 97.7906 | 97.9573 | 97.9828 | 97.923 | 97.8566 | 95.7696 | 97.2344 | 97.6169 | 97.8217 | 97.8136 | 97.7248 | 97.6765 | 2019-02-15 | 2019-03-01
Fronius International GmbH | Fronius Symo Advanced 24.0-3 480 Lite {480V} | N | N | Y | Y | Y | N | N | N | 24 kW, 480 Vac, three phase Grid Support Utility Interactive Inverter with arc detector and meter | 24.142 | 480 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [11/22/2018] | [ReCerbo V0.3.17.2, Roach V0.28.4.0, Guard V0.11.05.3] | 2020-05-11 | [11/22/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1 |  |  | 500 | 722 | 800 | 2.4142 | 4.8284 | 7.2425 | 12.0709 | 18.1063 | 24.1418 | 94.2986 | 96.1383 | 96.5889 | 96.9511 | 96.9529 | 96.9541 | 96.762 | 96.245 | 97.4769 | 97.7906 | 97.9573 | 97.9828 | 97.923 | 97.8566 | 95.7696 | 97.2344 | 97.6169 | 97.8217 | 97.8136 | 97.7248 | 97.6765 | 2020-05-11
Gamesa Electric | PV3800 {600V} | N | N | Y | Y | Y | N | N | N | 3800 kVA, 600 Vac Grid Support Utilitity Interactive Inverters | 3418.394 | 600 | 98 | No Information Submitted | No Information Submitted | MET | [12/3/2020] | [FIP 1027 1.1.4] | 2021-02-22 | [12/3/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer. | N | N | 267 |  |  | 835 | 1050 | 1300 | 341.8394 | 683.6788 | 1025.5182 | 1709.197 | 2563.7955 | 3418.394 | 97.5368 | 98.6736 | 98.6896 | 98.5623 | 98.2361 | 97.9035 | 98.3363 | 96.8188 | 98.0047 | 98.478 | 98.2951 | 97.85 | 97.4265 | 97.9642 | 95.972 | 97.5805 | 98.0808 | 98.0328 | 97.6733 | 97.2614 | 97.7044 | 2021-02-22
Gamesa Electric | PV4000 {630V} | N | N | Y | Y | Y | N | N | N | 4000 kVA, 630 Vac Grid Support Utilitity Interactive Inverters | 3597.332 | 630 | 98 | No Information Submitted | No Information Submitted | MET | [12/3/2020] | [FIP 1027 1.1.4] | 2021-02-22 | [12/3/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer. | N | N | 267 |  |  | 875 | 1050 | 1300 | 359.7332 | 719.4664 | 1079.1996 | 1798.666 | 2697.999 | 3597.332 | 97.4581 | 98.5595 | 98.6972 | 98.5797 | 98.2482 | 97.9387 | 98.3402 | 96.7477 | 98.0329 | 98.356 | 98.2625 | 97.8771 | 97.5187 | 97.9602 | 96.2671 | 97.713 | 98.2326 | 98.1645 | 97.7513 | 97.3373 | 97.8139 | 2021-02-22
Gamesa Electric | PV4200 {660V} | N | N | Y | Y | Y | N | N | N | 4200 kVA, 660 Vac Grid Support Utilitity Interactive Inverters | 3767.352 | 660 | 98 | No Information Submitted | No Information Submitted | MET | [12/3/2020] | [FIP 1027 1.1.4] | 2021-02-22 | [12/3/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer. | N | N | 267 |  |  | 915 | 1050 | 1300 | 376.7352 | 753.4704 | 1130.2056 | 1883.676 | 2825.514 | 3767.352 | 97.4802 | 98.7142 | 98.8271 | 98.6953 | 98.3759 | 98.0193 | 98.4604 | 96.9767 | 98.5407 | 98.7092 | 98.53 | 98.1361 | 97.7017 | 98.2397 | 96.4716 | 97.7801 | 98.2885 | 98.221 | 97.9008 | 97.4865 | 97.9307 | 2021-02-22
Gamesa Electric | PV4400 {690V} | N | N | Y | Y | Y | N | N | N | 4400 kVA, 690 Vac Grid Support Utilitity Interactive Inverters | 3939.574 | 690 | 98 | No Information Submitted | No Information Submitted | MET | [12/3/2020] | [FIP 1027 1.1.4] | 2021-02-22 | [12/3/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer. | N | N | 267 |  |  | 955 | 1050 | 1300 | 393.9574 | 787.9148 | 1181.8722 | 1969.787 | 2954.6805 | 3939.574 | 97.42 | 98.3506 | 98.6127 | 98.6011 | 98.3075 | 98.0508 | 98.3596 | 96.9302 | 98.0124 | 98.3502 | 98.3186 | 97.9864 | 97.6293 | 98.041 | 96.0812 | 97.6626 | 97.9195 | 97.9842 | 97.6762 | 97.2743 | 97.6855 | 2021-02-22
Gamesa Electric | PV4100 {600V} | N | N | Y | Y | Y | N | N | N | 4100 kVA, 600 Vac Grid Support Utilitity Interactive Inverters | 4054.978 | 600 | 98 | No Information Submitted | No Information Submitted | MET | [12/3/2020] | [FIP 1027 1.1.4] | 2021-02-22 | [12/3/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer. | N | N | 267 |  |  | 835 | 1050 | 1300 | 405.4978 | 810.9956 | 1216.4934 | 2027.489 | 3041.2335 | 4054.978 | 98.6581 | 99.3905 | 99.3538 | 99.178 | 98.9099 | 98.7334 | 99.0246 | 97.8835 | 98.7067 | 99.1432 | 98.9004 | 98.5255 | 98.1784 | 98.6444 | 96.9309 | 98.312 | 98.8228 | 98.7185 | 98.3973 | 98.1195 | 98.439 | 2021-02-22 | 2021-12-01
Gamesa Electric | PV4300 {630V} | N | N | Y | Y | Y | N | N | N | 4300 kVA, 630 Vac Grid Support Utilitity Interactive Inverters | 4260.428 | 630 | 98 | No Information Submitted | No Information Submitted | MET | [12/3/2020] | [FIP 1027 1.1.4] | 2021-02-22 | [12/3/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer. | N | N | 267 |  |  | 875 | 1050 | 1300 | 426.0428 | 852.0856 | 1278.1284 | 2130.214 | 3195.321 | 4260.428 | 97.572 | 98.6565 | 98.7953 | 98.6438 | 98.2843 | 97.9457 | 98.3943 | 97.0358 | 98.4773 | 98.5621 | 98.3725 | 97.9356 | 97.4696 | 98.0703 | 96.094 | 97.8374 | 98.3574 | 98.2203 | 97.7892 | 97.3192 | 97.859 | 2021-02-22 | 2021-12-01
Gamesa Electric | PV4500 {660V} | N | N | Y | Y | Y | N | N | N | 4500 kVA, 660 Vac Grid Support Utilitity Interactive Inverters | 4405.964 | 660 | 98 | No Information Submitted | No Information Submitted | MET | [12/3/2020] | [FIP 1027 1.1.4] | 2021-02-22 | [12/3/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer. | N | N | 267 |  |  | 915 | 1050 | 1300 | 440.5964 | 881.1928 | 1321.7892 | 2202.982 | 3304.473 | 4405.964 | 97.5099 | 98.7494 | 98.8289 | 98.6843 | 98.3181 | 98.0108 | 98.4302 | 96.9982 | 98.5232 | 98.5734 | 98.433 | 98.0395 | 97.6204 | 98.1478 | 96.4861 | 97.8213 | 98.4772 | 98.3072 | 97.8413 | 97.4256 | 97.9394 | 2021-02-22 | 2021-12-01
Gamesa Electric | PV4700 {690V} | N | N | Y | Y | Y | N | N | N | 4700 kVA, 690 Vac Grid Support Utilitity Interactive Inverters | 4654.418 | 690 | 98 | No Information Submitted | No Information Submitted | MET | [12/3/2020] | [FIP 1027 1.1.4] | 2021-02-22 | [12/3/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 4.7 MVA Magnetron, Loop Feed Pad-mounted Step-Up Transformer. | N | N | 267 |  |  | 955 | 1050 | 1300 | 465.4418 | 930.8836 | 1396.3254 | 2327.209 | 3490.8135 | 4654.418 | 97.4916 | 98.7995 | 98.8886 | 98.7326 | 98.3487 | 98.0507 | 98.4675 | 97.1562 | 98.4764 | 98.583 | 98.4348 | 98.0743 | 97.6869 | 98.1751 | 96.5244 | 97.9731 | 98.5074 | 98.4205 | 97.9383 | 97.5044 | 98.0314 | 2021-02-22 | 2021-12-01
GE Renewable Energy | RIU-2500-U {550V} | Y | N | Y | Y | Y | N | N | N | 2500 kVA, 550 Vac, Bi-directional, Grid Support Utility Interactive Hybrid Inverter | 2507.194 | 550 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [11/01/2019] | [DSP_RIU-2500-U_V11_V1_A, LCD_RIU-2500-U_V1_A] | 2020-03-23 | [11/01/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 2500 kVA Medium-Voltage Dry-Type Distribution Transformers Table in DOE216. | N | N | 62.8 |  |  | 800 | 975 | 1500 | 250.7194 | 501.4388 | 752.1582 | 1253.597 | 1880.3955 | 2507.194 | 96.1656 | 97.496 | 97.8461 | 97.9177 | 97.6547 | 97.324 | 97.6489 | 96.0246 | 97.2391 | 97.7308 | 97.8521 | 97.5444 | 97.19 | 97.5376 | 95.4326 | 96.8219 | 97.3458 | 97.4664 | 97.1968 | 96.9426 | 97.1693 | 2021-03-01
Generac Power Systems, Inc. | CP-380-V2 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 380 W, 208 Vac Grid Support Utility Interactive Inverter | 0.38 | 208 | 96.5 | Intertek | [6/27/2024] | Intertek | [6/27/2024] | [FW Rev 201] | 2024-08-21 | [7/29/2024] | 2024-08-21 | Intertek | 2024-09-06 | 2024-08-21 |  | N | Y | 0.14 |  |  | 32 | 34 | 36 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 90.65 | 95.2 | 96.2 | 96.81 | 96.89 | 96.73 | 96.45 | 89.74 | 94.94 | 96.04 | 96.74 | 96.89 | 96.77 | 96.37 | 89.3 | 94.61 | 95.92 | 96.66 | 96.87 | 96.78 | 96.29 | 2024-08-21 | 2024-11-01
Generac Power Systems, Inc. | CP-380-V2 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 380 W, 240 Vac Grid Support Utility Interactive Inverter | 0.38 | 240 | 96.5 | Intertek | [6/27/2024] | Intertek | [6/27/2024] | [FW Rev 201] | 2024-08-21 | [7/29/2024] | 2024-08-21 | Intertek | 2024-09-06 | 2024-08-21 |  | N | Y | 0.19 |  |  | 32 | 34 | 36 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 90.83 | 95.17 | 96.19 | 96.9 | 97.02 | 96.87 | 96.55 | 89.94 | 94.87 | 96.04 | 96.83 | 97.04 | 96.96 | 96.48 | 88.94 | 94.59 | 95.86 | 96.73 | 96.98 | 96.95 | 96.35 | 2024-08-21 | 2024-11-01
Generac Power Systems, Inc. | CP-760-V2 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 760 W, 240 Vac Grid Support Utility Interactive Inverter | 0.761 | 240 | 97 | Intertek | [6/27/2024] | Intertek | [6/27/2024] | [FW Rev 201] | 2024-08-21 | [7/29/2024] | 2024-08-21 | Intertek | 2024-09-06 | 2024-08-21 |  | N | Y | 0.19 |  |  | 63 | 68 | 72 | 0.076 | 0.152 | 0.228 | 0.381 | 0.571 | 0.761 | 94.05 | 96.47 | 97.05 | 97.27 | 97.07 | 96.71 | 96.94 | 93.42 | 96.27 | 96.93 | 97.24 | 97.11 | 96.78 | 96.91 | 92.93 | 96.05 | 96.8 | 97.2 | 97.13 | 96.89 | 96.87 | 2024-08-21 | 2024-11-01
Generac Power Systems, Inc. | CP-760-V2 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 760 W, 208 Vac Grid Support Utility Interactive Inverter | 0.762 | 208 | 96.7 | Intertek | [6/27/2024] | Intertek | [6/27/2024] | [FW Rev 201] | 2024-08-21 | [7/29/2024] | 2024-08-21 | Intertek | 2024-09-06 | 2024-08-21 |  | N | Y | 0.14 |  |  | 63 | 68 | 72 | 0.076 | 0.152 | 0.228 | 0.381 | 0.571 | 0.762 | 94.06 | 96.43 | 96.95 | 97.09 | 96.8 | 96.35 | 96.73 | 93.42 | 96.22 | 96.83 | 97.06 | 96.8 | 96.43 | 96.68 | 92.86 | 96.02 | 96.7 | 97.01 | 96.86 | 96.55 | 96.65 | 2024-08-21 | 2024-11-01
Generac Power Systems, Inc. | PM-820 {208V} | N | Y | N | N | N | N | Y* | N | 0.82 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.82 | 208 | 96.5 | Intertek | [6/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2025-06-26 | No Information Submitted |  | N | Y | 0.35 |  |  | 31.5 | 37.5 | 40 | 0.082 | 0.164 | 0.246 | 0.41 | 0.615 | 0.82 | 93.91 | 96.61 | 97.12 | 97.2 | 96.86 | 96.38 | 96.81 | 92.04 | 96 | 96.74 | 97.1 | 96.96 | 96.6 | 96.7 | 91.16 | 95.56 | 96.55 | 97.01 | 96.99 | 96.74 | 96.62 | 2025-08-01
Generac Power Systems, Inc. | PM-820 {240V} | N | Y | N | N | N | N | Y* | N | 0.82 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.82 | 240 | 97 | Intertek | [6/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2025-06-26 | No Information Submitted |  | N | Y | 0.39 |  |  | 31.5 | 37.5 | 40 | 0.082 | 0.164 | 0.246 | 0.41 | 0.615 | 0.82 | 94.18 | 96.63 | 97.19 | 97.32 | 97.01 | 96.54 | 96.94 | 92.61 | 96.02 | 96.83 | 97.24 | 97.15 | 96.85 | 96.88 | 91.65 | 95.64 | 96.66 | 97.18 | 97.19 | 96.99 | 96.81 | 2025-08-01
Generac Power Systems, Inc. | X7602 {240V} | Y | N | Y | Y | Y | Y | Y | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS Functionality | 7.586 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [10/09/2020] | [13430];[13590] | 2020-02-03 | [10/09/2020] | 2020-03-23 | SunSpec Alliance | 2019-11-26 | 2020-02-03 | Model number formerly listed as Pika Energy | N | N | 1.2917 |  |  | 390 | 400 | 420 | 0.759 | 1.517 | 2.276 | 3.793 | 5.689 | 7.586 | 91.67 | 95.89 | 96.62 | 97.26 | 97.24 | 97.04 | 96.87 | 91.01 | 95.4 | 96.52 | 97.26 | 97.15 | 97.01 | 96.75 | 90.48 | 95.21 | 96.33 | 96.86 | 97.02 | 96.91 | 96.55 | 2020-02-03 | 2021-04-01
Generac Power Systems, Inc. | XVT076A03 {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS Functionality | 7.606 | 240 | 96.5 | Intertek | [6/30/2023] | Intertek | [10/09/2020] | [13430];[13590] | 2020-10-01 | [10/09/2020] | 2020-10-01 | SunSpec Alliance | 2023-06-13 | 2020-10-01 |  | N | N | 41.9 |  |  | 390 | 400 | 420 | 0.76057 | 1.5211 | 2.2817 | 3.8028 | 5.7042 | 7.6057 | 93.8895 | 96.2047 | 96.7309 | 96.8111 | 96.547 | 96.1964 | 96.4836 | 93.6733 | 96.1311 | 96.6969 | 96.8149 | 96.6123 | 96.2609 | 96.5058 | 93.0587 | 95.8723 | 96.494 | 96.6834 | 96.4511 | 96.1331 | 96.3245 | 2020-10-01 | 2023-08-11
Generac Power Systems, Inc. | X11402 {208V} | Y | N | Y | Y | Y | Y | Y | Y | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS Functionality | 11.18 | 208 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [10/09/2020] | [13430];[13590] | 2020-02-03 | [10/09/2020] | 2020-03-23 | SunSpec Alliance | 2019-11-26 | 2020-02-03 | Model number formerly listed as Pika Energy | N | N | 0.125 |  |  | 390 | 400 | 420 | 1.118 | 2.236 | 3.354 | 5.59 | 8.385 | 11.18 | 97.25 | 97.35 | 97.58 | 97.65 | 97.44 | 97.06 | 97.47 | 97.03 | 97.35 | 97.67 | 97.54 | 97.25 | 96.93 | 97.34 | 95.83 | 97.24 | 97.27 | 97.39 | 97.08 | 96.89 | 97.12 | 2020-02-03 | 2021-04-01
Generac Power Systems, Inc. | XVT114G03 {208V} | Y | N | Y | Y | Y | Y | Y | Y | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS Functionality | 11.748 | 208 | 97 | No Information Submitted | No Information Submitted | Intertek | [10/09/2020] | [13430];[13590] | 2020-10-01 | [10/09/2020] | 2020-10-01 | SunSpec Alliance | 2019-11-26 | 2020-10-01 |  | N | N | 0.13 |  |  | 390 | 400 | 420 | 1.1748 | 2.3496 | 3.5243 | 5.8739 | 8.8109 | 11.7478 | 94.3952 | 96.3614 | 96.9844 | 97.3488 | 97.3913 | 97.3223 | 97.1588 | 93.8375 | 96.116 | 96.8135 | 97.3003 | 97.2556 | 97.1149 | 97.0112 | 92.9035 | 95.7659 | 96.54 | 97.0771 | 97.168 | 97.0658 | 96.8278 | 2020-10-01 | 2021-04-01
General Motors Energy LLC | GM Energy Inverter e1.11 {208V} | Y | Y | N | N | N | N | Y* | Y | 11.520 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.0568 | 208 | 97 | CSA Group | [5/15/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-28 | 2024-08-21 |  | N | N | 16.23 |  |  | 200 | 380 | 480 | 1.0057 | 2.0114 | 3.017 | 5.0284 | 7.5426 | 10.0568 | 94.5201 | 96.389 | 96.8997 | 96.9415 | 96.5333 | 95.9709 | 96.5472 | 95.9899 | 97.4283 | 97.7143 | 97.6655 | 97.2997 | 96.965 | 97.3636 | 95.4895 | 97.1344 | 97.5396 | 97.6477 | 97.4208 | 96.8726 | 97.3637 | 2024-08-21
General Motors Energy LLC | GM Energy Inverter e1.11 {240V} | Y | Y | N | N | N | N | Y* | Y | 11.520 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.5886 | 240 | 97.5 | CSA Group | [5/15/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-28 | 2024-08-21 |  | N | N | 16.48 |  |  | 200 | 380 | 480 | 1.1589 | 2.3177 | 3.4766 | 5.7943 | 8.6914 | 11.5886 | 94.7826 | 96.6129 | 97.0546 | 97.1271 | 96.6484 | 96.0211 | 96.6899 | 96.5172 | 97.7857 | 97.9547 | 97.9185 | 97.5962 | 97.3165 | 97.6593 | 96.0248 | 97.4984 | 97.8115 | 97.8312 | 97.6456 | 97.2776 | 97.6139 | 2024-08-21
Geneverse Energy Inc. | GVI-HS-5K-USM {240V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac, Grid Support Utility Interactive Inverter | 5.0897 | 240 | 97 | SGS | [6/2/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-07-03 | 2023-09-01 |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2023-09-01
Geneverse Energy Inc. | GVI-HS-6K-USM {240V} | Y | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac, Grid Support Utility Interactive Inverter | 6.1172 | 240 | 97 | SGS | [6/2/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-07-03 | 2023-09-01 |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2023-09-01
Geneverse Energy Inc. | GVI-HS-7K6-USM {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Grid Support Utility Interactive Inverter | 7.7647 | 240 | 97 | SGS | [6/2/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-07-03 | 2023-09-01 |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2023-09-01
Geneverse Energy Inc. | GVI-HS-8K-USM {240V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 240 Vac, Grid Support Utility Interactive Inverter | 8.0842 | 240 | 97.5 | SGS | [6/2/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-07-03 | 2023-09-01 |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2023-09-01
Geneverse Energy Inc. | GVI-HS-10K-USM {240V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 240 Vac, Grid Support Utility Interactive Inverter | 10.1767 | 240 | 97 | SGS | [6/2/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-07-03 | 2023-09-01 |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2023-09-01
Ginlong Technologies Co., Ltd. | Solis-1P2.5K-4G-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 2.5 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 2.5 | 240 | 97 | No Information Submitted | No Information Submitted | Intertek | [8/14/2017] | [08_01] | 2018-10-15 | [8/14/2017] | 2020-09-11 | CSA Group | 2020-07-20 | 2020-09-11 |  | N | N | 3.2 |  |  | 120 | 330 | 500 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.6401 | 94.6457 | 95.692 | 96.8363 | 96.713 | 96.4833 | 96.3786 | 93.9159 | 95.5043 | 96.5921 | 97.6896 | 97.4379 | 97.114 | 97.1355 | 93.7984 | 95.1685 | 96.3297 | 97.4269 | 96.9989 | 96.8047 | 96.7792 | 2017-10-16 | 2020-09-11
Ginlong Technologies Co., Ltd. | Solis-1P3K-4G-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 3 | 240 | 97 | No Information Submitted | No Information Submitted | Intertek | [8/14/2017] | [08_01] | 2018-10-15 | [8/14/2017] | 2020-09-11 | CSA Group | 2020-07-20 | 2020-09-11 |  | N | N | 3.3 |  |  | 140 | 330 | 500 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.8664 | 94.7136 | 95.6114 | 97.0574 | 96.8122 | 96.477 | 96.4801 | 94.0667 | 95.6697 | 96.5539 | 97.7675 | 97.4264 | 97.0012 | 97.1499 | 93.845 | 95.2969 | 96.1758 | 97.4408 | 97.1733 | 96.697 | 96.859 | 2017-10-16 | 2020-09-11
Ginlong Technologies Co., Ltd. | Solis-1P3.6K-4G-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 3.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 3.6 | 240 | 97 | Intertek | [9/13/2022] | Intertek | [8/14/2017] | [08_01] | 2018-10-15 | [8/14/2017] | 2020-09-11 | CSA Group | 2020-07-20 | 2020-09-11 |  | N | N | 3.5 |  |  | 180 | 330 | 500 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 93.8804 | 94.7446 | 95.6302 | 97.0904 | 96.8386 | 96.4907 | 96.506 | 93.9017 | 95.6722 | 96.8973 | 97.7959 | 97.4214 | 97.0622 | 97.1909 | 93.8792 | 95.4947 | 96.5522 | 97.4831 | 97.1511 | 96.7645 | 96.9159 | 2017-10-16 | 2023-02-01
Ginlong Technologies Co., Ltd. | S6-EH1P3.8K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 3.801 | 240 | 96.5 | CSA Group | [2/23/2024] | CSA Group | [1/13/2023] | [A2] | 2023-04-14 | [1/13/2023] | 2023-04-21 | CSA Group | 2023-01-28 | 2023-04-14 |  | N | N | 18.83 |  |  | 140 | 370 | 450 | 0.3801 | 0.7602 | 1.1403 | 1.9005 | 2.8507 | 3.801 | 96.5132 | 96.0087 | 96.4231 | 96.6237 | 96.6367 | 96.6709 | 96.5737 | 95.4944 | 96.0488 | 96.5134 | 96.4535 | 96.739 | 97.0521 | 96.5833 | 95.2959 | 95.8208 | 96.406 | 96.5264 | 96.7141 | 96.5462 | 96.528 | 2023-04-14 | 2025-06-11
Ginlong Technologies Co., Ltd. | Solis-1P4K-4G-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 4 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 4 | 240 | 97 | No Information Submitted | No Information Submitted | Intertek | [8/14/2017] | [08_01] | 2018-10-15 | [8/14/2017] | 2020-09-11 | CSA Group | 2020-07-20 | 2020-09-11 |  | N | N | 3.5 |  |  | 190 | 330 | 500 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.8715 | 94.7255 | 96.0908 | 97.0869 | 96.8217 | 96.404 | 96.546 | 94.0293 | 95.7206 | 96.9837 | 97.9192 | 97.4909 | 97.3216 | 97.2845 | 93.8761 | 95.4725 | 96.5568 | 97.5311 | 97.1444 | 96.7796 | 96.9225 | 2017-10-16 | 2020-09-11
Ginlong Technologies Co., Ltd. | Solis-1P4.6K-4G-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 4.6 | 240 | 97 | No Information Submitted | No Information Submitted | Intertek | [8/14/2017] | [08_01] | 2018-10-15 | [8/14/2017] | 2020-09-11 | CSA Group | 2020-07-20 | 2020-09-11 |  | N | N | 3.6 |  |  | 200 | 360 | 500 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.0282 | 94.3391 | 95.7359 | 96.9043 | 96.8001 | 96.5325 | 96.407 | 94.0655 | 95.5741 | 96.9074 | 97.9375 | 97.5427 | 97.3118 | 97.3003 | 93.7876 | 95.1009 | 96.5461 | 97.4374 | 97.2666 | 96.964 | 96.9534 | 2017-10-16 | 2020-09-11
Ginlong Technologies Co., Ltd. | Solis-1P5K-4G-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 5 | 240 | 97 | Intertek | [9/13/2022] | Intertek | [8/14/2017] | [08_01] | 2018-10-15 | [8/14/2017] | 2020-09-11 | CSA Group | 2020-07-20 | 2020-09-11 |  | N | N | 3.6 |  |  | 240 | 360 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.9967 | 94.5979 | 95.7172 | 97.3161 | 97.0155 | 96.5167 | 96.6563 | 94.5418 | 95.7374 | 96.5953 | 97.9319 | 97.6168 | 97.433 | 97.3342 | 94.0094 | 94.9752 | 96.145 | 97.4705 | 97.3308 | 96.8481 | 96.9431 | 2017-10-16 | 2023-02-01
Ginlong Technologies Co., Ltd. | S6-EH1P5K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 5.0017 | 240 | 96.5 | CSA Group | [2/23/2024] | CSA Group | [1/13/2023] | [A2] | 2023-04-14 | [1/13/2023] | 2023-04-21 | CSA Group | 2023-01-28 | 2023-04-14 |  | N | N | 18.83 |  |  | 140 | 370 | 450 | 0.50017 | 1.0003 | 1.5005 | 2.5008 | 3.7512 | 5.0017 | 94.2264 | 95.2572 | 96.6079 | 96.5986 | 96.7891 | 96.6855 | 96.5431 | 95.377 | 95.8168 | 96.542 | 96.5776 | 96.8363 | 96.978 | 96.6444 | 95.1057 | 95.5303 | 96.4585 | 96.5737 | 96.7108 | 96.7105 | 96.5285 | 2023-04-14 | 2025-06-11
Ginlong Technologies Co., Ltd. | RHI-1P5K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 5.003 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 115 | 330 | 450 | 0.5 | 1.001 | 1.501 | 2.501 | 3.752 | 5.003 | 95.12 | 96.18 | 96.94 | 97.37 | 97.18 | 96.63 | 97.03 | 95.66 | 97.24 | 97.42 | 97.55 | 97.7 | 96.96 | 97.49 | 95.38 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71 | 97.65 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | Solis-1P6K2-4G-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, 1-phase Utility Interactive Inverter, 2 channel | 6 | 240 | 97 | No Information Submitted | No Information Submitted | Intertek | [8/14/2017] | [08_01] | 2018-10-15 | [8/14/2017] | 2020-09-11 | CSA Group | 2020-07-20 | 2020-09-11 |  | N | N | 3.5 |  |  | 300 | 360 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1975 | 94.8034 | 95.9161 | 97.4325 | 97.2123 | 96.7122 | 96.837 | 94.4335 | 95.6416 | 96.5269 | 97.8303 | 97.7139 | 97.3363 | 97.3422 | 94.2126 | 95.1763 | 96.3489 | 97.6663 | 97.5266 | 97.0427 | 97.1403 | 2017-10-16 | 2020-09-11
Ginlong Technologies Co., Ltd. | Solis-1P6K-4G-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, 3 channel | 6 | 240 | 97.5 | CSA Group | [10/15/2022] | Intertek | [06/30/2019] | [08_01] | 2018-10-15 | [06/30/2019] | 2020-09-01 | CSA Group | 2020-07-20 | 2020-09-01 |  | N | N | 6 |  |  | 200 | 380 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.8998 | 96.1208 | 96.7645 | 97.3045 | 97.3234 | 96.4761 | 97.0529 | 95.5487 | 96.9813 | 97.3964 | 97.4228 | 97.3717 | 97.9525 | 97.322 | 95.3083 | 96.9146 | 97.4794 | 97.5873 | 97.5795 | 97.5828 | 97.4452 | 2017-10-16 | 2023-02-01
Ginlong Technologies Co., Ltd. | RHI-1P6K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 6.004 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 130 | 330 | 450 | 0.6 | 1.201 | 1.801 | 3.002 | 4.503 | 6.004 | 94.9 | 96.12 | 96.76 | 97.3 | 97.32 | 96.48 | 97.05 | 95.55 | 96.98 | 97.4 | 97.42 | 97.37 | 97.95 | 97.32 | 95.31 | 96.91 | 97.48 | 97.59 | 97.58 | 97.58 | 97.45 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | Solis-1P7K-4G-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 7 | 240 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [06/30/2019] | [08_01] | 2018-10-15 | [06/30/2019] | 2020-09-01 | CSA Group | 2020-07-20 | 2020-09-01 |  | Y | N | 7 |  |  | 250 | 380 | 500 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94.9607 | 96.155 | 96.8314 | 97.3565 | 97.3538 | 96.5398 | 97.0953 | 95.5846 | 97.0123 | 97.429 | 97.5 | 97.509 | 97.0437 | 97.3725 | 95.3208 | 96.9551 | 97.5201 | 97.6639 | 97.5988 | 97.5959 | 97.4796 | 2017-10-16 | 2020-09-01
Ginlong Technologies Co., Ltd. | RHI-1P7K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 7.006 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 160 | 330 | 450 | 0.701 | 1.401 | 2.102 | 3.503 | 5.254 | 7.006 | 94.96 | 96.16 | 96.83 | 97.36 | 97.35 | 96.54 | 97.1 | 95.58 | 97.01 | 97.43 | 97.5 | 97.51 | 97.04 | 97.37 | 95.32 | 96.96 | 97.52 | 97.66 | 97.6 | 97.6 | 97.48 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | Solis-1P7.6K-4G-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 7.6 | 240 | 97.5 | CSA Group | [10/15/2022] | Intertek | [06/30/2019] | [08_01] | 2018-10-15 | [06/30/2019] | 2020-09-01 | CSA Group | 2020-07-20 | 2020-09-01 |  | N | N | 7 |  |  | 200 | 380 | 500 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.0545 | 96.1601 | 96.8885 | 97.3433 | 97.1468 | 96.576 | 96.9955 | 95.631 | 97.1836 | 97.4753 | 97.7794 | 97.347 | 97.8962 | 97.4038 | 95.3586 | 96.7534 | 97.606 | 97.8242 | 97.8541 | 97.7094 | 97.6559 | 2017-10-16 | 2023-02-01
Ginlong Technologies Co., Ltd. | RHI-1P7.6K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 7.603 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 175 | 330 | 450 | 0.76 | 1.521 | 2.281 | 3.801 | 5.702 | 7.603 | 95.05 | 96.16 | 96.89 | 97.34 | 97.15 | 96.58 | 97 | 95.63 | 97.18 | 97.48 | 97.78 | 97.35 | 97.9 | 97.4 | 95.36 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71 | 97.66 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | S6-EH1P7.6K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.604 | 240 | 97 | CSA Group | [2/23/2024] | CSA Group | [8/5/2023] | [A2] | 2023-04-14 | [1/13/2023] | 2023-04-21 | CSA Group | 2023-04-19 | 2023-04-14 | Formerly S6-EH1P7.6K-H-L-US. | N | N | 16.33 |  |  | 175 | 380 | 450 | 0.76 | 1.521 | 2.281 | 3.802 | 5.703 | 7.604 | 95.78 | 96.57 | 97.14 | 97.12 | 97.27 | 97.32 | 97.13 | 95.02 | 96.11 | 97.17 | 97.26 | 97.29 | 97.63 | 97.13 | 94.73 | 96.14 | 96.95 | 97.09 | 97.15 | 97.33 | 96.97 | 2023-04-14 | 2025-06-11
Ginlong Technologies Co., Ltd. | Solis-1P8K-4G-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 8 | 240 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [06/30/2019] | [08_01] | 2018-10-15 | [06/30/2019] | 2020-09-01 | CSA Group | 2020-07-20 | 2020-09-01 |  | N | N | 6 |  |  | 250 | 380 | 500 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.1153 | 96.1755 | 96.939 | 97.3693 | 97.1827 | 96.6319 | 97.0321 | 95.6565 | 97.2399 | 97.4217 | 97.5479 | 97.7024 | 96.9559 | 97.494 | 95.3757 | 96.7466 | 97.6107 | 97.8173 | 97.8528 | 97.7053 | 97.6545 | 2017-10-16 | 2020-09-01
Ginlong Technologies Co., Ltd. | RHI-1P8K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 8.006 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 185 | 330 | 450 | 0.801 | 1.601 | 2.402 | 4.003 | 6.004 | 8.006 | 95.12 | 96.18 | 96.94 | 97.37 | 97.18 | 96.63 | 97.03 | 95.66 | 97.24 | 97.42 | 97.55 | 97.7 | 96.96 | 97.49 | 95.38 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71 | 97.65 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | Solis-1P9K-4G-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 9 | 240 | 97.5 | CSA Group | [10/15/2022] | Intertek | [06/30/2019] | [08_01] | 2018-10-15 | [06/30/2019] | 2020-09-01 | CSA Group | 2020-07-20 | 2020-09-01 |  | N | N | 7 |  |  | 250 | 380 | 500 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 95.142 | 96.7533 | 96.9992 | 97.4866 | 97.373 | 96.9957 | 97.2129 | 95.718 | 97.2744 | 97.4478 | 97.6088 | 97.7501 | 97.1064 | 97.5469 | 95.5774 | 96.7392 | 97.6611 | 97.8213 | 97.8215 | 97.7076 | 97.6526 | 2017-10-16 | 2024-03-11
Ginlong Technologies Co., Ltd. | RHI-1P9K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 9 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 9.006 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 210 | 330 | 450 | 0.901 | 1.801 | 2.702 | 4.503 | 6.754 | 9.006 | 95.14 | 96.75 | 97 | 97.49 | 97.37 | 97 | 97.21 | 95.72 | 97.27 | 97.45 | 97.61 | 97.75 | 97.11 | 97.55 | 95.58 | 96.74 | 97.66 | 97.82 | 97.82 | 97.71 | 97.65 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | S6-EH2P9.6K03-SV-YD-L-US {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 9.6471 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 27.1 |  |  | 240 | 370 | 425 | 0.965 | 1.929 | 2.894 | 4.824 | 7.235 | 9.647 | 93.18 | 94.41 | 95.47 | 96 | 95.5 | 95.52 | 95.46 | 93.21 | 94.44 | 95.48 | 96.01 | 95.51 | 95.53 | 95.47 | 92.36 | 94 | 95.48 | 96.01 | 95.54 | 95.59 | 95.43 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH1P9.9K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.9 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.99 | 240 | 97 | CSA Group | [2/23/2024] | CSA Group | [2/23/2024] | [A2] | 2024-05-21 | [2/23/2024] | 2024-05-21 | CSA Group | 2023-12-20 | 2024-05-21 |  | N | N | 16.38 |  |  | 230 | 380 | 450 | 0.999 | 1.998 | 2.997 | 4.995 | 7.493 | 9.99 | 93.57 | 96.11 | 97.39 | 97.27 | 97.33 | 97.21 | 97.11 | 93.52 | 95.74 | 97.27 | 97.32 | 97.21 | 97.39 | 97.03 | 92.78 | 95.46 | 97.38 | 97.33 | 97.28 | 97.6 | 97.05 | 2024-05-21 | 2025-06-11
Ginlong Technologies Co., Ltd. | Solis-1P10K-4G-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 10 | 240 | 97.5 | CSA Group | [10/15/2022] | Intertek | [06/30/2019] | [08_01] | 2018-10-15 | [06/30/2019] | 2020-09-01 | CSA Group | 2020-07-20 | 2020-09-01 |  | N | N | 7 |  |  | 250 | 380 | 500 | 1 | 2 | 3 | 5 | 7.5 | 10 | 95.2 | 96.8 | 97.1 | 97.5 | 97.6 | 97.1 | 97.4 | 95.3 | 96.3 | 97.6 | 97.7 | 97.7 | 97.2 | 97.5 | 95.6 | 96.8 | 97.7 | 97.8 | 97.8 | 97.7 | 97.6 | 2017-10-16 | 2023-02-01
Ginlong Technologies Co., Ltd. | S6-EH1P10K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 10.001 | 240 | 97 | CSA Group | [2/23/2024] | CSA Group | [8/5/2023] | [A2] | 2023-04-14 | [1/13/2023] | 2023-04-21 | CSA Group | 2023-04-19 | 2023-04-14 |  | N | N | 16.38 |  |  | 230 | 380 | 450 | 1 | 2 | 3 | 5 | 7.501 | 10.001 | 93.57 | 96.11 | 97.39 | 97.27 | 97.33 | 97.21 | 97.11 | 93.52 | 95.74 | 97.27 | 97.32 | 97.21 | 97.39 | 97.03 | 92.78 | 95.46 | 97.38 | 97.33 | 97.28 | 97.6 | 97.05 | 2023-04-14 | 2025-06-11
Ginlong Technologies Co., Ltd. | RHI-1P10K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 10.005 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 230 | 330 | 450 | 1 | 2.001 | 3.001 | 5.002 | 7.504 | 10.005 | 95.18 | 96.78 | 97.08 | 97.55 | 97.61 | 97.06 | 97.37 | 95.3 | 96.32 | 97.58 | 97.66 | 97.73 | 97.21 | 97.5 | 95.6 | 96.8 | 97.68 | 97.79 | 97.81 | 97.71 | 97.65 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | S6-EH1P11.4K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.406 | 240 | 97 | CSA Group | [2/23/2024] | CSA Group | [8/5/2023] | [A2] | 2023-04-14 | [1/13/2023] | 2023-04-21 | CSA Group | 2023-04-19 | 2023-04-14 |  | N | N | 15.36 |  |  | 245 | 380 | 450 | 1.141 | 2.281 | 3.422 | 5.703 | 8.554 | 11.406 | 94.77 | 96.19 | 97.09 | 97.38 | 97.26 | 97.27 | 97.11 | 95.99 | 96.88 | 96.88 | 97.03 | 97.23 | 97.34 | 97.08 | 95.55 | 96.65 | 97.05 | 97.18 | 97.22 | 97.57 | 97.11 | 2023-04-14 | 2025-06-11
Ginlong Technologies Co., Ltd. | S6-EH2P11.4K03-SV-YD-L-US {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 11.41 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 26.79 |  |  | 160 | 380 | 450 | 1.141 | 2.282 | 3.423 | 5.705 | 8.557 | 11.41 | 92.32 | 93.96 | 95.46 | 96.01 | 95.53 | 95.58 | 95.42 | 93.44 | 94.45 | 95.44 | 96.01 | 95.54 | 95.53 | 95.49 | 93.46 | 94.48 | 95.45 | 96.01 | 95.52 | 95.54 | 95.48 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH2P12K03-SV-YD-L-US-E {240V} | Y | Y | N | N | N | N | Y* | Y | 11.9 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 11.939 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 26.72 |  |  | 160 | 380 | 450 | 1.194 | 2.388 | 3.582 | 5.97 | 8.954 | 11.939 | 93.17 | 93.91 | 95.49 | 96.01 | 95.48 | 95.59 | 95.42 | 93.58 | 94.37 | 95.27 | 96.02 | 95.52 | 95.58 | 95.47 | 93.32 | 94.31 | 95.48 | 96.01 | 95.51 | 95.51 | 95.46 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH2P12K03-SV-YD-L-US {240V} | Y | Y | N | N | N | N | Y* | Y | 11.9 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 11.94 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 27.02 |  |  | 160 | 380 | 450 | 1.194 | 2.388 | 3.582 | 5.97 | 8.955 | 11.94 | 92.21 | 93.23 | 95.54 | 96.02 | 95.56 | 95.57 | 95.4 | 93.54 | 94.56 | 95.45 | 96.02 | 95.52 | 95.53 | 95.49 | 93.5 | 94.52 | 95.43 | 96.01 | 95.53 | 95.55 | 95.49 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH2P14K03-SV-YD-L-US {240V} | Y | Y | N | N | N | N | Y* | Y | 13.9 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 13.96 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 26.98 |  |  | 186 | 380 | 450 | 1.396 | 2.792 | 4.188 | 6.98 | 10.47 | 13.96 | 92.12 | 93.89 | 95.24 | 96.02 | 95.57 | 95.6 | 95.4 | 93.45 | 94.5 | 95.54 | 96.02 | 95.57 | 95.53 | 95.52 | 93.55 | 94.45 | 95.52 | 96.02 | 95.55 | 95.57 | 95.51 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH2P16K03-SV-YD-L-US {240V} | Y | Y | N | N | N | N | Y* | Y | 15.9 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 15.911 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 27.07 |  |  | 186 | 380 | 450 | 1.591 | 3.182 | 4.773 | 7.955 | 11.933 | 15.911 | 92.15 | 94.13 | 95.17 | 95.99 | 95.51 | 95.53 | 95.37 | 93.9 | 95.25 | 95.35 | 96 | 95.47 | 95.53 | 95.5 | 93.98 | 95.26 | 95.47 | 96 | 95.45 | 95.5 | 95.5 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH2P16K03-SV-YD-L-US-E {240V} | Y | Y | N | N | N | N | Y* | Y | 15.9 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 15.94 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 23.07 |  |  | 186 | 380 | 450 | 1.594 | 3.188 | 4.782 | 7.97 | 11.955 | 15.94 | 92.21 | 93.89 | 95.52 | 96.01 | 95.58 | 95.6 | 95.45 | 93.27 | 94.3 | 95.48 | 96.02 | 95.51 | 95.53 | 95.47 | 93.28 | 94.31 | 95.52 | 96 | 95.57 | 95.58 | 95.5 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-GC25K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 25 kW, 480 Vac Grid Support Utility Interactive Inverter | 24.8876 | 480 | 98.5 | CSA Group | [9/15/2023] | CSA Group | [9/15/2023] | [A2] | 2023-12-11 | [9/15/2023] | 2023-12-11 | CSA Group | 2023-08-25 | 2023-12-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 2.4888 | 4.9775 | 7.4663 | 12.4438 | 18.6657 | 24.8876 | 98.3085 | 98.5231 | 98.5821 | 98.598 | 98.4828 | 98.3112 | 98.5053 | 98.2835 | 98.5436 | 98.6114 | 98.5806 | 98.5088 | 98.4295 | 98.525 | 98.3192 | 98.4885 | 98.5276 | 98.5312 | 98.4377 | 98.377 | 98.4629 | 2023-12-11
Ginlong Technologies Co., Ltd. | Solis-25K-US-LSW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 25 kW, 480 Vac Grid Support Utility Interactive Inverter | 24.958 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [10/30/2019] | [1D] | 2020-09-11 | [10/30/2019] | 2020-09-11 | CSA Group | 2020-07-20 | 2020-09-11 |  | N | N | 1 |  |  | 347 | 470 | 800 | 2.4958 | 4.9916 | 7.4874 | 12.479 | 18.7185 | 24.9581 | 97.8538 | 98.3868 | 98.42 | 98.5665 | 98.4105 | 98.354 | 98.4181 | 98.0001 | 98.4275 | 98.4174 | 98.6659 | 98.423 | 98.3476 | 98.4529 | 97.893 | 98.4187 | 98.493 | 98.685 | 98.4659 | 98.373 | 98.4852 | 2020-09-11
Ginlong Technologies Co., Ltd. | Solis-25K-US {480V} | N | N | Y | Y | Y | N | N | N | 25 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 25 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [01/29/2018] | [1D] | 2018-10-15 | [01/29/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 14 |  |  | 580 | 650 | 780 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 97.1 | 97.4 | 97.6 | 97.9 | 98 | 97.8 | 97.9 | 97.1 | 97.3 | 97.6 | 97.8 | 98.3 | 97.6 | 98 | 97.2 | 97.4 | 97.7 | 97.8 | 98 | 97.5 | 97.9 | 2018-02-15 | 2019-11-15
Ginlong Technologies Co., Ltd. | Solis-25K-US-SW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 25 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box | 25 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [12/21/2018] | [1D] | 2019-03-01 | [12/21/2018] | 2020-08-21 | CSA Group | 2020-07-20 | 2020-08-21 |  | N | N | 14 |  |  | 580 | 650 | 770 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 97.143 | 97.3103 | 97.5582 | 97.902 | 98.1863 | 97.7856 | 97.9456 | 97.1369 | 97.2947 | 97.4013 | 97.8837 | 98.2954 | 97.7509 | 97.978 | 97.2361 | 97.396 | 97.5435 | 97.6922 | 98.0012 | 97.4855 | 97.7947 | 2019-03-01 | 2020-08-21
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-LV-YD-H-US(21A) {208V} | Y | Y | N | N | N | N | Y* |  | 25.88 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality | 25.8835 | 208 | 97 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 57.3 |  |  | 500 | 675 | 850 | 2.5884 | 5.1767 | 7.7651 | 12.9418 | 19.4127 | 25.8835 | 93.9922 | 95.7952 | 96.926 | 96.8916 | 97.1284 | 97.2124 | 96.8665 | 95.8284 | 95.9332 | 96.6126 | 96.9374 | 97.4868 | 97.2454 | 97.1104 | 89.5538 | 94.454 | 95.935 | 96.8496 | 97.2484 | 97.382 | 96.5662 | 2026-03-11
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-LV-YD-H-US {208V} | Y | Y | N | N | N | N | Y* |  | 30 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 25.9 | 208 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 58 |  |  | 360 | 605 | 850 | 2.59 | 5.18 | 7.7699 | 12.9499 | 19.4248 | 25.8998 | 95.778 | 96.9618 | 97.2838 | 97.282 | 97.046 | 96.712 | 97.0525 | 96.054 | 97.146 | 97.5836 | 97.52 | 97.414 | 97.27 | 97.3816 | 95.75 | 97.158 | 97.54 | 97.574 | 97.478 | 97.406 | 97.4169 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-LV-YD-H-US {240V} | Y | Y | N | N | N | N | Y* |  | 30 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 29.705 | 240 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 61 |  |  | 360 | 605 | 850 | 2.971 | 5.941 | 8.912 | 14.853 | 22.279 | 29.705 | 96.02 | 97 | 97.32 | 97.28 | 97.01 | 96.69 | 97.05 | 95.99 | 97.26 | 97.56 | 97.58 | 97.44 | 97.31 | 97.41 | 95.71 | 97.22 | 97.57 | 97.63 | 97.53 | 97.4 | 97.46 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-LV-YD-H-US(21A) {240V} | Y | Y | N | N | N | N | Y* |  | 29.83 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality | 29.8342 | 240 | 97 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 70.7 |  |  | 500 | 675 | 850 | 2.9834 | 5.9668 | 8.9503 | 14.9171 | 22.3756 | 29.8342 | 94.1056 | 95.74 | 95.9364 | 96.9676 | 97.0914 | 97.208 | 96.7456 | 95.8062 | 95.9614 | 96.708 | 96.93 | 97.4686 | 97.4116 | 97.1195 | 89.631 | 95.7398 | 96.8554 | 97.2412 | 97.5684 | 97.5508 | 97.0043 | 2026-03-11
Ginlong Technologies Co., Ltd. | S6-GC30K-LV-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 30 kW, 240 Vac Grid Support Utility Interactive Inverter | 29.8776 | 240 | 97 | CSA Group | [9/15/2023] | CSA Group | [9/15/2023] | [A2] | 2025-08-21 | [9/15/2023] | 2025-08-21 | CSA Group | 2023-08-25 | 2025-08-21 |  | N | N | 1.394 |  |  | 340 | 580 | 680 | 2.9878 | 5.9755 | 8.9633 | 14.9388 | 22.4082 | 29.8776 | 96.2499 | 97.4423 | 97.6992 | 97.5546 | 96.9364 | 96.4715 | 97.1323 | 96.0682 | 97.2327 | 97.5462 | 97.4672 | 96.8476 | 96.4121 | 97.0278 | 96.0928 | 97.0839 | 97.4292 | 97.368 | 96.8105 | 96.369 | 96.9647 | 2025-08-21
Ginlong Technologies Co., Ltd. | S6-GC30K-LV-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 30 kW, 208 Vac Grid Support Utility Interactive Inverter | 29.878 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [9/15/2023] | [A2] | 2023-12-11 | [9/15/2023] | 2023-12-11 | CSA Group | 2023-08-25 | 2023-12-11 |  | N | N | 1.394 |  |  | 340 | 580 | 680 | 2.988 | 5.976 | 8.963 | 14.939 | 22.408 | 29.878 | 96.25 | 97.44 | 97.69 | 97.55 | 96.93 | 96.47 | 97.13 | 96.06 | 97.23 | 97.54 | 97.46 | 96.84 | 96.41 | 97.02 | 96.09 | 97.08 | 97.42 | 97.36 | 96.81 | 96.36 | 96.96 | 2023-12-11
Ginlong Technologies Co., Ltd. | S6-GC30K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac Grid Support Utility Interactive Inverter | 29.883 | 480 | 98.5 | CSA Group | [9/15/2023] | CSA Group | [9/15/2023] | [A2] | 2023-12-11 | [9/15/2023] | 2023-12-11 | CSA Group | 2023-08-25 | 2023-12-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 2.988 | 5.977 | 8.965 | 14.941 | 22.412 | 29.883 | 97.84 | 98.48 | 98.58 | 98.53 | 98.48 | 98.23 | 98.47 | 98.05 | 98.49 | 98.59 | 98.53 | 98.44 | 98.29 | 98.46 | 98 | 98.44 | 98.58 | 98.56 | 98.49 | 98.31 | 98.48 | 2023-12-11
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-NV-YD-H-US(21A) {480V} | Y | Y | N | N | N | N | Y* |  | 29.88 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 29.8847 | 480 | 97 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 54.5 |  |  | 500 | 675 | 850 | 2.9885 | 5.9769 | 8.9654 | 14.9424 | 22.4135 | 29.8847 | 94.0686 | 95.8068 | 96.0994 | 97.282 | 97.2044 | 97.2516 | 96.8951 | 95.8456 | 96.0126 | 96.686 | 97.236 | 97.5746 | 97.4406 | 97.2429 | 89.6642 | 95.7374 | 96.8292 | 97.2394 | 97.57 | 97.6 | 97.0053 | 2026-03-11
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 30 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 29.891 | 480 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 56 |  |  | 360 | 605 | 850 | 2.989 | 5.978 | 8.967 | 14.946 | 22.418 | 29.891 | 95.77 | 97.04 | 97.31 | 97.33 | 97.07 | 96.72 | 97.08 | 95.92 | 96.99 | 97.63 | 97.52 | 97.47 | 97.3 | 97.4 | 95.81 | 96.97 | 97.57 | 97.55 | 97.5 | 97.44 | 97.42 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | Solis-30K-US-LSW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac Grid Support Utility Interactive Inverter | 29.948 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [10/30/2019] | [1D] | 2020-09-11 | [10/30/2019] | 2020-09-11 | CSA Group | 2020-07-20 | 2020-09-11 |  | N | N | 1 |  |  | 417 | 700 | 800 | 2.9948 | 5.9895 | 8.9843 | 14.9738 | 22.4607 | 29.9477 | 97.7689 | 98.392 | 98.4344 | 98.5669 | 98.4121 | 98.3166 | 98.4158 | 97.814 | 98.4242 | 98.504 | 98.651 | 98.42 | 98.356 | 98.4514 | 97.89 | 98.4279 | 98.517 | 98.6982 | 98.451 | 98.365 | 98.4829 | 2020-09-11
Ginlong Technologies Co., Ltd. | Solis-30K-US {480V} | N | N | Y | Y | Y | N | N | N | 30 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 30 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [01/29/2018] | [1D] | 2018-10-15 | [01/29/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 580 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.1 | 97.9 | 97.9 | 98.3 | 97.5 | 97.9 | 97.8 | 97.4 | 98.1 | 98.1 | 98.4 | 98.1 | 97.9 | 98.1 | 97.1 | 97.9 | 98 | 98.3 | 98 | 97.8 | 98 | 2018-02-15 | 2019-11-15
Ginlong Technologies Co., Ltd. | Solis-30K-US-SW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box | 30 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [12/21/2018] | [1D] | 2019-03-02 | [12/21/2018] | 2020-08-21 | CSA Group | 2020-07-20 | 2020-08-21 |  | N | N | 15 |  |  | 580 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.1367 | 97.9124 | 97.905 | 98.3089 | 97.8705 | 97.9174 | 97.9418 | 97.3783 | 98.0388 | 98.0359 | 98.3477 | 98.1139 | 97.915 | 98.1105 | 97.12 | 97.8656 | 97.9617 | 98.2389 | 97.9687 | 97.8103 | 97.9776 | 2019-03-01 | 2020-08-21
Ginlong Technologies Co., Ltd. | S6-GC33K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 33 kW, 480 Vac Grid Support Utility Interactive Inverter | 32.865 | 480 | 98.5 | CSA Group | [9/15/2023] | CSA Group | [9/15/2023] | [A2] | 2023-12-11 | [9/15/2023] | 2023-12-11 | CSA Group | 2023-08-25 | 2023-12-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 3.287 | 6.573 | 9.86 | 16.433 | 24.649 | 32.865 | 98.21 | 98.56 | 98.6 | 98.54 | 98.46 | 98.33 | 98.48 | 98.38 | 98.63 | 98.63 | 98.62 | 98.53 | 98.38 | 98.55 | 98.23 | 98.6 | 98.62 | 98.58 | 98.51 | 98.35 | 98.52 | 2023-12-11
Ginlong Technologies Co., Ltd. | S6-GC36K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac Grid Support Utility Interactive Inverter | 35.866 | 480 | 98.5 | CSA Group | [9/15/2023] | CSA Group | [9/15/2023] | [A2] | 2023-12-11 | [9/15/2023] | 2023-12-11 | CSA Group | 2023-08-25 | 2023-12-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 3.587 | 7.173 | 10.76 | 17.933 | 26.899 | 35.866 | 98.07 | 98.58 | 98.63 | 98.53 | 98.42 | 98.19 | 98.45 | 98.47 | 98.61 | 98.67 | 98.62 | 98.5 | 98.28 | 98.54 | 98.18 | 98.54 | 98.61 | 98.53 | 98.46 | 98.12 | 98.47 | 2023-12-11
Ginlong Technologies Co., Ltd. | Solis-36K-US-LSW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac Grid Support Utility Interactive Inverter | 35.925 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [10/30/2019] | [1D] | 2020-09-11 | [10/30/2019] | 2020-09-11 | CSA Group | 2020-07-20 | 2020-09-11 |  | N | N | 1 |  |  | 500 | 700 | 800 | 3.5925 | 7.185 | 10.7775 | 17.9625 | 26.9438 | 35.9251 | 97.7435 | 98.365 | 98.4061 | 98.579 | 98.4309 | 98.3073 | 98.4221 | 97.796 | 98.3474 | 98.465 | 98.636 | 98.468 | 98.334 | 98.4633 | 97.826 | 98.4038 | 98.496 | 98.6621 | 98.483 | 98.319 | 98.4837 | 2020-09-11
Ginlong Technologies Co., Ltd. | Solis-36K-US {480V} | N | N | Y | Y | Y | N | N | N | 36 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 36 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [01/29/2018] | [1D] | 2018-10-15 | [01/29/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 580 | 650 | 780 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3 | 98.2 | 98.1 | 98.4 | 97.6 | 98.1 | 97.9 | 97.7 | 98.3 | 98.3 | 98.4 | 98.3 | 98.1 | 98.3 | 97.4 | 98.1 | 98.2 | 98.3 | 98.2 | 98.1 | 98.2 | 2018-02-15 | 2019-11-15
Ginlong Technologies Co., Ltd. | Solis-36K-US-F-SW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box and external Fan | 36 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [12/21/2018] | [1D] | 2019-03-01 | [12/21/2018] | 2020-08-21 | CSA Group | 2020-07-20 | 2020-08-21 |  | N | N | 15 |  |  | 580 | 650 | 780 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3526 | 98.1527 | 98.1207 | 98.3457 | 98.0251 | 98.1578 | 98.09 | 97.6373 | 98.3239 | 98.2591 | 98.4238 | 98.3573 | 98.1446 | 98.3184 | 97.3742 | 98.154 | 98.2089 | 98.3757 | 98.1704 | 98.0833 | 98.1811 | 2019-03-01 | 2020-08-21
Ginlong Technologies Co., Ltd. | Solis-36K-US-SW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box | 36 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [12/21/2018] | [1D] | 2019-03-01 | [12/21/2018] | 2020-08-21 | CSA Group | 2020-07-20 | 2020-08-21 |  | N | N | 15 |  |  | 580 | 650 | 780 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3556 | 98.1469 | 98.1132 | 98.3457 | 98.0215 | 98.1483 | 98.0865 | 97.6545 | 98.3164 | 98.2591 | 98.438 | 98.343 | 98.1379 | 98.3138 | 97.3624 | 98.154 | 98.2138 | 98.3749 | 98.1715 | 98.0758 | 98.1813 | 2019-03-01 | 2020-08-21
Ginlong Technologies Co., Ltd. | S6-EH3P40K04-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 40 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 39.8029 | 480 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 57 |  |  | 360 | 605 | 850 | 3.9803 | 7.9606 | 11.9409 | 19.9015 | 29.8522 | 39.8029 | 95.9044 | 96.9128 | 97.332 | 97.2852 | 97.0552 | 96.724 | 97.067 | 95.986 | 97.1218 | 97.5562 | 97.5342 | 97.4136 | 97.367 | 97.382 | 95.72 | 97.18 | 97.56 | 97.5722 | 97.5 | 97.4684 | 97.4336 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | S6-GC40K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 40 kW, 480 Vac Grid Support Utility Interactive Inverter | 39.841 | 480 | 98.5 | CSA Group | [9/15/2023] | CSA Group | [9/15/2023] | [A2] | 2023-12-11 | [9/15/2023] | 2023-12-11 | CSA Group | 2023-08-25 | 2023-12-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 3.984 | 7.968 | 11.952 | 19.92 | 29.88 | 39.841 | 97.47 | 98.22 | 98.59 | 98.59 | 98.58 | 98.15 | 98.5 | 98.08 | 98.33 | 98.61 | 98.55 | 98.53 | 97.96 | 98.48 | 97.93 | 98.3 | 98.55 | 98.59 | 98.54 | 97.84 | 98.48 | 2023-12-11
Ginlong Technologies Co., Ltd. | S6-EH3P40K04-NV-YD-H-US(21A) {480V} | Y | Y | N | N | N | N | Y* |  | 39.84kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 39.844 | 480 | 97 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 70 |  |  | 500 | 675 | 850 | 3.9844 | 7.9688 | 11.9532 | 19.922 | 29.883 | 39.844 | 94.1092 | 95.8522 | 97.0008 | 97.3276 | 97.3346 | 97.4462 | 97.0955 | 96.0928 | 96.5924 | 96.914 | 97.447 | 97.4484 | 97.357 | 97.2824 | 94.472 | 96.3238 | 97.1636 | 97.5694 | 97.6026 | 97.3274 | 97.34 | 2026-03-11
Ginlong Technologies Co., Ltd. | Solis-40K-US-LSW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 40 kW, 480 Vac Grid Support Utility Interactive Inverter | 39.926 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [10/30/2019] | [1D] | 2020-09-11 | [10/30/2019] | 2020-09-11 | CSA Group | 2020-07-20 | 2020-09-11 |  | N | N | 1 |  |  | 556 | 700 | 800 | 3.9926 | 7.9852 | 11.9778 | 19.9629 | 29.9444 | 39.9259 | 97.7566 | 98.3499 | 98.431 | 98.5651 | 98.4319 | 98.3273 | 98.4234 | 97.787 | 98.3669 | 98.459 | 98.628 | 98.441 | 98.347 | 98.4479 | 97.832 | 98.4148 | 98.466 | 98.635 | 98.515 | 98.336 | 98.493 | 2020-09-11
Ginlong Technologies Co., Ltd. | Solis-40K-US {480V} | N | N | Y | Y | Y | N | N | N | 40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 40 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/29/2018] | [1D] | 2018-10-15 | [01/29/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 98 | 98.1 | 97.9 | 98.3 | 98.4 | 98.7 | 98.6 | 98.3 | 98.5 | 97.6 | 98.2 | 98.2 | 98.4 | 98.3 | 98.2 | 98.3 | 2018-02-15 | 2019-11-15
Ginlong Technologies Co., Ltd. | Solis-40K-US-F {480V} | N | N | Y | Y | Y | N | N | N | 40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter with external Fan | 40 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [01/29/2018] | [1D] | 2018-10-15 | [01/29/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 97.7 | 98.1 | 97.8 | 98.3 | 98.4 | 98.6 | 98.5 | 98.3 | 98.5 | 97.6 | 98.1 | 98.2 | 98.4 | 98.3 | 98 | 98.3 | 2018-02-15 | 2019-11-15
Ginlong Technologies Co., Ltd. | Solis-40K-US-F-SW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box and external Fan | 40 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/21/2018] | [1D] | 2019-03-02 | [12/21/2018] | 2020-08-21 | CSA Group | 2020-07-20 | 2020-08-21 |  | N | N | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.47 | 98.0068 | 98.0574 | 98.1972 | 98.114 | 98.0292 | 98.0893 | 97.9259 | 98.3089 | 98.392 | 98.7145 | 98.5725 | 98.3423 | 98.5301 | 97.5823 | 98.1565 | 98.1932 | 98.4353 | 98.3489 | 98.2444 | 98.3028 | 2019-03-01 | 2020-08-21
Ginlong Technologies Co., Ltd. | Solis-40K-US-SW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with seperable wiring box | 40 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/21/2018] | [1D] | 2019-03-02 | [12/21/2018] | 2020-08-21 | CSA Group | 2020-07-20 | 2020-08-21 |  | N | N | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.4777 | 98.0039 | 98.0564 | 98.1952 | 98.1258 | 98.0274 | 98.0951 | 97.9247 | 98.3105 | 98.4002 | 98.7211 | 98.5785 | 98.342 | 98.5357 | 97.5764 | 98.1504 | 98.1795 | 98.4337 | 98.3428 | 98.244 | 98.2971 | 2019-03-01 | 2020-08-21
Ginlong Technologies Co., Ltd. | S6-EH3P50K04-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 50 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 49.8003 | 480 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 52 |  |  | 450 | 650 | 850 | 4.98 | 9.9601 | 14.9401 | 24.9001 | 37.3502 | 49.8003 | 95.7862 | 96.9366 | 97.2908 | 97.3016 | 97.0498 | 96.686 | 97.0572 | 96.03 | 97.165 | 97.59 | 97.52 | 97.4236 | 97.3092 | 97.3894 | 95.714 | 97.195 | 97.5476 | 97.5848 | 97.5016 | 97.4614 | 97.4357 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | S6-EH3P50K04-NV-YD-H-US(21A) {480V} | Y | Y | N | N | N | N | Y* |  | 49.80 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 49.8034 | 480 | 97.5 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 76 |  |  | 600 | 725 | 850 | 4.9803 | 9.9607 | 14.941 | 24.9017 | 37.3526 | 49.8034 | 94.4062 | 96.4892 | 97.322 | 97.4496 | 97.3804 | 97.2358 | 97.2172 | 94.4798 | 96.4874 | 97.138 | 97.616 | 97.5676 | 97.5136 | 97.346 | 95.4054 | 96.9518 | 97.2974 | 97.5806 | 97.5812 | 97.4988 | 97.4244 | 2026-03-11
Ginlong Technologies Co., Ltd. | S6-GC50K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter | 49.848 | 480 | 98.5 | CSA Group | [9/15/2023] | CSA Group | [9/15/2023] | [A2] | 2023-12-11 | [9/15/2023] | 2023-12-11 | CSA Group | 2023-08-25 | 2023-12-11 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 4.985 | 9.97 | 14.955 | 24.924 | 37.386 | 49.848 | 97.74 | 98.52 | 98.55 | 98.63 | 98.46 | 98.16 | 98.46 | 97.43 | 98.38 | 98.69 | 98.73 | 98.57 | 98.36 | 98.55 | 97.5 | 98.2 | 98.53 | 98.64 | 98.51 | 98.34 | 98.47 | 2023-12-11
Ginlong Technologies Co., Ltd. | Solis-50K-US-F-LSW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter | 49.916 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [06/17/2020] | [1D] | 2020-09-01 | [06/17/2020] | 2020-09-01 | CSA Group | 2020-07-20 | 2020-09-01 |  | N | N | 1 |  |  | 568 | 720 | 850 | 4.9916 | 9.9832 | 14.9748 | 24.9581 | 37.4371 | 49.9161 | 97.752 | 98.3642 | 98.434 | 98.585 | 98.42 | 98.313 | 98.4215 | 97.791 | 98.3809 | 98.447 | 98.645 | 98.443 | 98.352 | 98.4522 | 97.84 | 98.411 | 98.483 | 98.68 | 98.493 | 98.3201 | 98.4922 | 2020-09-01
Ginlong Technologies Co., Ltd. | Solis-50K-US-LSW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter | 49.984 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [06/17/2020] | [1D] | 2020-09-01 | [06/17/2020] | 2020-09-01 | CSA Group | 2020-07-20 | 2020-09-01 |  | N | N | 1 |  |  | 568 | 720 | 850 | 4.9984 | 9.9967 | 14.9951 | 24.9918 | 37.4877 | 49.9837 | 97.743 | 98.3898 | 98.433 | 98.553 | 98.436 | 98.35 | 98.4259 | 97.794 | 98.358 | 98.449 | 98.655 | 98.437 | 98.31 | 98.4482 | 97.8057 | 98.4135 | 98.478 | 98.721 | 98.474 | 98.359 | 98.4908 | 2020-09-01
Ginlong Technologies Co., Ltd. | Solis-50K-US {480V} | N | N | Y | Y | Y | N | N | N | 50 kW, 480 Vac, Fanless, 3-phase Grid Support Utility Interactive Inverter | 50 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/23/2017] | [19/01] | 2018-10-15 | [12/23/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5 | 98.5 | 98.4 | 98.6 | 98.3 | 98.5 | 98.4 | 97.8 | 98.6 | 98.5 | 98.7 | 98.4 | 98.5 | 98.5 | 98 | 98.7 | 98.8 | 98.8 | 98.6 | 98.5 | 98.6 | 2018-02-01 | 2019-11-15
Ginlong Technologies Co., Ltd. | Solis-50K-US-F {480V} | N | N | Y | Y | Y | N | N | N | 50 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 50 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/23/2017] | [19/01] | 2018-10-15 | [12/23/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.74 | 98.44 | 98.46 | 98.58 | 98.45 | 98.35 | 98.44 | 97.8 | 98.53 | 98.55 | 98.7 | 98.51 | 98.4 | 98.52 | 97.88 | 98.58 | 98.65 | 98.76 | 98.57 | 98.46 | 98.59 | 2018-02-01 | 2019-11-15
Ginlong Technologies Co., Ltd. | Solis-50K-US-F-SW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 50 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/25/2017];[10/30/2019] | [19/01];[1D] | 2018-10-15 | [12/25/2017];[10/30/2019] | 2020-09-01 | CSA Group | 2020-07-15 | 2020-09-01 |  | N | N | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.7362 | 98.4442 | 98.4559 | 98.5822 | 98.45 | 98.3475 | 98.4445 | 97.7983 | 98.5313 | 98.5521 | 98.7004 | 98.5123 | 98.3959 | 98.5232 | 97.8768 | 98.5781 | 98.6506 | 98.7596 | 98.5678 | 98.4644 | 98.5857 | 2018-02-01 | 2020-09-01
Ginlong Technologies Co., Ltd. | Solis-50K-US-SW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac, Fanless, 3-phase Grid Support Utility Interactive Inverter | 50 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/25/2017];[10/30/2019] | [19/01];[1D] | 2018-10-15 | [12/25/2017];[10/30/2019] | 2020-09-01 | CSA Group | 2020-07-15 | 2020-09-01 |  | N | N | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5167 | 98.5279 | 98.441 | 98.5562 | 98.3221 | 98.4464 | 98.3698 | 97.7469 | 98.5505 | 98.5222 | 98.6539 | 98.4338 | 98.4888 | 98.4718 | 97.9805 | 98.7 | 98.8047 | 98.7919 | 98.5679 | 98.5006 | 98.6231 | 2018-02-01 | 2020-09-01
Ginlong Technologies Co., Ltd. | S6-EH3P60K04-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 60 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 59.7098 | 480 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 59 |  |  | 450 | 650 | 850 | 5.971 | 11.942 | 17.9129 | 29.8549 | 44.7823 | 59.7098 | 95.7718 | 96.9604 | 97.2936 | 97.2821 | 97.0418 | 96.7152 | 97.0513 | 96.0116 | 97.1956 | 97.5873 | 97.5413 | 97.4187 | 97.2794 | 97.3903 | 95.7391 | 97.1654 | 97.5485 | 97.6125 | 97.5087 | 97.3907 | 97.4414 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | S6-EH3P60K04-NV-YD-H-US(21A) {480V} | Y | Y | N | N | N | N | Y* |  | 59.76 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 59.763 | 480 | 97.5 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 76 |  |  | 600 | 725 | 850 | 5.976 | 11.953 | 17.929 | 29.882 | 44.822 | 59.763 | 96.01 | 97.2 | 97.59 | 97.54 | 97.42 | 97.28 | 97.39 | 95.84 | 96.83 | 97.37 | 97.65 | 97.49 | 97.31 | 97.4 | 95.74 | 97.17 | 97.55 | 97.61 | 97.51 | 97.39 | 97.44 | 2026-03-11
Ginlong Technologies Co., Ltd. | S6-GC60K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 59.898 | 480 | 98.5 | CSA Group | [9/15/2023] | CSA Group | [9/15/2023] | [A2] | 2023-12-11 | [9/15/2023] | 2023-12-11 | CSA Group | 2023-08-25 | 2023-12-11 |  | N | N | 3.1623 |  |  | 580 | 720 | 850 | 5.99 | 11.98 | 17.969 | 29.949 | 44.923 | 59.898 | 97.76 | 98.42 | 98.58 | 98.57 | 98.47 | 98.17 | 98.46 | 97.62 | 98.48 | 98.69 | 98.71 | 98.58 | 98.38 | 98.56 | 97.48 | 98.31 | 98.5 | 98.63 | 98.49 | 98.22 | 98.46 | 2023-12-11
Ginlong Technologies Co., Ltd. | Solis-60K-US-F-LSW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 59.933 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [06/17/2020] | [1D] | 2020-09-01 | [06/17/2020] | 2020-09-01 | CSA Group | 2020-07-20 | 2020-09-01 |  | N | N | 1 |  |  | 526 | 720 | 850 | 5.9933 | 11.9866 | 17.9798 | 29.9664 | 44.9496 | 59.9328 | 97.739 | 98.411 | 98.444 | 98.579 | 98.412 | 98.28 | 98.4173 | 97.787 | 98.4024 | 98.465 | 98.622 | 98.441 | 98.342 | 98.4489 | 97.809 | 98.434 | 98.522 | 98.689 | 98.48 | 98.326 | 98.4921 | 2020-09-01
Ginlong Technologies Co., Ltd. | S5-GC60K-LV-US {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 60 kW, 208 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 59.996 | 208 | 98 | CSA Group | [10/17/2024] | CSA Group | [10/17/2024] | [1C] | 2024-12-23 | [10/17/2024] | 2024-12-23 | CSA Group | 2024-10-15 | 2024-12-23 |  | N | N | 3.12 |  |  | 400 | 470 | 650 | 6 | 11.999 | 17.999 | 29.998 | 44.997 | 59.996 | 97.75 | 98.27 | 98.42 | 98.44 | 98.26 | 98.11 | 98.29 | 97.79 | 98.4 | 98.52 | 98.39 | 98.31 | 98.2 | 98.33 | 96.84 | 97.54 | 97.83 | 97.83 | 97.73 | 97.47 | 97.7 | 2024-12-23
Ginlong Technologies Co., Ltd. | S5-GC60K-LV-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 60 kW, 240 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 59.996 | 240 | 98 | CSA Group | [10/17/2024] | CSA Group | [10/17/2024] | [1C] | 2025-08-21 | [10/17/2024] | 2025-08-21 | CSA Group | 2024-10-15 | 2025-08-21 |  | N | N | 3.12 |  |  | 400 | 470 | 650 | 6 | 11.999 | 17.999 | 29.998 | 44.997 | 59.996 | 97.75 | 98.27 | 98.42 | 98.44 | 98.26 | 98.12 | 98.29 | 97.81 | 98.41 | 98.6 | 98.44 | 98.25 | 98.25 | 98.32 | 96.84 | 97.54 | 97.83 | 97.84 | 97.73 | 97.48 | 97.71 | 2025-08-21
Ginlong Technologies Co., Ltd. | Solis-60K-US-F {480V} | N | N | Y | Y | Y | N | N | N | 60 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 60 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/23/2017] | [19/01] | 2018-10-15 | [12/23/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 720 | 6 | 12 | 18 | 30 | 45 | 60 | 97.73 | 98.31 | 98.42 | 98.55 | 98.37 | 98.22 | 98.38 | 97.82 | 98.45 | 98.54 | 98.63 | 98.5 | 98.33 | 98.49 | 97.86 | 98.53 | 98.59 | 98.7 | 98.55 | 98.45 | 98.55 | 2018-02-01 | 2019-11-15
Ginlong Technologies Co., Ltd. | Solis-60K-US-F-SW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 60 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 60 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/25/2017];[10/30/2019] | [19/01];[1D] | 2018-10-15 | [12/25/2017];[10/30/2019] | 2020-09-01 | CSA Group | 2020-07-15 | 2020-09-01 |  | N | N | 1 |  |  | 580 | 650 | 720 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7251 | 98.3108 | 98.4189 | 98.5501 | 98.3711 | 98.2238 | 98.3782 | 97.8227 | 98.4496 | 98.5404 | 98.6262 | 98.499 | 98.3294 | 98.4926 | 97.8622 | 98.5252 | 98.5865 | 98.7 | 98.5526 | 98.4499 | 98.5535 | 2018-02-01 | 2020-09-01
Ginlong Technologies Co., Ltd. | Solis-66K-US-F-LSW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 66 kW, 480 Vac Grid Support Utility Interactive Inverter | 65.926 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [06/17/2020] | [1D] | 2020-09-01 | [06/17/2020] | 2020-09-01 | CSA Group | 2020-07-20 | 2020-09-01 |  | N | N | 1 |  |  | 579 | 720 | 850 | 6.5926 | 13.1851 | 19.7777 | 32.9628 | 49.4441 | 65.9255 | 97.752 | 98.351 | 98.413 | 98.588 | 98.42 | 98.31 | 98.4188 | 97.773 | 98.343 | 98.48 | 98.677 | 98.436 | 98.319 | 98.4549 | 97.807 | 98.369 | 98.501 | 98.657 | 98.487 | 98.321 | 98.483 | 2020-09-01
Ginlong Technologies Co., Ltd. | Solis-66K-US-F {480V} | N | N | Y | Y | Y | N | N | N | 66 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 66 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/23/2017] | [19/01] | 2018-10-15 | [12/23/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 580 | 650 | 720 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.57 | 98.38 | 98.48 | 98.56 | 98.42 | 98.31 | 98.42 | 97.74 | 98.5 | 98.55 | 98.7 | 98.5 | 98.39 | 98.51 | 97.77 | 98.67 | 98.65 | 98.77 | 98.56 | 98.49 | 98.58 | 2018-02-01 | 2019-11-15
Ginlong Technologies Co., Ltd. | Solis-66K-US-F-SW {480V} | N | N | Y | Y | Y | Y | Y* | Y | 66 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 66 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/25/2017];[10/30/2019] | [19/01];[1D] | 2018-10-15 | [12/25/2017];[10/30/2019] | 2020-09-01 | CSA Group | 2020-07-15 | 2020-09-01 | No Information Submitted | N | N | 1 |  |  | 580 | 650 | 720 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.5717 | 98.3763 | 98.4763 | 98.5633 | 98.4214 | 98.3118 | 98.416 | 97.7441 | 98.5006 | 98.5537 | 98.7042 | 98.4989 | 98.3902 | 98.513 | 97.7721 | 98.6713 | 98.6538 | 98.7738 | 98.5561 | 98.4918 | 98.5847 | 2018-02-01 | 2020-09-01
Ginlong Technologies Co., Ltd. | S6-EH3P75K10-LV-YD-H-US {208V} | Y | Y | N | N | N | N | Y* |  | 75 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 70.042 | 208 | 96 | CSA Group | [7/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-07-17 |  |  | N | N | 39.56 |  |  | 400 | 650 | 900 | 7.004 | 14.008 | 21.013 | 35.021 | 52.532 | 70.042 | 93.2 | 94.45 | 96 | 96.22 | 96.14 | 95.9 | 95.93 | 93.66 | 96.05 | 96.33 | 96.61 | 96.36 | 95.95 | 96.27 | 93.62 | 95.47 | 96.07 | 96.33 | 96.14 | 95.82 | 96.02 | 2026-09-01 |  | Y | N | N | N | N | N | Y | N | N
Ginlong Technologies Co., Ltd. | S5-GC75K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive Inverter | 74.574 | 480 | 98.5 | CSA Group | [7/18/2022] | CSA Group | [7/18/2022] | [1C] | 2022-12-12 | [7/18/2022] | 2022-12-12 | CSA Group | 2022-10-14 | 2022-12-12 |  | N | N | 2 |  |  | 550 | 730 | 850 | 7.4574 | 14.9148 | 22.3723 | 37.2871 | 55.9306 | 74.5742 | 97.1519 | 97.7396 | 97.9756 | 98.0455 | 97.9997 | 97.7577 | 97.9474 | 98.2493 | 98.6811 | 98.7466 | 98.7034 | 98.5655 | 98.3686 | 98.5995 | 97.9069 | 98.3276 | 97.9953 | 98.5443 | 98.3567 | 98.2661 | 98.3288 | 2022-12-12 | 2023-05-11
Ginlong Technologies Co., Ltd. | S6-EH3P75K10-LV-YD-H-US {240V} | Y | Y | N | N | N | N | Y* |  | 75 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 74.94 | 240 | 96 | CSA Group | [7/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-07-17 |  |  | N | N | 41.25 |  |  | 400 | 650 | 900 | 7.494 | 14.988 | 22.482 | 37.47 | 56.205 | 74.94 | 93.1 | 94.34 | 96.06 | 96.23 | 96.12 | 95.91 | 95.92 | 93.72 | 96.22 | 96.33 | 96.59 | 96.36 | 95.98 | 96.27 | 93.79 | 95.43 | 96.07 | 96.32 | 96.36 | 95.85 | 96.14 | 2026-09-01 |  | Y | N | N | N | N | N | Y | N | N
Ginlong Technologies Co., Ltd. | Solis-75K-5G-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 75 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive Inverter | 75 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [09/03/2020] | [1C] | 2020-10-01 | [09/03/2020] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-10-01 |  | N | N | 1 |  |  | 550 | 720 | 850 | 7.5002 | 15.0005 | 22.5007 | 37.5012 | 56.2517 | 75.0023 | 98.147 | 98.5383 | 98.525 | 98.6238 | 98.3792 | 98.2162 | 98.4386 | 98.1775 | 98.5215 | 98.5439 | 98.6666 | 98.4445 | 98.2384 | 98.4859 | 98.244 | 98.5737 | 99.0148 | 98.6211 | 98.5743 | 98.294 | 98.6098 | 2020-10-01
Ginlong Technologies Co., Ltd. | S5-GC80K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 85 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 79.446 | 480 | 98.5 | CSA Group | [7/18/2022] | CSA Group | [7/18/2022] | [1C] | 2022-12-12 | [7/18/2022] | 2022-12-12 | CSA Group | 2022-10-14 | 2022-12-12 |  | N | N | 2 |  |  | 550 | 730 | 850 | 7.9446 | 15.8892 | 23.8339 | 39.7231 | 59.5846 | 79.4462 | 97.2634 | 97.826 | 98.0173 | 98.037 | 97.8924 | 97.6791 | 97.8986 | 98.3446 | 98.6912 | 98.743 | 98.6499 | 98.4565 | 98.3341 | 98.5326 | 98.0783 | 98.4089 | 98.5773 | 98.5359 | 98.3844 | 98.2002 | 98.4191 | 2022-12-12 | 2023-05-11
Ginlong Technologies Co., Ltd. | Solis-80K-5G-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 85 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 80 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [09/03/2020] | [1C] | 2020-10-01 | [09/03/2020] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-10-01 |  | N | N | 1 |  |  | 550 | 720 | 850 | 8.0003 | 16.0006 | 24.0009 | 40.0015 | 60.0023 | 80.0031 | 98.1441 | 98.5363 | 98.5241 | 98.6265 | 98.3794 | 98.2123 | 98.4387 | 98.1764 | 98.5232 | 98.543 | 98.6654 | 98.4447 | 98.2424 | 98.4859 | 98.2451 | 98.5776 | 99.0149 | 98.6271 | 98.575 | 98.2898 | 98.6114 | 2020-10-01
Ginlong Technologies Co., Ltd. | S5-GC90K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 90 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 89.449 | 480 | 98 | CSA Group | [7/18/2022] | CSA Group | [7/18/2022] | [1C] | 2022-12-12 | [7/18/2022] | 2022-12-12 | CSA Group | 2022-10-14 | 2022-12-12 |  | N | N | 2 |  |  | 550 | 730 | 850 | 8.9449 | 17.8897 | 26.8346 | 44.7243 | 67.0864 | 89.4486 | 97.2768 | 97.7779 | 98.0978 | 98.0182 | 97.7335 | 97.5594 | 97.8123 | 98.4597 | 98.7601 | 98.72 | 98.6416 | 98.4168 | 98.2225 | 98.5096 | 98.1892 | 98.553 | 98.5772 | 98.5212 | 98.2871 | 98.094 | 98.3708 | 2022-12-12 | 2023-05-11
Ginlong Technologies Co., Ltd. | Solis-90K-5G-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 90 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 90 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [09/03/2020] | [1C] | 2020-10-01 | [09/03/2020] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-10-01 |  | N | N | 1 |  |  | 550 | 720 | 850 | 9.0005 | 18.001 | 27.0015 | 45.0024 | 67.5036 | 90.0049 | 98.1425 | 98.5301 | 98.5175 | 98.6202 | 98.382 | 98.2129 | 98.4376 | 98.1677 | 98.5208 | 98.5367 | 98.6571 | 98.4429 | 98.2296 | 98.4814 | 98.24 | 98.5713 | 99.0158 | 98.6197 | 98.5715 | 98.2914 | 98.6076 | 2020-10-01
Ginlong Technologies Co., Ltd. | S5-GC100K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 99.368 | 480 | 98 | CSA Group | [7/18/2022] | CSA Group | [7/18/2022] | [1C] | 2022-12-12 | [7/18/2022] | 2022-12-12 | CSA Group | 2022-10-14 | 2022-12-12 |  | N | N | 2 |  |  | 550 | 730 | 850 | 9.9368 | 19.8736 | 29.8105 | 49.6841 | 74.5262 | 99.3682 | 97.2872 | 97.736 | 97.7798 | 97.8454 | 97.733 | 97.4318 | 97.7295 | 98.5174 | 98.7659 | 98.7368 | 98.6111 | 98.3712 | 98.1531 | 98.4801 | 98.2563 | 98.5521 | 98.5681 | 98.4642 | 98.2153 | 98.045 | 98.3199 | 2022-12-12 | 2023-05-11
Ginlong Technologies Co., Ltd. | S6-EH3P100K10-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 100 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter | 99.945 | 480 | 97.5 | CSA Group | [7/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-07-17 |  |  | N | N | 40.78 |  |  | 550 | 725 | 900 | 9.994 | 19.989 | 29.983 | 49.972 | 74.958 | 99.945 | 95.92 | 96.72 | 97.1 | 97.32 | 97.54 | 97.52 | 97.33 | 94.98 | 96.22 | 96.71 | 96.85 | 97.29 | 97.29 | 96.98 | 95.41 | 96.63 | 97.27 | 97.43 | 97.72 | 97.7 | 97.46 | 2026-09-11 |  | Y | N | N | N | N | N | Y | N | N
Ginlong Technologies Co., Ltd. | Solis-100K-5G-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 100 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [09/03/2020] | [1C] | 2020-10-01 | [09/03/2020] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-10-01 |  | N | N | 1 |  |  | 550 | 720 | 850 | 10.0004 | 20.0008 | 30.0012 | 50.002 | 75.003 | 100.004 | 98.1406 | 98.5261 | 98.5197 | 98.6189 | 98.3796 | 98.2109 | 98.436 | 98.1693 | 98.5244 | 98.5388 | 98.6582 | 98.442 | 98.2301 | 98.4817 | 98.242 | 98.5714 | 99.0139 | 98.6188 | 98.571 | 98.2889 | 98.607 | 2020-10-01
Ginlong Technologies Co., Ltd. | Solis-100K-EHV-5G {600V} | N | N | Y | Y | Y | Y | Y* | Y | 100 kW, 600 Vac, 3-phase Grid Support Utility Interactive Inverter | 100 | 600 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [06/06/2019] | [V08] | 2019-08-15 | [06/06/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-10-01 |  | N | N | 1 |  |  | 860 | 950 | 1250 | 10.0084 | 20.0168 | 30.0251 | 50.0419 | 75.0628 | 100.0838 | 98.9662 | 99.0442 | 98.8859 | 98.9722 | 98.9 | 98.6475 | 98.9107 | 98.5983 | 98.7913 | 98.8721 | 98.8004 | 98.6123 | 98.636 | 98.6925 | 98.2767 | 98.6281 | 98.6406 | 98.6296 | 98.4678 | 98.2644 | 98.5127 | 2019-08-15 | 2020-10-01
Ginlong Technologies Co., Ltd. | S6-EH3P125K10-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 125 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter | 124.925 | 480 | 97.5 | CSA Group | [7/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-07-17 |  |  | N | N | 38.4 |  |  | 600 | 750 | 900 | 12.492 | 24.985 | 37.477 | 62.462 | 93.693 | 124.925 | 95.97 | 96.9 | 97.18 | 97.43 | 97.51 | 97.32 | 97.35 | 94.99 | 96.35 | 96.78 | 97.11 | 97.29 | 97.62 | 97.07 | 95.6 | 96.88 | 97.31 | 97.68 | 97.72 | 97.63 | 97.53 | 2026-09-11 |  | Y | N | N | N | N | N | Y | N | N
Ginlong Technologies Co., Ltd. | S5-GC125K-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 125 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 124.991 | 480 | 98 | CSA Group | [10/17/2024] | CSA Group | [10/17/2024] | [1C] | 2024-12-23 | [10/17/2024] | 2024-12-23 | CSA Group | 2024-10-15 | 2024-12-23 |  | N | N | 3.36 |  |  | 550 | 770 | 850 | 12.499 | 24.998 | 37.497 | 62.495 | 93.743 | 124.991 | 97.71 | 98.28 | 98.47 | 98.4 | 98.35 | 98.2 | 98.34 | 97.86 | 98.34 | 98.8 | 98.72 | 98.58 | 98.33 | 98.58 | 96.84 | 97.6 | 97.97 | 97.88 | 97.67 | 97.4 | 97.7 | 2024-12-23
Ginlong Technologies Co., Ltd. | Solis-125K-EHV-5G {600V} | N | N | Y | Y | Y | Y | Y* | Y | 125 kW, 600 Vac, 3-phase Grid Support Utility Interactive Inverter | 125 | 600 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [06/06/2019] | [V08] | 2019-08-15 | [06/06/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-10-01 |  | N | N | 1 |  |  | 860 | 950 | 1250 | 12.5083 | 25.0165 | 37.5248 | 62.5413 | 93.812 | 125.0827 | 98.9167 | 99.0279 | 98.941 | 98.9462 | 98.8521 | 98.7464 | 98.8886 | 98.5469 | 98.8405 | 98.7722 | 98.8039 | 98.6338 | 98.6288 | 98.6928 | 98.2805 | 98.7 | 98.7947 | 98.6619 | 98.4679 | 98.3006 | 98.5436 | 2019-08-15 | 2020-10-01
Ginlong Technologies Co., Ltd. | Solis-125K1-EHV-5G {600V} | N | N | Y | Y | Y | Y | Y* | Y | 125 kW, 600 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter, Single-Input | 125.083 | 600 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [08/21/2020] | [V08] | 2020-10-01 | [08/21/2020] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-10-01 |  | N | N | 1 |  |  | 860 | 1080 | 1250 | 12.5083 | 25.0165 | 37.5248 | 62.5413 | 93.812 | 125.0827 | 98.2442 | 98.6339 | 98.622 | 98.725 | 98.4773 | 98.3136 | 98.537 | 98.2735 | 98.6299 | 98.6462 | 98.7609 | 98.5469 | 98.336 | 98.5864 | 98.3436 | 98.6734 | 99.1159 | 98.7211 | 98.6759 | 98.3966 | 98.7108 | 2020-10-01
Ginlong Technologies Co., Ltd. | Solis-125K-EHV-5G-US-PLUS {600V} | N | Y | Y | Y | Y | Y | Y* | Y | 125K kW, 600 Vac, Grid Support Utility Interactive Transformerless Inverter | 136.724 | 600 | 98.5 | CSA Group | [8/15/2022] | CSA Group | [8/15/2022] | [V17] | 2023-03-21 | [8/15/2022] | 2023-03-21 | CSA Group | 2022-10-14 | 2023-03-21 |  | N | N | 2 |  |  | 860 | 1180 | 1300 | 13.6724 | 27.3448 | 41.0172 | 68.362 | 102.543 | 136.724 | 97.8422 | 98.2684 | 98.3999 | 98.2835 | 98.4066 | 97.7238 | 98.3163 | 97.9233 | 98.5743 | 98.6 | 98.5323 | 98.4073 | 98.1726 | 98.4339 | 97.7697 | 98.5037 | 98.5618 | 98.5007 | 98.3817 | 98.123 | 98.397 | 2023-03-21
Ginlong Technologies Co., Ltd. | S6-EH3P150K10-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 150 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter | 149.923 | 480 | 97.5 | CSA Group | [7/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-07-17 |  |  | N | N | 43.74 |  |  | 600 | 750 | 900 | 14.992 | 29.985 | 44.977 | 74.961 | 112.442 | 149.923 | 96.95 | 97.16 | 97.74 | 97.53 | 97.41 | 97.25 | 97.44 | 96.34 | 96.72 | 97.12 | 97.27 | 97.3 | 97.79 | 97.23 | 96.85 | 97.29 | 97.42 | 97.71 | 97.7 | 97.59 | 97.61 | 2026-09-11 |  | Y | N | N | N | N | N | Y | N | N
Ginlong Technologies Co., Ltd. | Solis-185K-EHV-5G-US-PLUS {600V} | N | Y | Y | Y | Y | Y | Y* | Y | 185 kW, 600 Vac, Grid Support Utility Interactive Inverter | 172.987 | 600 | 98 | CSA Group | [8/15/2022] | CSA Group | [6/30/2021] | [V17] | 2022-01-11 | [6/30/2021] | 2022-01-11 | CSA Group | 2021-10-21 | 2022-01-11 |  | N | N | 2 |  |  | 860 | 1180 | 1300 | 17.2987 | 34.5975 | 51.8962 | 86.4937 | 129.7406 | 172.9874 | 97.83 | 98.37 | 98.4098 | 98.2565 | 98.0974 | 97.7163 | 98.1522 | 97.901 | 98.575 | 98.672 | 98.529 | 98.3998 | 98.165 | 98.4367 | 97.8814 | 98.4996 | 98.627 | 98.5084 | 98.3616 | 98.1164 | 98.3997 | 2022-01-11 | 2023-01-23
Ginlong Technologies Co., Ltd. | Solis-185K-EHV-5G-US {600V} | N | N | Y | Y | Y | Y | Y* | Y | 185 kW, 600 Vac Grid Support Utility Interactive Inverter | 185.005 | 600 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [11/04/2020] | [V18] | 2021-01-11 | [11/04/2020] | 2021-01-11 | CSA Group | 2020-11-04 | 2021-01-11 |  | N | N | 1 |  |  | 850 | 1080 | 1300 | 18.5005 | 37.0011 | 55.5016 | 92.5026 | 138.7539 | 185.0053 | 97.818 | 98.477 | 98.621 | 98.627 | 98.457 | 98.25 | 98.4775 | 97.932 | 98.566 | 98.654 | 98.582 | 98.404 | 98.181 | 98.4495 | 97.65 | 98.488 | 98.579 | 98.893 | 98.698 | 98.444 | 98.6596 | 2021-01-11
Ginlong Technologies Co., Ltd. | Solis-255K-EHV-5G-US-PLUS {800V} | N | Y | Y | Y | Y | Y | Y* | Y | 255 kW, 800 Vac, Grid Support Utility Interactive Inverter | 238.706 | 800 | 98 | CSA Group | [8/15/2022] | CSA Group | [6/30/2021] | [V17] | 2022-01-11 | [6/30/2021] | 2022-01-11 | CSA Group | 2021-10-21 | 2022-01-11 |  | N | N | 2 |  |  | 860 | 1180 | 1300 | 23.8706 | 47.7412 | 71.6118 | 119.353 | 179.0295 | 238.706 | 95.934 | 96.599 | 97.77 | 97.502 | 97.458 | 97.255 | 97.3906 | 98.406 | 98.834 | 98.91 | 98.793 | 98.682 | 98.49 | 98.7196 | 97.887 | 98.63 | 98.792 | 98.745 | 98.66 | 98.454 | 98.651 | 2022-01-11 | 2023-01-23
Ginlong Technologies Co., Ltd. | S6-GU250K-EHV-US-M12 {600V} | N | Y | N | N | N | N | Y* | Y | 250 kW, 600 Vac Grid Support Utility Interactive Inverter | 248.751 | 600 | 98.5 | CSA Group | [8/19/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-10 | 2025-07-21 |  | N | N | 15.36 |  |  | 860 | 1080 | 1300 | 24.875 | 49.75 | 74.625 | 124.376 | 186.564 | 248.751 | 96.75 | 97.73 | 97.92 | 98.6 | 98.65 | 98.5 | 98.42 | 96.83 | 97.95 | 98.07 | 98.76 | 99.01 | 98.73 | 98.69 | 96.72 | 97.63 | 97.94 | 98.63 | 98.72 | 98.53 | 98.46 | 2025-07-21
Ginlong Technologies Co., Ltd. | Solis-255K-EHV-5G-US {800V} | N | N | Y | Y | Y | Y | Y* | Y | 255 kW, 800 Vac Grid Support Utility Interactive Inverter | 255.013 | 800 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [11/04/2020] | [V18] | 2021-01-11 | [11/04/2020] | 2021-01-11 | CSA Group | 2020-11-04 | 2021-01-11 |  | N | N | 1 |  |  | 850 | 1080 | 1300 | 25.5013 | 51.0025 | 76.5038 | 127.5063 | 191.2595 | 255.0126 | 97.818 | 98.477 | 98.621 | 98.627 | 98.457 | 98.25 | 98.4775 | 97.645 | 98.299 | 98.495 | 98.546 | 98.427 | 98.255 | 98.4139 | 98.059 | 98.701 | 98.84 | 98.835 | 98.696 | 98.521 | 98.7085 | 2021-01-11
Ginlong Technologies Co., Ltd. | S6-GU350K-EHV-US-M12 {800V} | N | Y | Y | Y | Y | Y | Y* | Y | 350 kW, 800Vac Grid Support Utility Interactive Inverter | 348.153 | 800 | 98.5 | CSA Group | [8/19/2024] | CSA Group | [8/19/2024] | [A3] | 2025-02-03 | [8/19/2024] | 2025-02-03 | CSA Group | 2024-09-10 | 2025-02-03 |  | N | N | 15.36 |  |  | 860 | 1080 | 1300 | 34.815 | 69.631 | 104.446 | 174.076 | 261.114 | 348.153 | 96.75 | 97.95 | 98.53 | 98.65 | 98.47 | 98.44 | 98.42 | 96.87 | 98.09 | 98.79 | 99.01 | 98.7 | 98.56 | 98.67 | 96.53 | 97.91 | 98.61 | 98.73 | 98.51 | 98.47 | 98.46 | 2025-02-03
Ginlong Technologies Co., Ltd. | S6-GU350K-EHV-US-M16 {800V} | N | Y | Y | Y | Y | Y | Y* | Y | 350 kW, 800Vac Grid Support Utility Interactive Inverter | 348.488 | 800 | 98.5 | CSA Group | [8/19/2024] | CSA Group | [8/19/2024] | [A3] | 2025-02-03 | [8/19/2024] | 2025-02-03 | CSA Group | 2024-09-10 | 2025-02-03 |  | N | N | 15.36 |  |  | 860 | 1080 | 1300 | 34.849 | 69.698 | 104.546 | 174.244 | 261.366 | 348.488 | 97.27 | 97.94 | 98.55 | 98.65 | 98.48 | 98.43 | 98.45 | 96.85 | 98.08 | 98.8 | 99.02 | 98.71 | 98.57 | 98.67 | 96.53 | 97.92 | 98.63 | 98.72 | 98.51 | 98.47 | 98.46 | 2025-02-03
Global Tech China Ltd. | SSM-6.0-SPHYB-UL {208V} | Y | Y | N | N | N | N | N |  | 6 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 6.124 | 208 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.61237 | 1.2247 | 1.8371 | 3.0618 | 4.6 | 6.1 | 91.5 | 94.4 | 95.4 | 96.1 | 96.2 | 96 | 95.8 | 93.6 | 96 | 96.7 | 97.2 | 97.1 | 97 | 96.9 | 93 | 95.5 | 96.3 | 96.9 | 96.9 | 96.8 | 96.6 | 2025-11-12
Global Tech China Ltd. | SSM-6.0-SPHYB-UL {240V} | Y | Y | N | N | N | N | N |  | 6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 6.149 | 240 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.61493 | 1.2299 | 1.8448 | 3.0747 | 4.6 | 6.1 | 91.6 | 94.4 | 95.5 | 96.3 | 96.4 | 96.4 | 96 | 93.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.4 | 97.2 | 92.7 | 95.4 | 96.4 | 97.1 | 97.3 | 97.3 | 96.9 | 2025-11-12
Global Tech China Ltd. | SSM-7.6-SPHYB-UL {240V} | Y | Y | N | N | N | N | N |  | 7.6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 7.6472 | 240 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.76472 | 1.5294 | 2.2942 | 3.8236 | 5.7 | 7.6 | 93 | 95.6 | 96.2 | 96.7 | 96.5 | 96.2 | 96.3 | 89.7 | 96.1 | 96.8 | 97.2 | 97 | 96.8 | 96.6 | 94.1 | 96.2 | 96.8 | 97.1 | 96.9 | 96.6 | 96.8 | 2025-11-12
Global Tech China Ltd. | SSM-7.6-SPHYB-UL {208V} | Y | Y | N | N | N | N | N |  | 7.6 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 7.648 | 208 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.7 | 7.6 | 92.9 | 95.5 | 96.2 | 96.6 | 96.4 | 96.2 | 96.3 | 93.7 | 96.1 | 96.8 | 97.2 | 97 | 96.8 | 96.8 | 94.1 | 96.2 | 96.8 | 97.1 | 96.9 | 96.7 | 96.8 | 2025-11-12
Global Tech China Ltd. | SSM-11.4-SPHYB-UL {240V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 10.14 | 240 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.6 | 10.2 | 92.9 | 95.5 | 96.1 | 96.6 | 96.4 | 96.1 | 96.2 | 93.7 | 96 | 96.7 | 97.1 | 96.9 | 96.7 | 96.7 | 94.1 | 96.2 | 96.7 | 97 | 96.8 | 96.6 | 96.7 | 2025-11-12
Global Tech China Ltd. | SSM-11.4-SPHYB-UL {208V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 10.186 | 208 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.028 | 3.042 | 5.07 | 7.6 | 10.1 | 93.1 | 95.6 | 96.2 | 96.7 | 96.5 | 96.2 | 96.3 | 93.7 | 96.1 | 96.8 | 97.2 | 97 | 96.8 | 96.8 | 94.1 | 96.3 | 96.8 | 97.1 | 96.9 | 96.7 | 96.8 | 2025-11-12
GoodWe Technologies Co., Ltd. | GEP5.0-1-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 4.333 kW, 208 Vac Grid Support Utility Interactive Inverter | 4.339 | 208 | 96 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 143 | 330 | 500 | 0.43395 | 0.8679 | 1.3018 | 2.1697 | 3.2546 | 4.3395 | 92.0543 | 94.21 | 94.9943 | 95.3743 | 95.2629 | 94.94 | 95.0569 | 94.7286 | 96.3729 | 96.8729 | 97.1357 | 97.11 | 96.98 | 96.9483 | 92.1757 | 95.17 | 96.01 | 96.6029 | 96.7329 | 96.6771 | 96.3556 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW5000-MS-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 4.33 kW, 208 Vac Grid Support Utility Interactive Inverter | 4.339 | 208 | 96 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 143 | 330 | 500 | 0.43395 | 0.8679 | 1.3018 | 2.1697 | 3.2546 | 4.3395 | 92.0543 | 94.21 | 94.9943 | 95.3743 | 95.2629 | 94.94 | 95.0569 | 94.7286 | 96.3729 | 96.8729 | 97.1357 | 97.11 | 96.98 | 96.9483 | 92.1757 | 95.17 | 96.01 | 96.6029 | 96.7329 | 96.6771 | 96.3556 | 2022-12-21
GoodWe Technologies Co., Ltd. | GEP5.0-1-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.968 | 240 | 96.5 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 165 | 380 | 500 | 0.49681 | 0.99362 | 1.4904 | 2.484 | 3.7261 | 4.9681 | 91.9714 | 94.0629 | 95.01 | 95.5371 | 96.0086 | 95.2843 | 95.4948 | 94.4443 | 96.3714 | 96.9971 | 97.3129 | 97.3414 | 97.2371 | 97.1245 | 92.8529 | 95.5986 | 96.4729 | 97.0057 | 97.1257 | 97.0871 | 96.773 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW5000-MS-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.968 | 240 | 96.5 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 165 | 380 | 500 | 0.49681 | 0.99362 | 1.4904 | 2.484 | 3.7261 | 4.9681 | 91.9714 | 94.0629 | 95.01 | 95.5371 | 96.0086 | 95.2843 | 95.4948 | 94.4443 | 96.3714 | 96.9971 | 97.3129 | 97.3414 | 97.2371 | 97.1245 | 92.8529 | 95.5986 | 96.4729 | 97.0057 | 97.1257 | 97.0871 | 96.773 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW5000H-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, Bi-directional Grid Support Utility Interactive PV and Battery Inverter | 4.989 | 240 | 95.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 | Efficiency data includes external Isolation transformer GW5000G-TF effect. | N | N | 47.36 |  |  | 300 | 400 | 480 | 0.499 | 0.998 | 1.497 | 2.495 | 3.742 | 4.989 | 87.29 | 92.59 | 94.36 | 95.51 | 95.76 | 95.68 | 95.04 | 88.08 | 93.35 | 94.82 | 95.82 | 96.09 | 96.05 | 95.42 | 87.62 | 93.17 | 94.65 | 95.74 | 96.09 | 96.02 | 95.36 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEH5.0-1U-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 5.0047 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 235 | 390 | 500 | 0.50047 | 1.0009 | 1.5014 | 2.5023 | 3.7535 | 5.0047 | 93.8586 | 96.2286 | 96.6214 | 97.1629 | 97.0571 | 96.9514 | 96.8524 | 95.3457 | 96.8429 | 97.3786 | 97.6771 | 97.6357 | 97.4343 | 97.4722 | 95.3371 | 96.5929 | 97.0314 | 97.4057 | 97.4243 | 97.2571 | 97.2398 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW5000-ES-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 5.0047 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 235 | 390 | 500 | 0.50047 | 1.0009 | 1.5014 | 2.5023 | 3.7535 | 5.0047 | 93.8586 | 96.2286 | 96.6214 | 97.1629 | 97.0571 | 96.9514 | 96.8524 | 95.3457 | 96.8429 | 97.3786 | 97.6771 | 97.6357 | 97.4343 | 97.4722 | 95.3371 | 96.5929 | 97.0314 | 97.4057 | 97.4243 | 97.2571 | 97.2398 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEH5.0-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 5.0675 | 240 | 97.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 11.24 |  |  | 300 | 400 | 480 | 0.50675 | 1.0135 | 1.5202 | 2.5337 | 3.8006 | 5.0675 | 93.9925 | 96.2316 | 96.8797 | 97.2517 | 97.2643 | 97.1484 | 97.0272 | 94.9307 | 96.9459 | 97.4098 | 97.6103 | 97.5959 | 97.5021 | 97.4328 | 94.8782 | 96.5215 | 97.2181 | 97.7266 | 97.6607 | 97.5509 | 97.4477 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW5000A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 5.0675 | 240 | 97.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 11.24 |  |  | 300 | 400 | 480 | 0.50675 | 1.0135 | 1.5202 | 2.5337 | 3.8006 | 5.0675 | 93.9925 | 96.2316 | 96.8797 | 97.2517 | 97.2643 | 97.1484 | 97.0272 | 94.9307 | 96.9459 | 97.4098 | 97.6103 | 97.5959 | 97.5021 | 97.4328 | 94.8782 | 96.5215 | 97.2181 | 97.7266 | 97.6607 | 97.5509 | 97.4477 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW5000A-MS {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter | 5.0675 | 240 | 97.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 11.24 |  |  | 300 | 400 | 480 | 0.50675 | 1.0135 | 1.5202 | 2.5337 | 3.8006 | 5.0675 | 93.9925 | 96.2316 | 96.8797 | 97.2517 | 97.2643 | 97.1484 | 97.0272 | 94.9307 | 96.9459 | 97.4098 | 97.6103 | 97.5959 | 97.5021 | 97.4328 | 94.8782 | 96.5215 | 97.2181 | 97.7266 | 97.6607 | 97.5509 | 97.4477 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW5000A-MS {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter | 5.133 | 208 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.31 |  |  | 300 | 400 | 480 | 0.5133 | 1.0266 | 1.5399 | 2.5665 | 3.8498 | 5.133 | 94.1098 | 96.0734 | 96.7353 | 97.0147 | 96.9328 | 96.7308 | 96.7603 | 95.0838 | 96.7112 | 97.1772 | 97.3376 | 97.2176 | 97.0668 | 97.1197 | 94.2209 | 96.3752 | 96.9856 | 97.2291 | 97.1353 | 96.9852 | 96.9749 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEP6.0-1-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 5.2 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.208 | 208 | 96 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 171 | 330 | 500 | 0.52083 | 1.0417 | 1.5625 | 2.6041 | 3.9062 | 5.2083 | 92.8971 | 94.7957 | 95.4586 | 95.73 | 95.5586 | 95.1986 | 95.42 | 94.7957 | 96.4271 | 96.8843 | 97.0914 | 97.0029 | 96.8214 | 96.8811 | 93.2071 | 95.5014 | 96.2229 | 96.5943 | 96.6071 | 96.4729 | 96.3603 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW6000-MS-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 5.2 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.208 | 208 | 96 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 171 | 330 | 500 | 0.52083 | 1.0417 | 1.5625 | 2.6041 | 3.9062 | 5.2083 | 92.8971 | 94.7957 | 95.4586 | 95.73 | 95.5586 | 95.1986 | 95.42 | 94.7957 | 96.4271 | 96.8843 | 97.0914 | 97.0029 | 96.8214 | 96.8811 | 93.2071 | 95.5014 | 96.2229 | 96.5943 | 96.6071 | 96.4729 | 96.3603 | 2022-12-21
GoodWe Technologies Co., Ltd. | GEH6.0-1U-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 5.9973 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 285 | 390 | 500 | 0.59973 | 1.1995 | 1.7992 | 2.9987 | 4.498 | 5.9973 | 95.2243 | 95.7757 | 96.4657 | 96.9057 | 96.9414 | 96.8086 | 96.7432 | 95.5114 | 96.5143 | 97.1643 | 97.62 | 97.61 | 97.41 | 97.4099 | 95.26 | 96.0886 | 96.7686 | 97.3786 | 97.3714 | 97.2786 | 97.1473 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW6000-ES-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 5.9973 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 285 | 390 | 500 | 0.59973 | 1.1995 | 1.7992 | 2.9987 | 4.498 | 5.9973 | 95.2243 | 95.7757 | 96.4657 | 96.9057 | 96.9414 | 96.8086 | 96.7432 | 95.5114 | 96.5143 | 97.1643 | 97.62 | 97.61 | 97.41 | 97.4099 | 95.26 | 96.0886 | 96.7686 | 97.3786 | 97.3714 | 97.2786 | 97.1473 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEP6.0-1-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.998 | 240 | 96.5 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 198 | 380 | 500 | 0.59981 | 1.1996 | 1.7994 | 2.999 | 4.4986 | 5.9981 | 93.36 | 94.9529 | 95.6429 | 95.98 | 95.88 | 95.5971 | 95.7112 | 95.5114 | 96.9014 | 97.2843 | 97.4414 | 97.3443 | 97.17 | 97.2533 | 94.72 | 96.4129 | 96.94 | 97.1886 | 97.1471 | 96.9743 | 96.9885 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW6000-MS-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.998 | 240 | 96.5 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 198 | 380 | 500 | 0.59981 | 1.1996 | 1.7994 | 2.999 | 4.4986 | 5.9981 | 93.36 | 94.9529 | 95.6429 | 95.98 | 95.88 | 95.5971 | 95.7112 | 95.5114 | 96.9014 | 97.2843 | 97.4414 | 97.3443 | 97.17 | 97.2533 | 94.72 | 96.4129 | 96.94 | 97.1886 | 97.1471 | 96.9743 | 96.9885 | 2022-12-21
GoodWe Technologies Co., Ltd. | GEH6.0-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 6.109 | 240 | 97.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.3 |  |  | 360 | 400 | 480 | 0.6109 | 1.2218 | 1.8327 | 3.0545 | 4.5817 | 6.109 | 95.1428 | 96.9138 | 97.2751 | 97.4472 | 97.3624 | 97.1646 | 97.2486 | 95.6917 | 97.2031 | 97.5713 | 97.6709 | 97.5587 | 97.3756 | 97.4822 | 95.3048 | 96.9647 | 97.385 | 97.593 | 97.4861 | 97.3196 | 97.3748 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW6000A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 6.109 | 240 | 97.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.3 |  |  | 360 | 400 | 480 | 0.6109 | 1.2218 | 1.8327 | 3.0545 | 4.5817 | 6.109 | 95.1428 | 96.9138 | 97.2751 | 97.4472 | 97.3624 | 97.1646 | 97.2486 | 95.6917 | 97.2031 | 97.5713 | 97.6709 | 97.5587 | 97.3756 | 97.4822 | 95.3048 | 96.9647 | 97.385 | 97.593 | 97.4861 | 97.3196 | 97.3748 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW6000A-MS {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter | 6.109 | 240 | 97.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.3 |  |  | 360 | 400 | 480 | 0.6109 | 1.2218 | 1.8327 | 3.0545 | 4.5817 | 6.109 | 95.1428 | 96.9138 | 97.2751 | 97.4472 | 97.3624 | 97.1646 | 97.2486 | 95.6917 | 97.2031 | 97.5713 | 97.6709 | 97.5587 | 97.3756 | 97.4822 | 95.3048 | 96.9647 | 97.385 | 97.593 | 97.4861 | 97.3196 | 97.3748 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW6000A-MS {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter | 6.138 | 208 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 11.5 |  |  | 360 | 400 | 480 | 0.6138 | 1.2276 | 1.8414 | 3.069 | 4.6035 | 6.138 | 95.1243 | 96.7475 | 97.0778 | 97.1859 | 96.9518 | 96.6585 | 96.9181 | 95.4926 | 96.9805 | 97.2832 | 97.3147 | 97.0895 | 96.7862 | 97.0756 | 95.1308 | 96.7711 | 97.1405 | 97.3004 | 97.0383 | 96.7392 | 97.001 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEP7.6-1-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 6.58 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.589 | 208 | 96.5 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 217 | 330 | 500 | 0.65888 | 1.3178 | 1.9767 | 3.2944 | 4.9416 | 6.5888 | 93.8986 | 95.5171 | 95.97 | 96.0643 | 96.1771 | 95.3957 | 95.9654 | 95.8471 | 96.9371 | 97.1529 | 97.1429 | 96.9 | 96.6014 | 96.9262 | 94.7386 | 96.2457 | 96.6357 | 96.7714 | 96.6029 | 96.3229 | 96.5358 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW7600-MS-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 6.58 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.589 | 208 | 96.5 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 217 | 330 | 500 | 0.65888 | 1.3178 | 1.9767 | 3.2944 | 4.9416 | 6.5888 | 93.8986 | 95.5171 | 95.97 | 96.0643 | 96.1771 | 95.3957 | 95.9654 | 95.8471 | 96.9371 | 97.1529 | 97.1429 | 96.9 | 96.6014 | 96.9262 | 94.7386 | 96.2457 | 96.6357 | 96.7714 | 96.6029 | 96.3229 | 96.5358 | 2022-12-21
GoodWe Technologies Co., Ltd. | GEP7.7-1-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 6.65 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.63 | 208 | 97 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 150 | 330 | 500 | 0.66297 | 1.3259 | 1.9889 | 3.3148 | 4.9723 | 6.6297 | 94.0729 | 95.6086 | 95.99 | 95.8357 | 95.6271 | 95.5329 | 95.6467 | 97.4 | 97.7114 | 97.7657 | 97.63 | 97.4386 | 97.0057 | 97.5085 | 96.5271 | 97.0129 | 97.5914 | 97.34 | 97.1886 | 97.25 | 97.2365 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW7700-MS-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 6.65 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.63 | 208 | 97 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 150 | 330 | 500 | 0.66297 | 1.3259 | 1.9889 | 3.3148 | 4.9723 | 6.6297 | 94.0729 | 95.6086 | 95.99 | 95.8357 | 95.6271 | 95.5329 | 95.6467 | 97.4 | 97.7114 | 97.7657 | 97.63 | 97.4386 | 97.0057 | 97.5085 | 96.5271 | 97.0129 | 97.5914 | 97.34 | 97.1886 | 97.25 | 97.2365 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW7000A-MS {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter | 7.007 | 208 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.34 |  |  | 210 | 400 | 480 | 0.7007 | 1.4014 | 2.1021 | 3.5035 | 5.2553 | 7.007 | 94.2187 | 95.7079 | 96.1084 | 96.2315 | 95.9417 | 95.6578 | 95.9277 | 95.7596 | 96.9959 | 97.2728 | 97.3125 | 97.1223 | 96.8193 | 97.1043 | 95.1508 | 96.6691 | 97.0496 | 97.1497 | 96.9746 | 96.6823 | 96.9175 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEH7.0-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.057 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.48 |  |  | 210 | 400 | 480 | 0.7057 | 1.4114 | 2.1171 | 3.5285 | 5.2927 | 7.057 | 94.3693 | 95.9144 | 96.3821 | 96.5425 | 96.3948 | 96.1519 | 96.3071 | 95.9384 | 97.2694 | 97.5935 | 97.666 | 97.5651 | 97.3232 | 97.4978 | 95.3006 | 96.8755 | 97.3229 | 97.7033 | 97.5711 | 97.3319 | 97.4315 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW7000A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.057 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.48 |  |  | 210 | 400 | 480 | 0.7057 | 1.4114 | 2.1171 | 3.5285 | 5.2927 | 7.057 | 94.3693 | 95.9144 | 96.3821 | 96.5425 | 96.3948 | 96.1519 | 96.3071 | 95.9384 | 97.2694 | 97.5935 | 97.666 | 97.5651 | 97.3232 | 97.4978 | 95.3006 | 96.8755 | 97.3229 | 97.7033 | 97.5711 | 97.3319 | 97.4315 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW7000A-MS {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter | 7.057 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.48 |  |  | 210 | 400 | 480 | 0.7057 | 1.4114 | 2.1171 | 3.5285 | 5.2927 | 7.057 | 94.3693 | 95.9144 | 96.3821 | 96.5425 | 96.3948 | 96.1519 | 96.3071 | 95.9384 | 97.2694 | 97.5935 | 97.666 | 97.5651 | 97.3232 | 97.4978 | 95.3006 | 96.8755 | 97.3229 | 97.7033 | 97.5711 | 97.3319 | 97.4315 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEH7.6-1U-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 7.5882 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 180 | 390 | 500 | 0.75882 | 1.5176 | 2.2765 | 3.7941 | 5.6911 | 7.5882 | 94.8629 | 96.1257 | 96.6114 | 96.8586 | 96.7071 | 96.0729 | 96.5929 | 95.9643 | 97.0057 | 97.6957 | 97.6157 | 97.45 | 97.29 | 97.4246 | 95.6529 | 96.9743 | 97.35 | 97.3486 | 97.2 | 96.8929 | 97.1607 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW7600-ES-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 7.5882 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 180 | 390 | 500 | 0.75882 | 1.5176 | 2.2765 | 3.7941 | 5.6911 | 7.5882 | 94.8629 | 96.1257 | 96.6114 | 96.8586 | 96.7071 | 96.0729 | 96.5929 | 95.9643 | 97.0057 | 97.6957 | 97.6157 | 97.45 | 97.29 | 97.4246 | 95.6529 | 96.9743 | 97.35 | 97.3486 | 97.2 | 96.8929 | 97.1607 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEP7.6-1-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.589 | 240 | 97 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 250 | 380 | 500 | 0.7589 | 1.5178 | 2.2767 | 3.7945 | 5.6917 | 7.589 | 94.2671 | 95.6814 | 96.1771 | 96.3357 | 96.1329 | 95.7814 | 96.066 | 95.8886 | 97.0914 | 97.3457 | 97.3814 | 97.18 | 96.9229 | 97.1732 | 95.4857 | 96.9543 | 97.2729 | 97.2286 | 97.0771 | 96.7571 | 97.0466 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW7600-MS-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.589 | 240 | 97 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 250 | 380 | 500 | 0.7589 | 1.5178 | 2.2767 | 3.7945 | 5.6917 | 7.589 | 94.2671 | 95.6814 | 96.1771 | 96.3357 | 96.1329 | 95.7814 | 96.066 | 95.8886 | 97.0914 | 97.3457 | 97.3814 | 97.18 | 96.9229 | 97.1732 | 95.4857 | 96.9543 | 97.2729 | 97.2286 | 97.0771 | 96.7571 | 97.0466 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW7600A-MS {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter | 7.61 | 208 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.58 |  |  | 230 | 400 | 480 | 0.761 | 1.522 | 2.283 | 3.805 | 5.7075 | 7.61 | 94.5466 | 95.9281 | 96.2648 | 96.3508 | 96.0423 | 95.6545 | 96.0489 | 95.9428 | 97.0933 | 97.3304 | 97.3007 | 97.0466 | 96.6994 | 97.0749 | 95.3873 | 96.7795 | 97.0987 | 97.1136 | 96.8863 | 96.5432 | 96.877 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEH7.6-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.644 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.44 |  |  | 230 | 400 | 480 | 0.7644 | 1.5288 | 2.2932 | 3.822 | 5.733 | 7.644 | 94.8643 | 96.15 | 96.5255 | 96.6841 | 96.4443 | 96.1981 | 96.4142 | 96.2197 | 97.3623 | 97.6532 | 97.6811 | 97.5297 | 97.2607 | 97.5021 | 95.6202 | 97.0112 | 97.3977 | 97.5881 | 97.4473 | 97.198 | 97.3636 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW7600A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.644 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.44 |  |  | 230 | 400 | 480 | 0.7644 | 1.5288 | 2.2932 | 3.822 | 5.733 | 7.644 | 94.8643 | 96.15 | 96.5255 | 96.6841 | 96.4443 | 96.1981 | 96.4142 | 96.2197 | 97.3623 | 97.6532 | 97.6811 | 97.5297 | 97.2607 | 97.5021 | 95.6202 | 97.0112 | 97.3977 | 97.5881 | 97.4473 | 97.198 | 97.3636 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW7600A-MS {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter | 7.644 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.44 |  |  | 230 | 400 | 480 | 0.7644 | 1.5288 | 2.2932 | 3.822 | 5.733 | 7.644 | 94.8643 | 96.15 | 96.5255 | 96.6841 | 96.4443 | 96.1981 | 96.4142 | 96.2197 | 97.3623 | 97.6532 | 97.6811 | 97.5297 | 97.2607 | 97.5021 | 95.6202 | 97.0112 | 97.3977 | 97.5881 | 97.4473 | 97.198 | 97.3636 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEP7.7-1-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 7.68 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.678 | 240 | 97 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 170 | 380 | 500 | 0.76784 | 1.5357 | 2.3035 | 3.8392 | 5.7588 | 7.6784 | 93.62 | 95.45 | 95.8857 | 96.03 | 95.8829 | 95.8743 | 95.8015 | 96.35 | 97.4386 | 97.6586 | 97.7457 | 97.6543 | 97.5286 | 97.6048 | 94.9686 | 97.0729 | 97.37 | 97.4486 | 97.41 | 97.3114 | 97.2939 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW7700-MS-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 7.68 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.678 | 240 | 97 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 170 | 380 | 500 | 0.76784 | 1.5357 | 2.3035 | 3.8392 | 5.7588 | 7.6784 | 93.62 | 95.45 | 95.8857 | 96.03 | 95.8829 | 95.8743 | 95.8015 | 96.35 | 97.4386 | 97.6586 | 97.7457 | 97.6543 | 97.5286 | 97.6048 | 94.9686 | 97.0729 | 97.37 | 97.4486 | 97.41 | 97.3114 | 97.2939 | 2022-12-21
GoodWe Technologies Co., Ltd. | GEP9.6-1-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 8.32 kW, 208 Vac Grid Support Utility Interactive Inverter | 8.301 | 208 | 96.5 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 182 | 330 | 500 | 0.83015 | 1.6603 | 2.4904 | 4.1507 | 6.2261 | 8.3015 | 94.1286 | 95.3971 | 95.8029 | 96.4029 | 96.1471 | 95.1 | 95.9889 | 95.4414 | 96.7143 | 97.0129 | 97.4114 | 97.2057 | 96.63 | 97.1018 | 93.7671 | 95.73 | 96.3186 | 96.6129 | 96.54 | 96.3314 | 96.3669 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW9600-MS-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 8.32 kW, 208 Vac Grid Support Utility Interactive Inverter | 8.301 | 208 | 96.5 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 182 | 330 | 500 | 0.83015 | 1.6603 | 2.4904 | 4.1507 | 6.2261 | 8.3015 | 94.1286 | 95.3971 | 95.8029 | 96.4029 | 96.1471 | 95.1 | 95.9889 | 95.4414 | 96.7143 | 97.0129 | 97.4114 | 97.2057 | 96.63 | 97.1018 | 93.7671 | 95.73 | 96.3186 | 96.6129 | 96.54 | 96.3314 | 96.3669 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW8600A-MS {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 8.6 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter | 8.612 | 208 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.87 |  |  | 260 | 400 | 480 | 0.8612 | 1.7224 | 2.5836 | 4.306 | 6.459 | 8.612 | 95.1683 | 96.2326 | 96.481 | 96.4873 | 96.0901 | 95.6801 | 96.1702 | 96.2574 | 97.1978 | 97.3196 | 97.1885 | 96.8348 | 96.3944 | 96.9403 | 95.7378 | 96.9162 | 97.1345 | 97.1567 | 96.792 | 96.3471 | 96.8515 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEH8.6-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.614 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.54 |  |  | 260 | 400 | 480 | 0.8614 | 1.7228 | 2.5842 | 4.307 | 6.4605 | 8.614 | 95.3737 | 96.4874 | 96.7887 | 96.8743 | 96.5976 | 96.3068 | 96.6096 | 96.4937 | 97.4708 | 97.6603 | 97.6447 | 97.424 | 97.1058 | 97.4479 | 95.8593 | 97.1544 | 97.4506 | 97.5009 | 97.321 | 97.0125 | 97.2921 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW8600A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.614 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.54 |  |  | 260 | 400 | 480 | 0.8614 | 1.7228 | 2.5842 | 4.307 | 6.4605 | 8.614 | 95.3737 | 96.4874 | 96.7887 | 96.8743 | 96.5976 | 96.3068 | 96.6096 | 96.4937 | 97.4708 | 97.6603 | 97.6447 | 97.424 | 97.1058 | 97.4479 | 95.8593 | 97.1544 | 97.4506 | 97.5009 | 97.321 | 97.0125 | 97.2921 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW8600A-MS {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter | 8.614 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.54 |  |  | 260 | 400 | 480 | 0.8614 | 1.7228 | 2.5842 | 4.307 | 6.4605 | 8.614 | 95.3737 | 96.4874 | 96.7887 | 96.8743 | 96.5976 | 96.3068 | 96.6096 | 96.4937 | 97.4708 | 97.6603 | 97.6447 | 97.424 | 97.1058 | 97.4479 | 95.8593 | 97.1544 | 97.4506 | 97.5009 | 97.321 | 97.0125 | 97.2921 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEP9.6-1-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.566 | 240 | 97 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 210 | 380 | 500 | 0.95659 | 1.9132 | 2.8698 | 4.783 | 7.1744 | 9.5659 | 94.2514 | 95.5914 | 96.1086 | 96.8214 | 96.6686 | 95.6643 | 96.4327 | 96.2314 | 97.3129 | 97.5571 | 97.5886 | 97.3929 | 97.1486 | 97.391 | 95.3114 | 96.7714 | 97.1614 | 97.3143 | 97.1743 | 96.94 | 97.0958 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW9600-MS-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.566 | 240 | 97 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 210 | 380 | 500 | 0.95659 | 1.9132 | 2.8698 | 4.783 | 7.1744 | 9.5659 | 94.2514 | 95.5914 | 96.1086 | 96.8214 | 96.6686 | 95.6643 | 96.4327 | 96.2314 | 97.3129 | 97.5571 | 97.5886 | 97.3929 | 97.1486 | 97.391 | 95.3114 | 96.7714 | 97.1614 | 97.3143 | 97.1743 | 96.94 | 97.0958 | 2022-12-21
GoodWe Technologies Co., Ltd. | GEH9.6-1U-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 9.5862 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 225 | 390 | 500 | 0.95862 | 1.9172 | 2.8759 | 4.7931 | 7.1897 | 9.5862 | 95.3614 | 96.4043 | 96.9143 | 97.0186 | 96.8414 | 96.36 | 96.7822 | 96.0729 | 97.21 | 97.52 | 97.59 | 97.2314 | 97.05 | 97.2849 | 95.8657 | 97.0657 | 97.39 | 97.3929 | 97.0029 | 96.67 | 97.0722 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW9600-ES-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 9.5862 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 225 | 390 | 500 | 0.95862 | 1.9172 | 2.8759 | 4.7931 | 7.1897 | 9.5862 | 95.3614 | 96.4043 | 96.9143 | 97.0186 | 96.8414 | 96.36 | 96.7822 | 96.0729 | 97.21 | 97.52 | 97.59 | 97.2314 | 97.05 | 97.2849 | 95.8657 | 97.0657 | 97.39 | 97.3929 | 97.0029 | 96.67 | 97.0722 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEH9.6-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 9.628 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.4 |  |  | 300 | 400 | 480 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7607 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 97.378 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369 | 97.2329 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW9600A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 9.628 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.4 |  |  | 300 | 400 | 480 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7607 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 97.378 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369 | 97.2329 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW9600A-MS {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter | 9.628 | 208 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.67 |  |  | 300 | 400 | 480 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.688 | 96.5402 | 96.7441 | 96.5807 | 96.1525 | 95.6874 | 96.291 | 96.474 | 97.2271 | 97.2978 | 97.0928 | 96.6375 | 96.1254 | 96.8097 | 95.999 | 96.9906 | 97.1322 | 96.9389 | 96.682 | 96.131 | 96.7505 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW9600A-MS {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter | 9.628 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.4 |  |  | 300 | 400 | 480 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7607 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 97.378 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369 | 97.2329 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW9600H-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional Grid Support Utility Interactive PV and Battery Inverter | 9.628 | 240 | 95.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 | Efficiency data includes external Isolation transformer GW9600G-TF effect. | N | N | 45.22 |  |  | 300 | 400 | 480 | 0.9519 | 1.9038 | 2.8557 | 4.7595 | 7.1393 | 9.519 | 92.2072 | 94.7398 | 95.3899 | 95.5471 | 95.1557 | 94.5552 | 95.0973 | 93.0285 | 95.4529 | 96.0211 | 96.1062 | 95.7384 | 95.1732 | 95.6986 | 92.6051 | 95.1829 | 95.7232 | 95.9558 | 95.6413 | 94.9918 | 95.5403 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEP11.4-1-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 9.88 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.8814 | 208 | 96.5 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 217 | 330 | 500 | 0.98814 | 1.9763 | 2.9644 | 4.9407 | 7.411 | 9.8814 | 95.0829 | 95.9714 | 96.21 | 96.55 | 96.1543 | 95.27 | 96.1479 | 95.8886 | 96.8971 | 97.1029 | 97.0443 | 96.7729 | 96.4329 | 96.8233 | 94.6771 | 96.1986 | 96.5743 | 96.6643 | 96.4371 | 96.12 | 96.4031 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW11K4-MS-US30 {208V} | N | Y | N | N | N | N | Y* | Y | 9.88 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.8814 | 208 | 96.5 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 217 | 330 | 500 | 0.98814 | 1.9763 | 2.9644 | 4.9407 | 7.411 | 9.8814 | 95.0829 | 95.9714 | 96.21 | 96.55 | 96.1543 | 95.27 | 96.1479 | 95.8886 | 96.8971 | 97.1029 | 97.0443 | 96.7729 | 96.4329 | 96.8233 | 94.6771 | 96.1986 | 96.5743 | 96.6643 | 96.4371 | 96.12 | 96.4031 | 2022-12-21
GoodWe Technologies Co., Ltd. | GEH11.4-1U-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 11.3793 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 270 | 390 | 500 | 1.1379 | 2.2759 | 3.4138 | 5.6896 | 8.5345 | 11.3793 | 95.6314 | 96.44 | 96.7957 | 97.0514 | 96.98 | 96.7171 | 96.8788 | 96.49 | 97.4429 | 97.5329 | 97.4414 | 97.2029 | 96.98 | 97.2649 | 96.2414 | 97.1871 | 97.2243 | 97.1386 | 96.99 | 96.3657 | 96.998 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW11K4-ES-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 11.3793 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 270 | 390 | 500 | 1.1379 | 2.2759 | 3.4138 | 5.6896 | 8.5345 | 11.3793 | 95.6314 | 96.44 | 96.7957 | 97.0514 | 96.98 | 96.7171 | 96.8788 | 96.49 | 97.4429 | 97.5329 | 97.4414 | 97.2029 | 96.98 | 97.2649 | 96.2414 | 97.1871 | 97.2243 | 97.1386 | 96.99 | 96.3657 | 96.998 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEP11.4-1-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.397 | 240 | 97 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 250 | 380 | 500 | 1.1397 | 2.2794 | 3.4191 | 5.6985 | 8.5478 | 11.397 | 94.5714 | 95.9 | 96.32 | 96.94 | 96.6886 | 95.7543 | 96.5263 | 96.0429 | 97.1886 | 97.4571 | 97.6214 | 97.43 | 96.9071 | 97.3798 | 95.3171 | 96.7671 | 97.1414 | 97.2357 | 97.0314 | 96.7514 | 96.9917 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW11K4-MS-US30 {240V} | N | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.397 | 240 | 97 | SGS | [10/28/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS China | 2022-10-18 | 2022-12-21 |  | N | N | 4.5 |  |  | 250 | 380 | 500 | 1.1397 | 2.2794 | 3.4191 | 5.6985 | 8.5478 | 11.397 | 94.5714 | 95.9 | 96.32 | 96.94 | 96.6886 | 95.7543 | 96.5263 | 96.0429 | 97.1886 | 97.4571 | 97.6214 | 97.43 | 96.9071 | 97.3798 | 95.3171 | 96.7671 | 97.1414 | 97.2357 | 97.0314 | 96.7514 | 96.9917 | 2022-12-21
GoodWe Technologies Co., Ltd. | GW22KLV-SMT-US {208V} | N | Y | N | N | N | N | Y* | Y | 22 kW, 208 Vac Grid Support Utility Interactive Inverter | 22.1588 | 208 | 97 | CSA Group | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-08-28 | 2024-11-12 |  | N | N | 4.47 |  |  | 350 | 450 | 750 | 2.2159 | 4.4318 | 6.6476 | 11.0794 | 16.6191 | 22.1588 | 95.9672 | 96.8711 | 96.9346 | 96.9687 | 96.6744 | 96.3792 | 96.7342 | 95.3274 | 96.6071 | 96.6503 | 96.8189 | 96.6151 | 96.3378 | 96.5963 | 96.2702 | 96.2073 | 96.3881 | 96.5282 | 96.9802 | 96.6831 | 96.7323 | 2024-11-12 | 2025-10-13
GoodWe Technologies Co., Ltd. | GW22KLV-SMT-US {240V} | N | Y | N | N | N | N | Y* | Y | 22 kW, 240 Vac Grid Support Utility Interactive Inverter | 25.002 | 240 | 97 | CSA Group | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-08-28 | 2024-11-12 |  | N | N | 3.08 |  |  | 350 | 450 | 750 | 2.5002 | 5.0004 | 7.5006 | 12.501 | 18.7515 | 25.002 | 95.448 | 96.7042 | 96.8374 | 96.8323 | 96.5699 | 96.3094 | 96.6059 | 95.4847 | 96.8338 | 97.0085 | 97.1623 | 97.0132 | 96.7838 | 96.9624 | 95.8906 | 95.5633 | 96.114 | 96.5281 | 96.5326 | 96.3578 | 96.3986 | 2024-11-12 | 2025-10-13
GoodWe Technologies Co., Ltd. | GW28KLV-SMT-US {208V} | N | Y | N | N | N | N | Y* | Y | 28 kW, 208 Vac Grid Support Utility Interactive Inverter | 28.1868 | 208 | 97 | CSA Group | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-08-28 | 2024-11-12 |  | N | N | 5.59 |  |  | 350 | 450 | 750 | 2.8187 | 5.6374 | 8.456 | 14.0934 | 21.1401 | 28.1868 | 95.501 | 96.8597 | 97.1295 | 97.1204 | 96.8249 | 96.5285 | 96.8575 | 97.7622 | 96.9613 | 97.3006 | 97.5425 | 97.4815 | 97.2673 | 97.4471 | 95.933 | 96.1044 | 96.5208 | 96.8132 | 96.8139 | 96.661 | 96.7002 | 2024-11-12 | 2025-10-13
GoodWe Technologies Co., Ltd. | GW28KLV-SMT-US {240V} | N | Y | N | N | N | N | Y* | Y | 28 kW, 240 Vac Grid Support Utility Interactive Inverter | 32.1452 | 240 | 97 | CSA Group | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-08-28 | 2024-11-12 |  | N | N | 5.23 |  |  | 350 | 450 | 750 | 3.2145 | 6.429 | 9.6436 | 16.0726 | 24.1089 | 32.1452 | 96.3561 | 96.9969 | 97.2375 | 97.1336 | 96.7634 | 96.42 | 96.8762 | 96.3726 | 97.1495 | 97.4255 | 97.4428 | 97.1938 | 96.8913 | 97.2237 | 96.6327 | 96.3109 | 96.6462 | 96.8504 | 96.7115 | 96.4498 | 96.6966 | 2024-11-12 | 2025-10-13
GoodWe Technologies Co., Ltd. | GW50K-SMT-US {480V} | N | Y | N | N | N | N | Y* | Y | 50 kW, 480 Vac, Transformerless Grid Support Utility Interactive Inverter | 51.252 | 480 | 98 | CSA Group | [8/16/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-10-07 | 2022-12-12 |  | N | N | 7.14 |  |  | 550 | 720 | 850 | 5.1252 | 10.2504 | 15.3756 | 25.626 | 38.439 | 51.252 | 95.5271 | 97.1543 | 97.4986 | 97.8614 | 97.9057 | 97.8371 | 97.7114 | 97.0871 | 98.2357 | 98.5043 | 98.6143 | 98.5886 | 98.5329 | 98.5034 | 96.5657 | 97.8557 | 98.2057 | 98.4143 | 98.4 | 98.3657 | 98.2774 | 2022-12-12
GoodWe Technologies Co., Ltd. | GW60K-SMT-US {480V} | N | Y | N | N | N | N | Y* | Y | 60 kW, 480 Vac, Transformerless Grid Support Utility Interactive Inverter | 61.469 | 480 | 98 | CSA Group | [8/16/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-10-07 | 2022-12-12 |  | N | N | 7.1 |  |  | 550 | 720 | 850 | 6.1469 | 12.2937 | 18.4406 | 30.7343 | 46.1014 | 61.4686 | 96.4343 | 97.3271 | 97.6386 | 97.9029 | 97.8743 | 97.7457 | 97.7606 | 97.6843 | 98.3814 | 98.54 | 98.6314 | 98.5586 | 98.4643 | 98.5231 | 97.0443 | 98.0371 | 98.29 | 98.4514 | 98.3686 | 98.2957 | 98.3034 | 2022-12-12
Green Solutions (Chengdu) Co., Ltd | H12K-US {208V} | Y | Y | N | N | N | N | N | N | 12 kW, 208 Vac Grid Support Interactive Hybrid Inverter | 10.49 | 208 | 96.5 | Intertek | [3/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.05 | 2.1 | 3.15 | 5.25 | 7.875 | 10.499 | 93.48 | 95.27 | 95.93 | 95.85 | 95.61 | 95.29 | 95.58 | 95.07 | 96.66 | 97.03 | 97.31 | 97.1 | 96.41 | 96.99 | 94.29 | 96.71 | 97.16 | 96.95 | 96.77 | 96.47 | 96.74 | 2024-05-21
Green Solutions (Chengdu) Co., Ltd | H12K-US {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Interactive Hybrid Inverter | 11.93 | 240 | 97 | Intertek | [3/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.193 | 2.387 | 3.58 | 5.966 | 8.949 | 11.933 | 95.02 | 96.1 | 96.54 | 96.5 | 96.13 | 95.9 | 96.2 | 96.59 | 97.19 | 97.51 | 97.34 | 97.24 | 97.1 | 97.26 | 95.82 | 97.01 | 97.42 | 97.26 | 97.14 | 97.04 | 97.13 | 2024-05-21
Guangzhou Sanjing Electric Co., Ltd. | H2-5K-LS3-US {208V} | Y | Y | N | N | N | N | N | N | 4.4 kW, 208Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 4.363 | 208 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 24.6 |  |  | 190 | 380 | 510 | 0.436 | 0.873 | 1.309 | 2.181 | 3.272 | 4.363 | 89.13 | 93.12 | 95.34 | 96.49 | 96.89 | 96.68 | 96.11 | 90.68 | 93.87 | 96 | 96.7 | 97.28 | 96.45 | 96.53 | 88.88 | 93.04 | 95.55 | 96.82 | 97.13 | 97.08 | 96.34 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-5K-LS3-US {240V} | Y | Y | N | N | N | N | N | N | 5.0 kW, 240Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 5.067 | 240 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 24.1 |  |  | 190 | 380 | 510 | 0.507 | 1.013 | 1.52 | 2.534 | 3.8 | 5.067 | 89.8 | 93.15 | 95.17 | 96.61 | 96.96 | 97.01 | 96.2 | 90.59 | 94.59 | 96.74 | 96.99 | 97.27 | 97.23 | 96.75 | 89.47 | 93 | 95.78 | 96.73 | 97.18 | 97.13 | 96.4 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-7.6K-S3-US {208V} | Y | Y | N | N | N | N | N | N | 6.6 kW, 208 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 6.605 | 208 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.1 |  |  | 200 | 380 | 550 | 0.66054 | 1.3211 | 1.9816 | 3.3027 | 4.954 | 6.6054 | 91.2646 | 94.8961 | 96.1247 | 96.9883 | 97.1549 | 96.7701 | 96.6285 | 92.3867 | 96.0621 | 97.2134 | 97.6384 | 97.5579 | 97.5114 | 97.2495 | 90.7261 | 94.6534 | 96.0471 | 96.9029 | 97.328 | 97.3169 | 96.6867 | 2023-03-13
Guangzhou Sanjing Electric Co., Ltd. | H2-7.6K-LS3-US {208V} | Y | Y | N | N | N | N | N | N | 6.6 kW, 208Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 6.609 | 208 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 23.9 |  |  | 190 | 380 | 510 | 0.661 | 1.322 | 1.983 | 3.305 | 4.957 | 6.609 | 90.83 | 93.44 | 95.36 | 96.26 | 96.98 | 96.91 | 96.21 | 91.46 | 94.71 | 96.1 | 97.02 | 97.33 | 97.32 | 96.75 | 90.1 | 93.69 | 95.46 | 96.43 | 97.13 | 97.14 | 96.33 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-7.6K-S3-US {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 7.606 | 240 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.1 |  |  | 200 | 380 | 550 | 0.76061 | 1.5212 | 2.2818 | 3.803 | 5.7046 | 7.6061 | 91.6757 | 95.0333 | 96.06 | 96.9014 | 97.0114 | 96.8343 | 96.553 | 93.3129 | 96.5629 | 96.8173 | 97.5543 | 97.7557 | 97.6629 | 97.3588 | 89.9229 | 94.5157 | 95.957 | 96.9959 | 97.4427 | 97.3929 | 96.721 | 2023-03-13
Guangzhou Sanjing Electric Co., Ltd. | H2-7.6K-LS3-US {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 7.61 | 240 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 23.8 |  |  | 190 | 380 | 510 | 0.761 | 1.522 | 2.283 | 3.805 | 5.708 | 7.61 | 90.19 | 93.39 | 95.24 | 95.94 | 96.48 | 96.51 | 95.82 | 91.29 | 95.55 | 96.58 | 97.22 | 97.41 | 97.24 | 96.92 | 91.16 | 94.6 | 96.13 | 96.79 | 97.35 | 97.19 | 96.69 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-9.6K-LS4-US {208V} | Y | Y | N | N | N | N | N | N | 8.3 kW, 208Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 8.316 | 208 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 24.3 |  |  | 190 | 380 | 510 | 0.832 | 1.663 | 2.495 | 4.158 | 6.237 | 8.316 | 90.63 | 93.84 | 95.22 | 96.21 | 96.23 | 96.19 | 95.76 | 91.43 | 94.79 | 96.31 | 97.12 | 97.29 | 97.28 | 96.78 | 89.48 | 93.84 | 95.64 | 96.44 | 97.09 | 97.12 | 96.32 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-10K-S4-US {208V} | Y | Y | N | N | N | N | N | N | 8.8 kW, 208 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 8.798 | 208 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.9 |  |  | 200 | 380 | 550 | 0.87978 | 1.7596 | 2.6394 | 4.3989 | 6.5984 | 8.7978 | 91.9266 | 94.9857 | 95.9901 | 96.6531 | 96.7526 | 96.5514 | 96.3488 | 93.3406 | 96.2684 | 97.2293 | 97.7784 | 97.8737 | 97.7571 | 97.509 | 90.1603 | 94.3034 | 95.8667 | 96.8204 | 97.1063 | 97.1454 | 96.4815 | 2023-03-13
Guangzhou Sanjing Electric Co., Ltd. | H2-9.6K-LS4-US {240V} | Y | Y | N | N | N | N | N | N | 9.6 kW, 240Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 9.605 | 240 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 24.2 |  |  | 190 | 380 | 510 | 0.96 | 1.921 | 2.881 | 4.802 | 7.204 | 9.605 | 90.78 | 94.02 | 94.95 | 96.2 | 96.55 | 96.62 | 95.93 | 91.87 | 95.28 | 96.52 | 97.45 | 97.38 | 97.25 | 96.96 | 89.9 | 94.28 | 95.82 | 97.23 | 97.04 | 97.03 | 96.51 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-11.4K-LS4-US {208V} | Y | Y | N | N | N | N | N | N | 9.9 kW, 208Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 9.881 | 208 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 24.1 |  |  | 190 | 380 | 510 | 0.988 | 1.976 | 2.964 | 4.94 | 7.411 | 9.881 | 91.26 | 94.37 | 95.55 | 96.31 | 96.34 | 96 | 95.92 | 92.71 | 95.49 | 96.99 | 97.27 | 97.31 | 97.15 | 96.98 | 90.94 | 94.23 | 96.38 | 97.13 | 97.29 | 97.2 | 96.74 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-10K-S4-US {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 10.089 | 240 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3 |  |  | 200 | 380 | 550 | 1.0089 | 2.0179 | 3.0268 | 5.0447 | 7.5671 | 10.0894 | 92.505 | 95.285 | 96.1289 | 96.6833 | 96.757 | 96.5369 | 96.4115 | 93.3783 | 96.0274 | 96.8706 | 97.488 | 97.6233 | 97.8881 | 97.2682 | 91.7759 | 95.115 | 96.252 | 97.1056 | 97.3409 | 97.2843 | 96.8241 | 2023-03-13
Guangzhou Sanjing Electric Co., Ltd. | H2-12K-S4-US {208V} | Y | Y | N | N | N | N | N | N | 10.4 kW, 208 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 10.417 | 208 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.8 |  |  | 200 | 380 | 550 | 1.0417 | 2.0833 | 3.125 | 5.2084 | 7.8126 | 10.4167 | 92.9157 | 95.6341 | 96.2164 | 96.654 | 96.3786 | 96.1233 | 96.2285 | 94.2331 | 96.697 | 97.4084 | 97.7706 | 97.7253 | 97.5054 | 97.4947 | 91.3866 | 95.1003 | 96.1777 | 96.8868 | 97.0123 | 96.3247 | 96.5308 | 2023-03-13
Guangzhou Sanjing Electric Co., Ltd. | H2-11.4K-LS4-US {240V} | Y | Y | N | N | N | N | N | N | 11.3 kW, 240Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 11.298 | 240 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 24 |  |  | 190 | 380 | 510 | 1.13 | 2.26 | 3.389 | 5.649 | 8.474 | 11.298 | 92.02 | 94.77 | 95.72 | 96.39 | 96.3 | 96.18 | 95.99 | 93.01 | 95.73 | 96.74 | 97.43 | 97.37 | 97.36 | 97.05 | 91.95 | 95.01 | 96.59 | 97.29 | 97.19 | 97.21 | 96.82 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-12K-S4-US {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 12.034 | 240 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.2 |  |  | 200 | 380 | 550 | 1.2034 | 2.4068 | 3.6103 | 6.0171 | 9.0257 | 12.0342 | 93.1914 | 95.6541 | 96.3079 | 96.6811 | 96.526 | 96.1971 | 96.339 | 93.908 | 96.3353 | 97.0489 | 97.4993 | 97.4757 | 97.2611 | 97.219 | 92.4186 | 95.4427 | 96.5387 | 97.1697 | 97.2534 | 97.11 | 96.859 | 2023-03-13
Gwatt Innovations Ltd | GLADE RM-900M-X {240V} | N | Y | Y | Y | Y | Y | Y* |  | 0.45 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.45 | 240 | 95 | Intertek | [7/1/2026] | Intertek | [7/1/2026] | [GJ1.0] | 2026-07-13 | [7/1/2026] | 2026-07-13 | Intertek | 2026-03-12 |  |  | N | Y | 0.04 |  |  | 27 | 43 | 59 | 0.045 | 0.09 | 0.135 | 0.225 | 0.337 | 0.45 | 85.29 | 92.98 | 94.54 | 95.72 | 95.87 | 95.49 | 95.09 | 84.46 | 90.85 | 93.96 | 95.82 | 96.51 | 96.06 | 95.27 | 80.94 | 87.78 | 92.23 | 94.94 | 96.22 | 96.25 | 94.44 | 2026-07-13 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
Gwatt Innovations Ltd | GLADE RM-450M-X {240V} | N | Y | Y | Y | Y | Y | Y* |  | 0.903 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.903 | 240 | 95 | Intertek | [7/1/2026] | Intertek | [7/1/2026] | [GJ1.0] | 2026-07-13 | [7/1/2026] | 2026-07-13 | Intertek | 2026-03-12 |  |  | N | Y | 0.903 |  |  | 29 | 44 | 59 | 0.09 | 0.181 | 0.271 | 0.451 | 0.677 | 0.903 | 90.35 | 93.81 | 95.46 | 96.16 | 95.89 | 95.25 | 95.54 | 84.76 | 91.69 | 94.52 | 96.55 | 95.93 | 95.52 | 95.21 | 80.62 | 88.39 | 93.5 | 95.67 | 95.92 | 95.65 | 94.58 | 2026-07-13 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
HiQ Solar | TSXL480-10k {480V} | N | N | Y | Y | Y | N | N | N | 9.975 kW, 480 Vac Grid Support Utility Interactive Inverter | 9.975 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [09/28/2018] | [0.28] | 2019-02-01 | [09/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 8.3 |  |  | 450 | 750 | 850 | 0.9975 | 1.995 | 2.9925 | 4.9875 | 7.4812 | 9.975 | 94.1157 | 96.7771 | 97.3429 | 97.7271 | 97.6957 | 97.5171 | 97.4619 | 94.11 | 96.8457 | 97.6443 | 98.1614 | 98.22 | 98.14 | 97.9015 | 93.1871 | 96.46 | 97.4557 | 98.1029 | 98.2386 | 98.2 | 97.8232 | 2018-11-01 | 2019-02-15
Hitachi Energy Power Conversion Solutions S.L.U | MP2Ms2.3BsWD3-V850 {850V} | Y | Y | N | N | N | N | N |  | 1304.52 kW, 850 Vac Grid Support Utility Interactive Inverter with external transformer. (made up of two 1MsWD3-V850 installed together rated max output power = 2,609kW) | 1304.52 | 850 | 98.5 | SGS | [4/6/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | Y | N | 181.5592 |  |  | 1216 | 1310 | 1500 | 130.452 | 260.904 | 391.356 | 652.26 | 978.39 | 1304.52 | 97.4306 | 98.241 | 98.5415 | 98.5348 | 98.2694 | 98.0394 | 98.3113 | 97.3156 | 98.2211 | 98.5166 | 98.4941 | 98.2684 | 97.9794 | 98.2906 | 97.1603 | 98.0934 | 98.498 | 98.4325 | 98.2143 | 97.9187 | 98.2312 | 2026-10-12 |  | Y | N | N | N | N | N | Y | N | No Information Submitted
Holu Hou Energy LLC | HH9600H-HI {240V} | Y | N | Y | Y | Y | N | N | N | 9.6 KW, 240 Vac Non-isolated Grid Support Utility Interactive Hybrid Inverter | 9.628 | 240 | 97 | No Information Submitted | No Information Submitted | CSA Group | [5/20/2020] | [00, 13] | 2023-03-13 | [5/20/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model number can also be configured as an Isolated Inverter with Isolation Transformer HH9600H-IT which changes the overal weighted efficiency to 95.5% and night tare loss to 45.22 W. | Y | N | 9.4 |  |  | 300 | 400 | 480 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7607 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 97.378 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369 | 97.2329 | 2023-03-13
Hongyibo New Energy Technology (Shenzhen) Co., Ltd. | PCSR5KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac, Grid Support Utility Inverter with PCS functionality. | 5.0897 | 240 | 97 | SGS | [2/24/2025] | SGS | [2/24/2025] | [V1.04.06(DSP), V1.03.03(ARM)] | 2025-06-11 | [2/24/2025] | 2025-06-11 | SGS | 2025-03-14 | 2025-06-11 |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2025-06-11
Hongyibo New Energy Technology (Shenzhen) Co., Ltd. | PCSR6KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac, Grid Support Utility Inverter with PCS functionality. | 6.1172 | 240 | 97 | SGS | [2/24/2025] | SGS | [2/24/2025] | [V1.04.06(DSP), V1.03.03(ARM)] | 2025-06-11 | [2/24/2025] | 2025-06-11 | SGS | 2025-03-14 | 2025-06-11 |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2025-06-11
Hongyibo New Energy Technology (Shenzhen) Co., Ltd. | PCSR7K6LNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Grid Support Utility Inverter with PCS functionality. | 7.7647 | 240 | 97 | SGS | [2/24/2025] | SGS | [2/24/2025] | [V1.04.06(DSP), V1.03.03(ARM)] | 2025-06-11 | [2/24/2025] | 2025-06-11 | SGS | 2025-03-14 | 2025-06-11 |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2025-06-11
Hongyibo New Energy Technology (Shenzhen) Co., Ltd. | PCSR8KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.0 kW, 240 Vac, Grid Support Utility Inverter with PCS functionality. | 8.0842 | 240 | 97.5 | SGS | [2/24/2025] | SGS | [2/24/2025] | [V1.04.06(DSP), V1.03.03(ARM)] | 2025-06-11 | [2/24/2025] | 2025-06-11 | SGS | 2025-03-14 | 2025-06-11 |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2025-06-11
Hongyibo New Energy Technology (Shenzhen) Co., Ltd. | PCSR10KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.0 kW, 240 Vac, Grid Support Utility Inverter with PCS functionality. | 10.1767 | 240 | 97 | SGS | [2/24/2025] | SGS | [2/24/2025] | [V1.04.06(DSP), V1.03.03(ARM)] | 2025-06-11 | [2/24/2025] | 2025-06-11 | SGS | 2025-03-14 | 2025-06-11 |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2025-06-11
Hoymiles Power Electronics Inc. | HM-300N {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 295 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.29542 | 240 | 96.5 | CSA Group | [2/27/2023] | CSA Group | [06/12/2020] | [V01.01.00] | 2020-08-03 | [06/12/2020] | 2021-03-11 | CSA Group | 2023-02-21 | 2021-03-11 |  | N | Y | 0.105 |  |  | 33 | 40 | 48 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 96.436 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 96.4594 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412 | 96.4528 | 2020-08-03 | 2023-04-11
Hoymiles Power Electronics Inc. | HM-300NT {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 295 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.29542 | 240 | 96.5 | CSA Group | [2/27/2023] | CSA Group | [06/12/2020] | [V01.01.00] | 2020-08-03 | [06/12/2020] | 2021-03-11 | CSA Group | 2023-02-21 | 2021-03-11 |  | N | Y | 0.108 |  |  | 29 | 40 | 48 | 0.029542 | 0.059084 | 0.088625 | 0.14771 | 0.22156 | 0.29542 | 95.7121 | 96.1282 | 96.1964 | 96.433 | 96.6065 | 96.1055 | 96.4361 | 95.909 | 95.9846 | 96.359 | 96.3181 | 96.6257 | 96.449 | 96.4595 | 95.3737 | 95.8309 | 96.4129 | 96.185 | 96.6993 | 96.541 | 96.4526 | 2020-08-03 | 2023-04-11
Hoymiles Power Electronics Inc. | HM-300NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 295 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.29542 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [06/12/2020] | [V01.01.00] | 2020-08-03 | [06/12/2020] | 2021-03-11 | CSA Group | 2021-01-26 | 2021-03-11 |  | N | Y | 0.108 |  |  | 29 | 40 | 48 | 0.029542 | 0.059084 | 0.088625 | 0.14771 | 0.22156 | 0.29542 | 95.7121 | 96.1282 | 96.1964 | 96.433 | 96.6065 | 96.1055 | 96.4361 | 95.909 | 95.9846 | 96.359 | 96.3181 | 96.6257 | 96.449 | 96.4595 | 95.3737 | 95.8309 | 96.4129 | 96.185 | 96.6993 | 96.541 | 96.4526 | 2020-08-03 | 2021-03-11
Hoymiles Power Electronics Inc. | HMS-300-1A-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 295 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.29542 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-11 | [01/29/2021] | 2021-03-11 | CSA Group | 2021-01-26 | 2021-03-11 |  | N | Y | 0.108 |  |  | 29 | 40 | 48 | 0.029542 | 0.059084 | 0.088625 | 0.14771 | 0.22156 | 0.29542 | 95.7121 | 96.1282 | 96.1964 | 96.433 | 96.6065 | 96.1055 | 96.4361 | 95.909 | 95.9846 | 96.359 | 96.3181 | 96.6257 | 96.449 | 96.4595 | 95.3737 | 95.8309 | 96.4129 | 96.185 | 96.6993 | 96.541 | 96.4526 | 2021-03-11
Hoymiles Power Electronics Inc. | HMS-300-1D-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 295 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.29542 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-11 | [01/29/2021] | 2021-03-11 | CSA Group | 2021-01-26 | 2021-03-11 |  | N | Y | 0.108 |  |  | 29 | 40 | 48 | 0.029542 | 0.059084 | 0.088625 | 0.14771 | 0.22156 | 0.29542 | 95.7121 | 96.1282 | 96.1964 | 96.433 | 96.6065 | 96.1055 | 96.4361 | 95.909 | 95.9846 | 96.359 | 96.3181 | 96.6257 | 96.449 | 96.4595 | 95.3737 | 95.8309 | 96.4129 | 96.185 | 96.6993 | 96.541 | 96.4526 | 2021-03-11
Hoymiles Power Electronics Inc. | HMS-300-1T-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 295 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.29542 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-11 | [01/29/2021] | 2021-03-11 | CSA Group | 2021-01-26 | 2021-03-11 |  | N | Y | 0.108 |  |  | 29 | 40 | 48 | 0.029542 | 0.059084 | 0.088625 | 0.14771 | 0.22156 | 0.29542 | 95.7121 | 96.1282 | 96.1964 | 96.433 | 96.6065 | 96.1055 | 96.4361 | 95.909 | 95.9846 | 96.359 | 96.3181 | 96.6257 | 96.449 | 96.4595 | 95.3737 | 95.8309 | 96.4129 | 96.185 | 96.6993 | 96.541 | 96.4526 | 2021-03-11
Hoymiles Power Electronics Inc. | HMS-350-1A-NA {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.3218 | 240 | 96.5 | CSA Group | [2/27/2023] | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-11 | [01/29/2021] | 2021-03-11 | CSA Group | 2023-02-21 | 2021-03-11 |  | N | Y | 0.09 |  |  | 33 | 42 | 48 | 0.03218 | 0.064359 | 0.096539 | 0.1609 | 0.24135 | 0.3218 | 94.4933 | 96.0424 | 96.3722 | 96.4732 | 96.515 | 96.0615 | 96.3619 | 94.7692 | 95.8757 | 96.4474 | 96.4821 | 96.4994 | 96.1342 | 96.3709 | 94.0869 | 95.7885 | 96.3838 | 96.4832 | 96.4915 | 96.1272 | 96.3273 | 2021-03-11 | 2023-04-11
Hoymiles Power Electronics Inc. | HMS-350-1T-NA {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.3218 | 240 | 96.5 | CSA Group | [2/27/2023] | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-11 | [01/29/2021] | 2021-03-11 | CSA Group | 2023-02-21 | 2021-03-11 |  | N | Y | 0.09 |  |  | 33 | 42 | 48 | 0.03218 | 0.064359 | 0.096539 | 0.1609 | 0.24135 | 0.3218 | 94.4933 | 96.0424 | 96.3722 | 96.4732 | 96.515 | 96.0615 | 96.3619 | 94.7692 | 95.8757 | 96.4474 | 96.4821 | 96.4994 | 96.1342 | 96.3709 | 94.0869 | 95.7885 | 96.3838 | 96.4832 | 96.4915 | 96.1272 | 96.3273 | 2021-03-11 | 2023-04-11
Hoymiles Power Electronics Inc. | MIS-350-1A-NA {240V} | N | Y | N | N | N | N | Y* | Y | 319 W, 240 Vac, Grid Support Utility Interactive Microinverter | 0.33029 | 240 | 97 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-16 | 2025-03-11 |  | N | Y | 0.07 |  |  | 27 | 37.5 | 48 | 0.033029 | 0.066057 | 0.099086 | 0.16514 | 0.24771 | 0.33029 | 94.4021 | 95.3979 | 95.9979 | 97.3016 | 97.1989 | 96.8005 | 96.8545 | 94.9052 | 95.7014 | 96.302 | 97.1992 | 97.1071 | 96.9008 | 96.8611 | 94.6978 | 95.5044 | 96.099 | 97.3991 | 97.3016 | 96.6991 | 96.9536 | 2025-03-11
Hoymiles Power Electronics Inc. | MIS-350-1NA {240V} | N | Y | N | N | N | N | Y* | Y | 319 W, 240 Vac, Grid Support Utility Interactive Microinverter | 0.33029 | 240 | 97 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-16 | 2025-03-11 |  | N | Y | 0.07 |  |  | 27 | 37.5 | 48 | 0.033029 | 0.066057 | 0.099086 | 0.16514 | 0.24771 | 0.33029 | 94.4021 | 95.3979 | 95.9979 | 97.3016 | 97.1989 | 96.8005 | 96.8545 | 94.9052 | 95.7014 | 96.302 | 97.1992 | 97.1071 | 96.9008 | 96.8611 | 94.6978 | 95.5044 | 96.099 | 97.3991 | 97.3016 | 96.6991 | 96.9536 | 2025-03-11
Hoymiles Power Electronics Inc. | HM-350N {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.3495 | 240 | 96.5 | CSA Group | [2/27/2023] | CSA Group | [06/12/2020] | [V01.01.00] | 2020-08-03 | [06/12/2020] | 2021-03-11 | CSA Group | 2023-02-21 | 2021-03-11 |  | N | Y | 0.105 |  |  | 33 | 40 | 48 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 96.436 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 96.4594 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412 | 96.4528 | 2020-08-03 | 2023-04-11
Hoymiles Power Electronics Inc. | HM-350NT {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.3495 | 240 | 96.5 | CSA Group | [2/27/2023] | CSA Group | [06/12/2020] | [V01.01.00] | 2020-08-03 | [06/12/2020] | 2021-03-11 | CSA Group | 2023-02-21 | 2021-03-11 |  | N | Y | 0.105 |  |  | 33 | 40 | 48 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 96.436 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 96.4594 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412 | 96.4528 | 2020-08-03 | 2023-04-11
Hoymiles Power Electronics Inc. | HM-350NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.3495 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [06/12/2020] | [V01.01.00] | 2020-08-03 | [06/12/2020] | 2021-03-11 | CSA Group | 2021-01-26 | 2021-03-11 |  | N | Y | 0.105 |  |  | 33 | 40 | 48 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 96.436 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 96.4594 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412 | 96.4528 | 2020-08-03 | 2021-03-11
Hoymiles Power Electronics Inc. | HMS-350-1D-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.3495 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-11 | [01/29/2021] | 2021-03-11 | CSA Group | 2021-01-26 | 2021-03-11 |  | N | Y | 0.105 |  |  | 33 | 40 | 48 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 96.436 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 96.4594 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412 | 96.4528 | 2021-03-11
Hoymiles Power Electronics Inc. | HMS-400-1A-NA {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 382 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.3618 | 240 | 96.5 | CSA Group | [2/27/2023] | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-11 | [01/29/2021] | 2021-03-11 | CSA Group | 2023-02-21 | 2021-03-11 |  | N | Y | 0.09 |  |  | 34 | 42 | 48 | 0.03618 | 0.072359 | 0.10854 | 0.1809 | 0.27135 | 0.3618 | 94.708 | 96.059 | 96.3405 | 96.4559 | 96.5234 | 96.071 | 96.3688 | 94.6678 | 95.7403 | 96.4642 | 96.4729 | 96.4939 | 96.1093 | 96.356 | 94.0267 | 95.737 | 96.3644 | 96.4424 | 96.4564 | 96.1272 | 96.2928 | 2021-03-11 | 2023-04-11
Hoymiles Power Electronics Inc. | HMS-400-1T-NA {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 382 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.3618 | 240 | 96.5 | CSA Group | [2/27/2023] | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-11 | [01/29/2021] | 2021-03-11 | CSA Group | 2023-02-21 | 2021-03-11 |  | N | Y | 0.09 |  |  | 34 | 42 | 48 | 0.03618 | 0.072359 | 0.10854 | 0.1809 | 0.27135 | 0.3618 | 94.708 | 96.059 | 96.3405 | 96.4559 | 96.5234 | 96.071 | 96.3688 | 94.6678 | 95.7403 | 96.4642 | 96.4729 | 96.4939 | 96.1093 | 96.356 | 94.0267 | 95.737 | 96.3644 | 96.4424 | 96.4564 | 96.1272 | 96.2928 | 2021-03-11 | 2023-04-11
Hoymiles Power Electronics Inc. | HMS-360-1WM-LV {120V} | N | Y | N | N | N | N | N |  | 366 W, 120 Vac Grid Support Utility Interactive Microinverter | 0.366 | 120 | 95.5 | CSA Group | [7/3/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | Y | 0.13 |  |  | 28 | 38 | 48 | 0.037 | 0.073 | 0.11 | 0.183 | 0.274 | 0.366 | 93.91 | 95.12 | 95.42 | 95.34 | 95.33 | 94.86 | 95.25 | 93.66 | 95.02 | 95.47 | 95.45 | 95.39 | 95.05 | 95.31 | 93.66 | 94.9 | 95.41 | 95.49 | 95.38 | 95.01 | 95.29 | 2026-08-21 |  | Y | N | N | N | N | N | N | N | N
Hoymiles Power Electronics Inc. | MIS-400-1A-NA {240V} | N | Y | N | N | N | N | Y* | Y | 360 W, 240 Vac, Grid Support Utility Interactive Microinverter | 0.36763 | 240 | 97 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-16 | 2025-03-11 |  | N | Y | 0.07 |  |  | 28 | 38 | 48 | 0.036763 | 0.073527 | 0.11029 | 0.18382 | 0.27573 | 0.36763 | 94.6032 | 95.6215 | 96.398 | 97.205 | 97.2022 | 96.7019 | 96.8983 | 94.8007 | 96.0032 | 96.499 | 97.4918 | 97.2965 | 96.8963 | 97.0573 | 94.7008 | 95.7952 | 96.2972 | 97.3077 | 97.3043 | 96.807 | 96.9797 | 2025-03-11
Hoymiles Power Electronics Inc. | MIS-400-1NA {240V} | N | Y | N | N | N | N | Y* | Y | 360 W, 240 Vac, Grid Support Utility Interactive Microinverter | 0.36763 | 240 | 97 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-16 | 2025-03-11 |  | N | Y | 0.07 |  |  | 28 | 38 | 48 | 0.036763 | 0.073527 | 0.11029 | 0.18382 | 0.27573 | 0.36763 | 94.6032 | 95.6215 | 96.398 | 97.205 | 97.2022 | 96.7019 | 96.8983 | 94.8007 | 96.0032 | 96.499 | 97.4918 | 97.2965 | 96.8963 | 97.0573 | 94.7008 | 95.7952 | 96.2972 | 97.3077 | 97.3043 | 96.807 | 96.9797 | 2025-03-11
Hoymiles Power Electronics Inc. | HM-400NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 382 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.38254 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [06/12/2020] | [V01.01.00] | 2020-08-03 | [06/12/2020] | 2021-03-11 | CSA Group | 2021-01-26 | 2021-03-11 |  | N | Y | 0.105 |  |  | 34 | 42 | 48 | 0.038254 | 0.076508 | 0.11476 | 0.19127 | 0.28691 | 0.38254 | 95.2284 | 96.2184 | 96.2572 | 96.5457 | 96.7835 | 96.1938 | 96.5505 | 95.6795 | 96.127 | 96.4072 | 96.3431 | 96.7759 | 96.5316 | 96.5522 | 96.0364 | 95.9735 | 96.4085 | 96.2046 | 96.6989 | 96.6089 | 96.4929 | 2020-08-03 | 2021-03-11
Hoymiles Power Electronics Inc. | HMS-400-1D-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 382 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.38254 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-11 | [01/29/2021] | 2021-03-11 | CSA Group | 2021-01-26 | 2021-03-11 |  | N | Y | 0.105 |  |  | 34 | 42 | 48 | 0.038 | 0.077 | 0.115 | 0.191 | 0.287 | 0.383 | 95.23 | 96.22 | 96.26 | 96.55 | 96.78 | 96.19 | 96.55 | 95.68 | 96.13 | 96.41 | 96.34 | 96.78 | 96.53 | 96.55 | 96.04 | 95.97 | 96.41 | 96.2 | 96.7 | 96.61 | 96.49 | 2021-03-11
Hoymiles Power Electronics Inc. | HM-400N {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 382 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.38254 | 240 | 96.5 | CSA Group | [2/27/2023] | CSA Group | [06/12/2020] | [V01.01.00] | 2020-08-03 | [06/12/2020] | 2021-03-11 | CSA Group | 2023-02-21 | 2021-03-11 |  | N | Y | 0.105 |  |  | 34 | 42 | 48 | 0.038254 | 0.076508 | 0.11476 | 0.19127 | 0.28691 | 0.38254 | 95.2284 | 96.2184 | 96.2572 | 96.5457 | 96.7835 | 96.1938 | 96.5505 | 95.6795 | 96.127 | 96.4072 | 96.3431 | 96.7759 | 96.5316 | 96.5522 | 96.0364 | 95.9735 | 96.4085 | 96.2046 | 96.6989 | 96.6089 | 96.4929 | 2020-08-03 | 2023-04-11
Hoymiles Power Electronics Inc. | HM-400NT {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 382 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.38254 | 240 | 96.5 | CSA Group | [2/27/2023] | CSA Group | [06/12/2020] | [V01.01.00] | 2020-08-03 | [06/12/2020] | 2021-03-11 | CSA Group | 2023-02-21 | 2021-03-11 |  | N | Y | 0.105 |  |  | 34 | 42 | 48 | 0.038254 | 0.076508 | 0.11476 | 0.19127 | 0.28691 | 0.38254 | 95.2284 | 96.2184 | 96.2572 | 96.5457 | 96.7835 | 96.1938 | 96.5505 | 95.6795 | 96.127 | 96.4072 | 96.3431 | 96.7759 | 96.5316 | 96.5522 | 96.0364 | 95.9735 | 96.4085 | 96.2046 | 96.6989 | 96.6089 | 96.4929 | 2020-08-03 | 2023-04-11
Hoymiles Power Electronics Inc. | HM-400N {208V} | N | Y | N | N | N | N | Y* | Y | 382 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.38726 | 208 | 96.5 | CSA Group | [2/24/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-02-21 | 2023-10-02 |  | N | Y | 0.09 |  |  | 38 | 42 | 48 | 0.038726 | 0.077452 | 0.11618 | 0.19363 | 0.29045 | 0.38726 | 94.6456 | 96.0225 | 96.3244 | 96.4166 | 96.4735 | 95.9551 | 96.3221 | 94.6265 | 95.7556 | 96.3916 | 96.4249 | 96.447 | 96.0618 | 96.3091 | 94.8633 | 95.8439 | 96.3819 | 96.3279 | 96.5471 | 96.2922 | 96.366 | 2023-10-02
Hoymiles Power Electronics Inc. | HM-400NT {208V} | N | Y | N | N | N | N | Y* | Y | 382 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.38726 | 208 | 96.5 | CSA Group | [2/24/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-02-21 | 2023-10-02 |  | N | Y | 0.09 |  |  | 38 | 42 | 48 | 0.038726 | 0.077452 | 0.11618 | 0.19363 | 0.29045 | 0.38726 | 94.6456 | 96.0225 | 96.3244 | 96.4166 | 96.4735 | 95.9551 | 96.3221 | 94.6265 | 95.7556 | 96.3916 | 96.4249 | 96.447 | 96.0618 | 96.3091 | 94.8633 | 95.8439 | 96.3819 | 96.3279 | 96.5471 | 96.2922 | 96.366 | 2023-10-02
Hoymiles Power Electronics Inc. | HMS-391-1WM-LV {120V} | N | Y | N | N | N | N | N |  | 398 W, 120 Vac Grid Support Utility Interactive Microinverter | 0.398 | 120 | 95.5 | CSA Group | [7/3/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | Y | 0.17 |  |  | 30 | 39 | 48 | 0.04 | 0.08 | 0.119 | 0.199 | 0.298 | 0.398 | 93.86 | 95.11 | 95.34 | 95.43 | 95.35 | 94.88 | 95.27 | 93.58 | 95 | 95.41 | 95.49 | 95.32 | 94.92 | 95.26 | 93.56 | 94.91 | 95.33 | 95.49 | 95.29 | 94.95 | 95.23 | 2026-08-21 |  | Y | N | N | N | N | N | N | N | N
Hoymiles Power Electronics Inc. | HMS-450-1A-NA {240V} | N | Y | N | N | N | N | Y* | Y | 410 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.41128 | 240 | 96.5 | CSA Group | [2/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-02-21 | 2023-04-11 |  | N | Y | 0.09 |  |  | 36 | 42 | 48 | 0.041128 | 0.082256 | 0.12338 | 0.20564 | 0.30846 | 0.41128 | 94.6142 | 96.0375 | 96.3485 | 96.4614 | 96.4934 | 96.063 | 96.3498 | 94.6576 | 95.8028 | 96.4413 | 96.4383 | 96.4895 | 96.1109 | 96.3464 | 94.1088 | 95.7415 | 96.373 | 96.4537 | 96.4623 | 96.0927 | 96.3011 | 2023-04-11
Hoymiles Power Electronics Inc. | HMS-450-1T-NA {240V} | N | Y | N | N | N | N | Y* | Y | 410 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.41128 | 240 | 96.5 | CSA Group | [2/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-02-21 | 2023-04-11 |  | N | Y | 0.09 |  |  | 36 | 42 | 48 | 0.041128 | 0.082256 | 0.12338 | 0.20564 | 0.30846 | 0.41128 | 94.6142 | 96.0375 | 96.3485 | 96.4614 | 96.4934 | 96.063 | 96.3498 | 94.6576 | 95.8028 | 96.4413 | 96.4383 | 96.4895 | 96.1109 | 96.3464 | 94.1088 | 95.7415 | 96.373 | 96.4537 | 96.4623 | 96.0927 | 96.3011 | 2023-04-11
Hoymiles Power Electronics Inc. | MIS-450-1A-NA {240V} | N | Y | N | N | N | N | Y* | Y | 410 W, 240 Vac, Grid Support Utility Interactive Microinverter | 0.42088 | 240 | 97 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-16 | 2025-03-11 |  | N | Y | 0.03 |  |  | 30 | 39 | 48 | 0.042088 | 0.084176 | 0.12626 | 0.21044 | 0.31566 | 0.42088 | 94.8575 | 95.8335 | 96.2888 | 97.1966 | 97.0991 | 96.7996 | 96.8544 | 95.8859 | 96.5265 | 96.7132 | 97.218 | 97.2016 | 97.1891 | 97.0594 | 95.2753 | 96.1027 | 96.4084 | 97.1043 | 97.2951 | 97.4053 | 97.0137 | 2025-03-11
Hoymiles Power Electronics Inc. | MIS-450-1NA {240V} | N | Y | N | N | N | N | Y* | Y | 410 W, 240 Vac, Grid Support Utility Interactive Microinverter | 0.42088 | 240 | 97 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-16 | 2025-03-11 |  | N | Y | 0.03 |  |  | 30 | 39 | 48 | 0.042088 | 0.084176 | 0.12626 | 0.21044 | 0.31566 | 0.42088 | 94.8575 | 95.8335 | 96.2888 | 97.1966 | 97.0991 | 96.7996 | 96.8544 | 95.8859 | 96.5265 | 96.7132 | 97.218 | 97.2016 | 97.1891 | 97.0594 | 95.2753 | 96.1027 | 96.4084 | 97.1043 | 97.2951 | 97.4053 | 97.0137 | 2025-03-11
Hoymiles Power Electronics Inc. | HMS-420-1WM-LV {120V} | N | Y | N | N | N | N | N |  | 427 W, 120 Vac Grid Support Utility Interactive Microinverter | 0.427 | 120 | 95.5 | CSA Group | [7/3/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | Y | 0.18 |  |  | 32 | 40 | 48 | 0.043 | 0.085 | 0.128 | 0.214 | 0.321 | 0.427 | 93.87 | 95.12 | 95.37 | 95.4 | 95.34 | 94.78 | 95.26 | 93.61 | 95.01 | 95.43 | 95.48 | 95.34 | 94.97 | 95.28 | 93.6 | 94.91 | 95.36 | 95.49 | 95.32 | 94.99 | 95.26 | 2026-08-21 |  | Y | N | N | N | N | N | N | N | N
Hoymiles Power Electronics Inc. | HMS-500-1A-NA {240V} | N | Y | N | N | N | N | Y* | Y | 475 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.47616 | 240 | 96.5 | CSA Group | [2/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-02-21 | 2023-04-11 |  | N | Y | 0.09 |  |  | 38 | 42 | 48 | 0.047616 | 0.095232 | 0.14285 | 0.23808 | 0.35712 | 0.47616 | 94.6979 | 96.0131 | 96.3419 | 96.4429 | 96.4863 | 96.0307 | 96.3419 | 94.6546 | 95.8147 | 96.4264 | 96.4413 | 96.475 | 96.1019 | 96.3376 | 94.0386 | 95.745 | 96.3613 | 96.4537 | 96.4738 | 96.1063 | 96.3038 | 2023-04-11
Hoymiles Power Electronics Inc. | HMS-500-1T-NA {240V} | N | Y | N | N | N | N | Y* | Y | 475 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.47616 | 240 | 96.5 | CSA Group | [2/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-02-21 | 2023-04-11 |  | N | Y | 0.09 |  |  | 38 | 42 | 48 | 0.047616 | 0.095232 | 0.14285 | 0.23808 | 0.35712 | 0.47616 | 94.6979 | 96.0131 | 96.3419 | 96.4429 | 96.4863 | 96.0307 | 96.3419 | 94.6546 | 95.8147 | 96.4264 | 96.4413 | 96.475 | 96.1019 | 96.3376 | 94.0386 | 95.745 | 96.3613 | 96.4537 | 96.4738 | 96.1063 | 96.3038 | 2023-04-11
Hoymiles Power Electronics Inc. | MIS-500-1A-NA {240V} | N | Y | N | N | N | N | Y* | Y | 475 W, 240 Vac, Grid Support Utility Interactive Microinverter | 0.47636 | 240 | 96.5 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-16 | 2025-03-11 |  | N | Y | 0.07 |  |  | 32 | 40 | 48 | 0.047636 | 0.095272 | 0.14291 | 0.23818 | 0.35727 | 0.47636 | 94.1545 | 95.2732 | 96.0067 | 96.7294 | 96.9104 | 96.2948 | 96.541 | 94.6921 | 94.9749 | 96.402 | 96.7201 | 96.7251 | 96.7036 | 96.5154 | 94.4099 | 95.4819 | 96.7881 | 96.8403 | 96.6448 | 96.4121 | 96.5439 | 2025-03-11
Hoymiles Power Electronics Inc. | MIS-500-1NA {240V} | N | Y | N | N | N | N | Y* | Y | 475 W, 240 Vac, Grid Support Utility Interactive Microinverter | 0.47636 | 240 | 96.5 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-16 | 2025-03-11 |  | N | Y | 0.02 |  |  | 32 | 40 | 48 | 0.047956 | 0.095911 | 0.14387 | 0.23978 | 0.35967 | 0.47956 | 94.3356 | 95.2717 | 95.3596 | 96.7151 | 96.7161 | 96.3012 | 96.3649 | 94.9961 | 95.791 | 95.6352 | 96.6208 | 96.9094 | 96.8833 | 96.5621 | 94.7976 | 95.6261 | 96.3959 | 96.5337 | 96.7113 | 96.9765 | 96.5186 | 2025-03-11
Hoymiles Power Electronics Inc. | MIS-500-1A-NA {208V} | N | Y | N | N | N | N | Y* | Y | 475 W, 208 Vac, Grid Support Utility Interactive Microinverter | 0.47956 | 208 | 96.5 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-16 | 2025-03-11 |  | N | Y | 0.02 |  |  | 32 | 40 | 48 | 0.047956 | 0.095911 | 0.14387 | 0.23978 | 0.35967 | 0.47956 | 94.3356 | 95.2717 | 95.3596 | 96.7151 | 96.7161 | 96.3012 | 96.3649 | 94.9961 | 95.791 | 95.6352 | 96.6208 | 96.9094 | 96.8833 | 96.5621 | 94.7976 | 95.6261 | 96.3959 | 96.5337 | 96.7113 | 96.9765 | 96.5186 | 2025-03-11
Hoymiles Power Electronics Inc. | MIS-500-1NA {208V} | N | Y | N | N | N | N | Y* | Y | 475 W, 208 Vac, Grid Support Utility Interactive Microinverter | 0.47956 | 208 | 96.5 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-16 | 2025-03-11 |  | N | Y | 0.02 |  |  | 32 | 40 | 48 | 0.047956 | 0.095911 | 0.14387 | 0.23978 | 0.35967 | 0.47956 | 94.3356 | 95.2717 | 95.3596 | 96.7151 | 96.7161 | 96.3012 | 96.3649 | 94.9961 | 95.791 | 95.6352 | 96.6208 | 96.9094 | 96.8833 | 96.5621 | 94.7976 | 95.6261 | 96.3959 | 96.5337 | 96.7113 | 96.9765 | 96.5186 | 2025-03-11
Hoymiles Power Electronics Inc. | HM-600N {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 590 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.591 | 240 | 96.5 | CSA Group | [3/15/2023] | CSA Group | [04/03/2020] | [V01.01.00] | 2020-05-11 | [04/03/2020] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 29 | 37 | 48 | 0.059145 | 0.11829 | 0.17743 | 0.29572 | 0.44358 | 0.59145 | 95.4668 | 96.1756 | 96.2278 | 96.4901 | 96.5298 | 96.1502 | 96.406 | 95.7931 | 96.0557 | 96.3854 | 96.3313 | 96.632 | 96.4892 | 96.4698 | 95.7024 | 95.9011 | 96.3892 | 96.1954 | 96.5933 | 96.5756 | 96.4141 | 2020-05-11 | 2023-04-21
Hoymiles Power Electronics Inc. | HM-600NT {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 590 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.591 | 240 | 96.5 | CSA Group | [3/15/2023] | CSA Group | [04/03/2020] | [V01.01.00] | 2020-05-11 | [04/03/2020] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 29 | 37 | 48 | 0.059145 | 0.11829 | 0.17743 | 0.29572 | 0.44358 | 0.59145 | 95.4668 | 96.1756 | 96.2278 | 96.4901 | 96.5298 | 96.1502 | 96.406 | 95.7931 | 96.0557 | 96.3854 | 96.3313 | 96.632 | 96.4892 | 96.4698 | 95.7024 | 95.9011 | 96.3892 | 96.1954 | 96.5933 | 96.5756 | 96.4141 | 2020-05-11 | 2023-04-21
Hoymiles Power Electronics Inc. | HMS-600-2D-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 590W, 240 Vac Grid Support Utility Interactive Microinverter | 0.591 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 29 | 37 | 48 | 0.059145 | 0.11829 | 0.17743 | 0.29572 | 0.44358 | 0.59145 | 95.4668 | 96.1756 | 96.2278 | 96.4901 | 96.5298 | 96.1502 | 96.406 | 95.7931 | 96.0557 | 96.3854 | 96.3313 | 96.632 | 96.4892 | 96.4698 | 95.7024 | 95.9011 | 96.3892 | 96.1954 | 96.5933 | 96.5756 | 96.4141 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-600-2T-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 590W, 240 Vac Grid Support Utility Interactive Microinverter | 0.591 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 29 | 37 | 48 | 0.059145 | 0.11829 | 0.17743 | 0.29572 | 0.44358 | 0.59145 | 95.4668 | 96.1756 | 96.2278 | 96.4901 | 96.5298 | 96.1502 | 96.406 | 95.7931 | 96.0557 | 96.3854 | 96.3313 | 96.632 | 96.4892 | 96.4698 | 95.7024 | 95.9011 | 96.3892 | 96.1954 | 96.5933 | 96.5756 | 96.4141 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-700-2T-NA {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 696W, 240 Vac Grid Support Utility Interactive Microinverter | 0.6422 | 240 | 96.5 | CSA Group | [1/18/2023] | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 33 | 42 | 48 | 0.06422 | 0.12844 | 0.19266 | 0.3211 | 0.48165 | 0.6422 | 94.7288 | 96.076 | 96.3794 | 96.4585 | 96.5234 | 96.0205 | 96.3732 | 94.7843 | 95.8032 | 96.4528 | 96.4633 | 96.4882 | 96.1174 | 96.3578 | 94.298 | 95.8059 | 96.3992 | 96.4927 | 96.4899 | 96.1241 | 96.3394 | 2021-03-01 | 2023-03-13
Hoymiles Power Electronics Inc. | MIS-700-2NA {240V} | N | Y | N | N | N | N | N | Y | 638 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.64712 | 240 | 96.5 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-06-02 |  | N | Y | 0.09 |  |  | 27 | 37 | 48 | 0.064712 | 0.12942 | 0.19414 | 0.32356 | 0.48534 | 0.64712 | 88.7677 | 94.4272 | 96.8589 | 96.9783 | 96.7842 | 96.9821 | 96.4053 | 89.45 | 94.7943 | 96.8857 | 96.9986 | 96.7529 | 96.97 | 96.4412 | 88.5814 | 94.1086 | 96.9986 | 97.0486 | 96.6971 | 97.0457 | 96.3705 | 2025-06-02
Hoymiles Power Electronics Inc. | HM-700N {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 696 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.697 | 240 | 96.5 | CSA Group | [3/15/2023] | CSA Group | [04/03/2020] | [V01.01.00] | 2020-05-11 | [04/03/2020] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 33 | 42 | 48 | 0.06975 | 0.1395 | 0.20925 | 0.34875 | 0.52312 | 0.6975 | 95.4666 | 96.1751 | 96.2274 | 96.4896 | 96.53 | 96.1505 | 96.406 | 95.7929 | 96.0559 | 96.3859 | 96.3322 | 96.632 | 96.4896 | 96.47 | 95.7024 | 95.901 | 96.3897 | 96.3322 | 96.5935 | 96.5753 | 96.443 | 2020-05-11 | 2023-04-21
Hoymiles Power Electronics Inc. | HM-700NT {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 696 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.697 | 240 | 96.5 | CSA Group | [3/15/2023] | CSA Group | [04/03/2020] | [V01.01.00] | 2020-05-11 | [04/03/2020] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 33 | 42 | 48 | 0.06975 | 0.1395 | 0.20925 | 0.34875 | 0.52312 | 0.6975 | 95.4666 | 96.1751 | 96.2274 | 96.4896 | 96.53 | 96.1505 | 96.406 | 95.7929 | 96.0559 | 96.3859 | 96.3322 | 96.632 | 96.4896 | 96.47 | 95.7024 | 95.901 | 96.3897 | 96.3322 | 96.5935 | 96.5753 | 96.443 | 2020-05-11 | 2023-04-21
Hoymiles Power Electronics Inc. | HMS-700-2D-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 696W, 240 Vac Grid Support Utility Interactive Microinverter | 0.697 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 33 | 42 | 48 | 0.06975 | 0.1395 | 0.20925 | 0.34875 | 0.52312 | 0.6975 | 95.4666 | 96.1751 | 96.2274 | 96.4896 | 96.53 | 96.1505 | 96.406 | 95.7929 | 96.0559 | 96.3859 | 96.3322 | 96.632 | 96.4896 | 96.47 | 95.7024 | 95.901 | 96.3897 | 96.3322 | 96.5935 | 96.5753 | 96.443 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-800-2T-NA {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 766W, 240 Vac Grid Support Utility Interactive Microinverter | 0.7262 | 240 | 96.5 | CSA Group | [1/18/2023] | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.07262 | 0.14524 | 0.21786 | 0.3631 | 0.54465 | 0.7262 | 94.7363 | 96.0459 | 96.3894 | 96.4669 | 96.5221 | 96.0704 | 96.3768 | 94.8038 | 95.8094 | 96.449 | 96.4808 | 96.5252 | 96.1175 | 96.3817 | 94.3481 | 95.7983 | 96.3887 | 96.4528 | 96.4904 | 96.1057 | 96.3308 | 2021-03-01 | 2023-03-13
Hoymiles Power Electronics Inc. | MIS-800-2NA {240V} | N | Y | N | N | N | N | N | Y | 720 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.72958 | 240 | 97 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-06-02 |  | N | Y | 0.09 |  |  | 28 | 38 | 48 | 0.072958 | 0.14592 | 0.21887 | 0.36479 | 0.54718 | 0.72958 | 94.2298 | 94.6646 | 96.6002 | 97.2804 | 97.4235 | 96.8417 | 96.9999 | 94.7086 | 95.1814 | 96.9029 | 97.1329 | 97.3629 | 96.8229 | 97.0171 | 95.8857 | 96.1429 | 97.3871 | 97.16 | 97.3114 | 96.62 | 97.1387 | 2025-06-02
Hoymiles Power Electronics Inc. | HM-800N {208V} | N | Y | N | N | N | N | Y* | Y | 766 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.767 | 208 | 96.5 | CSA Group | [3/15/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2021-01-26 | 2023-04-21 |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.07671 | 0.15342 | 0.23013 | 0.38355 | 0.57533 | 0.7671 | 94.7583 | 96.0685 | 96.3783 | 96.4713 | 96.5088 | 96.0574 | 96.3707 | 94.8184 | 95.8015 | 96.4279 | 96.4518 | 96.4948 | 96.1343 | 96.358 | 94.3079 | 95.7956 | 96.3964 | 96.4624 | 96.4815 | 96.0999 | 96.327 | 2023-04-21
Hoymiles Power Electronics Inc. | HM-800N {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 766 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.767 | 240 | 96.5 | CSA Group | [3/15/2023] | CSA Group | [04/03/2020] | [V01.01.00] | 2020-05-11 | [04/03/2020] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.076709 | 0.15342 | 0.23013 | 0.38354 | 0.57532 | 0.76709 | 95.467 | 96.1734 | 96.2274 | 96.4901 | 96.6946 | 96.1498 | 96.4932 | 95.7932 | 96.0559 | 96.3844 | 96.3319 | 96.7007 | 96.4903 | 96.5062 | 95.7028 | 95.9016 | 96.4122 | 96.1946 | 96.7005 | 96.575 | 96.4735 | 2020-05-11 | 2023-04-21
Hoymiles Power Electronics Inc. | HM-800NT {208V} | N | Y | N | N | N | N | Y* | Y | 766 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.767 | 208 | 96.5 | CSA Group | [3/15/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2021-01-26 | 2023-04-21 |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.07671 | 0.15342 | 0.23013 | 0.38355 | 0.57533 | 0.7671 | 94.7583 | 96.0685 | 96.3783 | 96.4713 | 96.5088 | 96.0574 | 96.3707 | 94.8184 | 95.8015 | 96.4279 | 96.4518 | 96.4948 | 96.1343 | 96.358 | 94.3079 | 95.7956 | 96.3964 | 96.4624 | 96.4815 | 96.0999 | 96.327 | 2023-04-21
Hoymiles Power Electronics Inc. | HM-800NT {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 766 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.767 | 240 | 96.5 | CSA Group | [3/15/2023] | CSA Group | [04/03/2020] | [V01.01.00] | 2020-05-11 | [04/03/2020] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.076709 | 0.15342 | 0.23013 | 0.38354 | 0.57532 | 0.76709 | 95.467 | 96.1734 | 96.2274 | 96.4901 | 96.6946 | 96.1498 | 96.4932 | 95.7932 | 96.0559 | 96.3844 | 96.3319 | 96.7007 | 96.4903 | 96.5062 | 95.7028 | 95.9016 | 96.4122 | 96.1946 | 96.7005 | 96.575 | 96.4735 | 2020-05-11 | 2023-04-21
Hoymiles Power Electronics Inc. | HMS-800-2D-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 766W, 240 Vac Grid Support Utility Interactive Microinverter | 0.767 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.076709 | 0.15342 | 0.23013 | 0.38354 | 0.57532 | 0.76709 | 95.467 | 96.1734 | 96.2274 | 96.4901 | 96.6946 | 96.1498 | 96.4932 | 95.7932 | 96.0559 | 96.3844 | 96.3319 | 96.7007 | 96.4903 | 96.5062 | 95.7028 | 95.9016 | 96.4122 | 96.1946 | 96.7005 | 96.575 | 96.4735 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-900-2T-NA {240V} | N | Y | N | N | N | N | Y* | Y | 820W, 240Vac Grid Support Utility Interactive Microinverter | 0.82731 | 240 | 96.5 | CSA Group | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-02-15 | 2023-03-13 |  | N | Y | 0.11 |  |  | 36 | 42 | 48 | 0.082731 | 0.16546 | 0.24819 | 0.41366 | 0.62048 | 0.82731 | 95.1144 | 96.0483 | 96.37 | 96.4585 | 96.5257 | 96.0684 | 96.3897 | 94.8177 | 95.7894 | 96.4261 | 96.4516 | 96.4927 | 96.1351 | 96.3561 | 94.2417 | 95.779 | 96.382 | 96.5126 | 96.4859 | 96.1371 | 96.3365 | 2023-03-13
Hoymiles Power Electronics Inc. | MIS-900-2NA {240V} | N | Y | N | N | N | N | N | Y | 820 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.82978 | 240 | 97 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-06-02 |  | N | Y | 0.09 |  |  | 30 | 39 | 48 | 0.082978 | 0.16596 | 0.24893 | 0.41489 | 0.62234 | 0.82978 | 94.9273 | 95.8313 | 97.164 | 96.8748 | 97.4356 | 95.3502 | 97.0004 | 95.3056 | 95.974 | 97.2487 | 97.0639 | 97.3715 | 96.0931 | 97.0757 | 95.5099 | 96.3888 | 97.2361 | 97.0361 | 97.3536 | 96.4921 | 97.1078 | 2025-06-02
Hoymiles Power Electronics Inc. | MIS-1000-2NA {208V} | N | Y | N | N | N | N | N | Y | 958 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.96094 | 208 | 96.5 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-06-02 |  | N | Y | 0.07 |  |  | 32 | 40 | 48 | 0.096094 | 0.19219 | 0.28828 | 0.48047 | 0.7207 | 0.96094 | 95.2071 | 96.8729 | 96.6457 | 96.8529 | 96.68 | 95.5029 | 96.6041 | 95.9271 | 96.7454 | 96.6795 | 96.8973 | 96.5991 | 95.6994 | 96.6068 | 96.1114 | 96.7071 | 96.7829 | 96.8814 | 96.3871 | 95.8271 | 96.5154 | 2025-06-02
Hoymiles Power Electronics Inc. | MIS-1000-2NA {240V} | N | Y | N | N | N | N | N | Y | 958 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.96476 | 240 | 97 | CSA Group | [1/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-06-02 |  | N | Y | 0.1 |  |  | 32 | 40 | 48 | 0.096476 | 0.19295 | 0.28943 | 0.48238 | 0.72357 | 0.96476 | 95.0014 | 97.3043 | 97.3843 | 97.3971 | 97.1043 | 96.6743 | 97.1038 | 96.12 | 97.3471 | 97.3457 | 97.3271 | 96.9471 | 96.2 | 97.0243 | 96.1957 | 97.3843 | 97.3529 | 97.5 | 96.9371 | 96.2786 | 97.065 | 2025-06-02
Hoymiles Power Electronics Inc. | HMS-1000-2T-NA {208V} | N | Y | N | N | N | N | Y* | Y | 958W, 208Vac Grid Support Utility Interactive Microinverter | 0.96521 | 208 | 96.5 | CSA Group | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-02-15 | 2023-03-13 |  | N | Y | 0.11 |  |  | 38 | 42 | 48 | 0.096521 | 0.19304 | 0.28956 | 0.4826 | 0.72391 | 0.96521 | 94.7004 | 96.0376 | 96.3562 | 96.456 | 96.497 | 96.0474 | 96.3542 | 94.7845 | 95.7831 | 96.4141 | 96.4416 | 96.4864 | 96.1267 | 96.3471 | 94.2501 | 95.7772 | 96.3822 | 96.4522 | 96.4731 | 96.0923 | 96.3151 | 2023-03-13
Hoymiles Power Electronics Inc. | HMS-1000-2T-NA {240V} | N | Y | N | N | N | N | Y* | Y | 958W, 240Vac Grid Support Utility Interactive Microinverter | 0.967 | 240 | 96.5 | CSA Group | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-02-15 | 2023-03-13 |  | N | Y | 0.11 |  |  | 38 | 42 | 48 | 0.09667 | 0.19334 | 0.29001 | 0.48335 | 0.72503 | 0.9667 | 94.7004 | 96.0376 | 96.3562 | 96.456 | 96.497 | 96.0474 | 96.3542 | 94.7845 | 95.7831 | 96.4141 | 96.4416 | 96.4864 | 96.1267 | 96.3471 | 94.2501 | 95.7772 | 96.3822 | 96.4522 | 96.4731 | 96.0923 | 96.3151 | 2023-03-13
Hoymiles Power Electronics Inc. | HM-1000N {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.0 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.985 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 32 | 40 | 48 | 0.095806 | 0.19161 | 0.28742 | 0.47903 | 0.71854 | 0.95806 | 95.815 | 96.1851 | 96.2672 | 96.6194 | 96.5502 | 96.1507 | 96.4632 | 95.9365 | 96.1559 | 96.3958 | 96.552 | 96.6254 | 96.1894 | 96.5096 | 95.783 | 96.0056 | 96.4296 | 96.3542 | 96.6506 | 96.5455 | 96.4896 | 2021-03-01
Hoymiles Power Electronics Inc. | HM-1000NT {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.0 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.985 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 32 | 40 | 48 | 0.095806 | 0.19161 | 0.28742 | 0.47903 | 0.71854 | 0.95806 | 95.815 | 96.1851 | 96.2672 | 96.6194 | 96.5502 | 96.1507 | 96.4632 | 95.9365 | 96.1559 | 96.3958 | 96.552 | 96.6254 | 96.1894 | 96.5096 | 95.783 | 96.0056 | 96.4296 | 96.3542 | 96.6506 | 96.5455 | 96.4896 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-1000-4D-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 985 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.985 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 32 | 40 | 48 | 0.095806 | 0.19161 | 0.28742 | 0.47903 | 0.71854 | 0.95806 | 95.815 | 96.1851 | 96.2672 | 96.6194 | 96.5502 | 96.1507 | 96.4632 | 95.9365 | 96.1559 | 96.3958 | 96.552 | 96.6254 | 96.1894 | 96.5096 | 95.783 | 96.0056 | 96.4296 | 96.3542 | 96.6506 | 96.5455 | 96.4896 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-1000-4T-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.0 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.985 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 32 | 40 | 48 | 0.095806 | 0.19161 | 0.28742 | 0.47903 | 0.71854 | 0.95806 | 95.815 | 96.1851 | 96.2672 | 96.6194 | 96.5502 | 96.1507 | 96.4632 | 95.9365 | 96.1559 | 96.3958 | 96.552 | 96.6254 | 96.1894 | 96.5096 | 95.783 | 96.0056 | 96.4296 | 96.3542 | 96.6506 | 96.5455 | 96.4896 | 2021-03-01
Hoymiles Power Electronics Inc. | HM-1000 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.0 kW, 240 Vac Grid Support Utility Interactive Microinverters | 1.032 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2019-10-15 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.03 |  |  | 27 | 37 | 48 | 0.10324 | 0.20649 | 0.30973 | 0.51622 | 0.77433 | 1.0324 | 95.6081 | 96.4152 | 96.5362 | 96.4505 | 96.7161 | 96.3963 | 96.5634 | 96.0046 | 96.2823 | 96.573 | 96.6487 | 96.7153 | 96.605 | 96.6286 | 95.8394 | 96.0883 | 96.3396 | 96.6799 | 96.7142 | 96.6125 | 96.5907 | 2019-10-15 | 2021-03-01
Hoymiles Power Electronics Inc. | HM-1000T {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.0 kW, 240 Vac Grid Support Utility Interactive Microinverters | 1.032 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2019-10-15 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.03 |  |  | 27 | 37 | 48 | 0.10324 | 0.20649 | 0.30973 | 0.51622 | 0.77433 | 1.0324 | 95.6081 | 96.4152 | 96.5362 | 96.4505 | 96.7161 | 96.3963 | 96.5634 | 96.0046 | 96.2823 | 96.573 | 96.6487 | 96.7153 | 96.605 | 96.6286 | 95.8394 | 96.0883 | 96.3396 | 96.6799 | 96.7142 | 96.6125 | 96.5907 | 2019-10-15 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-1000-4D {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.0 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.032 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.03 |  |  | 27 | 37 | 48 | 0.10324 | 0.20649 | 0.30973 | 0.51622 | 0.77433 | 1.0324 | 95.6081 | 96.4152 | 96.5362 | 96.4505 | 96.7161 | 96.3963 | 96.5634 | 96.0046 | 96.2823 | 96.573 | 96.6487 | 96.7153 | 96.605 | 96.6286 | 95.8394 | 96.0883 | 96.3396 | 96.6799 | 96.7142 | 96.6125 | 96.5907 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-1000-4T {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.0 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.032 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.03 |  |  | 27 | 37 | 48 | 0.10324 | 0.20649 | 0.30973 | 0.51622 | 0.77433 | 1.0324 | 95.6081 | 96.4152 | 96.5362 | 96.4505 | 96.7161 | 96.3963 | 96.5634 | 96.0046 | 96.2823 | 96.573 | 96.6487 | 96.7153 | 96.605 | 96.6286 | 95.8394 | 96.0883 | 96.3396 | 96.6799 | 96.7142 | 96.6125 | 96.5907 | 2021-03-01
Hoymiles Power Electronics Inc. | HM-1200 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.2 kW, 240 Vac Grid Support Utility Interactive Microinverters | 1.213 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2019-10-15 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.01461 |  |  | 32 | 40 | 48 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 96.2758 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 96.4351 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013 | 96.3737 | 2019-10-15 | 2021-03-01
Hoymiles Power Electronics Inc. | HM-1200N {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.213 | 240 | 96.5 | CSA | [6/6/2023] | CSA Group | [03/12/2020] | [V01.01.00] | 2020-05-11 | [03/12/2020] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.01461 |  |  | 32 | 40 | 48 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 96.2758 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 96.4351 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013 | 96.3737 | 2020-05-11 | 2023-08-11
Hoymiles Power Electronics Inc. | HM-1200NT {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.213 | 240 | 96.5 | CSA | [6/6/2023] | CSA Group | [03/12/2020] | [V01.01.00] | 2020-05-11 | [03/12/2020] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.01461 |  |  | 32 | 40 | 48 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 96.2758 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 96.4351 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013 | 96.3737 | 2020-05-11 | 2023-08-11
Hoymiles Power Electronics Inc. | HM-1200T {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.2 kW, 240 Vac Grid Support Utility Interactive Microinverters | 1.213 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2019-10-15 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.01461 |  |  | 32 | 40 | 48 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 96.2758 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 96.4351 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013 | 96.3737 | 2019-10-15 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-1200-4D {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.213 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.01461 |  |  | 32 | 40 | 48 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 96.2758 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 96.4351 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013 | 96.3737 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-1200-4D-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.213 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.01461 |  |  | 32 | 40 | 48 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 96.2758 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 96.4351 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013 | 96.3737 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-1200-4T {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.213 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.01461 |  |  | 32 | 40 | 48 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 96.2758 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 96.4351 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013 | 96.3737 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-1200-4T-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.2 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.213 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.01461 |  |  | 32 | 40 | 48 | 0.12132 | 0.24264 | 0.36395 | 0.60659 | 0.90989 | 1.2132 | 95.813 | 96.1105 | 96.2544 | 96.6096 | 96.2797 | 95.4203 | 96.2758 | 95.8493 | 96.168 | 96.2843 | 96.5421 | 96.5331 | 96.0437 | 96.4351 | 95.3869 | 95.9598 | 96.2058 | 96.321 | 96.553 | 96.3013 | 96.3737 | 2021-03-01
Hoymiles Power Electronics Inc. | HMT-1600-4T-208-NA {208V} | N | Y | N | N | N | N | Y* | Y | 1440 W, 208 Vac Grid Support Utility Interactive Microinverter | 1.438 | 208 | 96.5 | CSA Group | [9/11/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-12-15 | 2024-02-01 |  | N | Y | 0.1559 |  |  | 28 | 38 | 48 | 0.144 | 0.288 | 0.432 | 0.719 | 1.079 | 1.438 | 93.48 | 95.66 | 96.42 | 96.71 | 96.77 | 95.74 | 96.48 | 93.38 | 95.06 | 96.12 | 96.75 | 96.89 | 96 | 96.49 | 92.85 | 95.12 | 96.18 | 96.81 | 96.82 | 96.33 | 96.47 | 2024-02-01
Hoymiles Power Electronics Inc. | HM-1500N {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 1.438 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.439 | 240 | 96.5 | CSA | [6/6/2023] | CSA Group | [03/12/2020] | [V01.01.00] | 2020-05-11 | [03/12/2020] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 36 | 42 | 48 | 0.1439 | 0.2878 | 0.4317 | 0.7195 | 1.0793 | 1.439 | 95.475 | 96.1751 | 96.2272 | 96.4894 | 96.5302 | 96.1507 | 96.4064 | 95.7865 | 96.0559 | 96.3858 | 96.332 | 96.6319 | 96.4894 | 96.4696 | 95.703 | 95.9005 | 96.3909 | 96.1942 | 96.5937 | 96.5755 | 96.4142 | 2020-05-11 | 2023-08-11
Hoymiles Power Electronics Inc. | HM-1500NT {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 1.438 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.439 | 240 | 96.5 | CSA | [6/6/2023] | CSA Group | [03/12/2020] | [V01.01.00] | 2020-05-11 | [03/12/2020] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 36 | 42 | 48 | 0.1439 | 0.2878 | 0.4317 | 0.7195 | 1.0793 | 1.439 | 95.475 | 96.1751 | 96.2272 | 96.4894 | 96.5302 | 96.1507 | 96.4064 | 95.7865 | 96.0559 | 96.3858 | 96.332 | 96.6319 | 96.4894 | 96.4696 | 95.703 | 95.9005 | 96.3909 | 96.1942 | 96.5937 | 96.5755 | 96.4142 | 2020-05-11 | 2023-08-11
Hoymiles Power Electronics Inc. | HMS-1500-4D-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.438 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.439 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 36 | 42 | 48 | 0.1439 | 0.2878 | 0.4317 | 0.7195 | 1.0793 | 1.439 | 95.475 | 96.1751 | 96.2272 | 96.4894 | 96.5302 | 96.1507 | 96.4064 | 95.7865 | 96.0559 | 96.3858 | 96.332 | 96.6319 | 96.4894 | 96.4696 | 95.703 | 95.9005 | 96.3909 | 96.1942 | 96.5937 | 96.5755 | 96.4142 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-1500-4T-NA {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.5 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.439 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.11 |  |  | 36 | 42 | 48 | 0.1439 | 0.2878 | 0.4317 | 0.7195 | 1.0793 | 1.439 | 95.475 | 96.1751 | 96.2272 | 96.4894 | 96.5302 | 96.1507 | 96.4064 | 95.7865 | 96.0559 | 96.3858 | 96.332 | 96.6319 | 96.4894 | 96.4696 | 95.703 | 95.9005 | 96.3909 | 96.1942 | 96.5937 | 96.5755 | 96.4142 | 2021-03-01
Hoymiles Power Electronics Inc. | HM-1500N {208V} | N | Y | N | N | N | N | N | Y | 1.438 kW, 208 Vac Grid Support Utility Interactive Microinverter | 1.44 | 208 | 96.5 | CSA | [6/6/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2021-08-12 |  | N | Y | 0.01461 |  |  | 36 | 42 | 48 | 0.144 | 0.288 | 0.432 | 0.72 | 1.08 | 1.44 | 94.73 | 96.06 | 96.37 | 96.47 | 96.51 | 96.05 | 96.37 | 94.82 | 95.8 | 96.43 | 96.45 | 96.49 | 96.13 | 96.36 | 94.28 | 95.8 | 96.4 | 96.46 | 96.48 | 96.1 | 96.33 | 2023-08-11 | 2024-01-22
Hoymiles Power Electronics Inc. | HM-1500NT {208V} | N | Y | N | N | N | N | N | Y | 1.438 kW, 208 Vac Grid Support Utility Interactive Microinverter | 1.44 | 208 | 96.5 | CSA | [6/6/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2021-08-12 |  | N | Y | 0.01461 |  |  | 36 | 42 | 48 | 0.144 | 0.288 | 0.432 | 0.72 | 1.08 | 1.44 | 94.73 | 96.06 | 96.37 | 96.47 | 96.51 | 96.05 | 96.37 | 94.82 | 95.8 | 96.43 | 96.45 | 96.49 | 96.13 | 96.36 | 94.28 | 95.8 | 96.4 | 96.46 | 96.48 | 96.1 | 96.33 | 2023-08-11 | 2024-01-22
Hoymiles Power Electronics Inc. | HMS-1600-4T-NA {240V} | N | Y | N | N | N | N | Y* | Y | 1440 W, 240 Vac Grid Support Utility Interactive Microinverter | 1.447 | 240 | 96.5 | CSA Group | [11/10/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-01-29 | 2023-02-21 |  | N | Y | 0.11 |  |  | 29 | 42 | 48 | 0.14472 | 0.28944 | 0.43415 | 0.72359 | 1.0854 | 1.4472 | 94.6961 | 96.0527 | 96.3843 | 96.4744 | 96.5176 | 96.0288 | 96.372 | 94.7366 | 95.7868 | 96.4262 | 96.4529 | 96.5031 | 96.1136 | 96.3574 | 94.2175 | 95.7975 | 96.3803 | 96.4615 | 96.4814 | 96.1025 | 96.3214 | 2023-02-21
Hoymiles Power Electronics Inc. | HM-1500 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.5 kW, 240 Vac Grid Support Utility Interactive Microinverters | 1.551 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2019-10-15 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.03 |  |  | 36 | 42 | 48 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 96.5592 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 96.4894 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591 | 96.4346 | 2019-10-15 | 2021-03-01
Hoymiles Power Electronics Inc. | HM-1500T {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.5 kW, 240 Vac Grid Support Utility Interactive Microinverters | 1.551 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2019-10-15 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.03 |  |  | 36 | 42 | 48 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 96.5592 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 96.4894 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591 | 96.4346 | 2019-10-15 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-1500-4D {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.5 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.551 | 240 | 95.6 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.03 |  |  | 36 | 42 | 48 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 96.5592 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 96.4894 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591 | 96.4346 | 2021-03-01
Hoymiles Power Electronics Inc. | HMS-1500-4T {240V} | N | N | Y | Y | Y | Y | Y* | Y | 1.5 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.551 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2021] | [V01.01.00] | 2021-03-01 | [01/29/2021] | 2021-03-01 | CSA Group | 2021-01-26 | 2021-03-01 |  | N | Y | 0.03 |  |  | 36 | 42 | 48 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 96.5592 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 96.4894 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591 | 96.4346 | 2021-03-01
Hoymiles Power Electronics Inc. | THM-1500 {240V} | N | N | Y | Y | Y | N | N | N | 1.5 kW, 240 Vac Grid Support Utility Interactive Microinverters | 1.551 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [03/12/2020] | [V01.01.00] | 2020-05-21 | [03/12/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.03 |  |  | 36 | 42 | 48 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 96.5592 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 96.4894 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591 | 96.4346 | 2020-05-21 | 2021-01-11
Hoymiles Power Electronics Inc. | HMS-1800-4T-NA {240V} | N | Y | N | N | N | N | Y* | Y | 1660 W, 240 Vac Grid Support Utility Interactive Microinverter | 1.668 | 240 | 96.5 | CSA Group | [11/10/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-01-29 | 2023-02-21 |  | N | Y | 0.11 |  |  | 32 | 42 | 48 | 0.16683 | 0.33366 | 0.50048 | 0.83414 | 1.2512 | 1.6683 | 94.6864 | 96.0431 | 96.3746 | 96.4648 | 96.508 | 96.0191 | 96.3623 | 94.7275 | 95.7773 | 96.4166 | 96.4432 | 96.4935 | 96.1039 | 96.3478 | 94.2081 | 95.7879 | 96.3707 | 96.4518 | 96.4717 | 96.0929 | 96.3117 | 2023-02-21
Hoymiles Power Electronics Inc. | HMT-1800-4T-208-NA {208V} | N | Y | N | N | N | N | Y* | Y | 1728 W, 208 Vac Grid Support Utility Interactive Microinverter | 1.726 | 208 | 96.5 | CSA Group | [9/11/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-12-15 | 2024-02-01 |  | N | Y | 0.176 |  |  | 31 | 39.5 | 48 | 0.173 | 0.345 | 0.518 | 0.863 | 1.294 | 1.726 | 94.21 | 95.99 | 96.48 | 96.53 | 96.84 | 95.81 | 96.53 | 94.07 | 95.55 | 96.6 | 96.73 | 96.76 | 95.34 | 96.5 | 94.13 | 95.31 | 96.29 | 96.78 | 96.75 | 96 | 96.49 | 2024-02-01
Hoymiles Power Electronics Inc. | HMT-2000-4T-208-NA {208V} | N | Y | N | N | N | N | Y* | Y | 1918 W, 208 Vac Grid Support Utility Interactive Microinverter | 1.919 | 208 | 96.5 | CSA Group | [9/11/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-12-15 | 2024-02-01 |  | N | Y | 0.176 |  |  | 32 | 40 | 48 | 0.192 | 0.384 | 0.576 | 0.959 | 1.439 | 1.919 | 93.79 | 96.21 | 96.54 | 96.5 | 96.78 | 95.68 | 96.49 | 95.29 | 95.81 | 96.35 | 96.73 | 96.74 | 95.1 | 96.5 | 93.33 | 95.34 | 96.61 | 96.83 | 96.77 | 95.56 | 96.49 | 2024-02-01
Hoymiles Power Electronics Inc. | HMS-2000-4T-NA {208V} | N | Y | N | N | N | N | Y* | Y | 1918 W, 208 Vac Grid Support Utility Interactive Microinverter | 1.926 | 208 | 96.5 | CSA Group | [11/10/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-01-29 | 2023-02-21 |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.19262 | 0.38524 | 0.57785 | 0.96309 | 1.4446 | 1.9262 | 94.6588 | 96.017 | 96.3472 | 96.4366 | 96.4795 | 95.9909 | 96.3342 | 94.6994 | 95.7512 | 96.3902 | 96.4151 | 96.4651 | 96.0758 | 96.3198 | 94.176 | 95.762 | 96.3436 | 96.4237 | 96.4435 | 96.0647 | 96.2836 | 2023-02-21
Hoymiles Power Electronics Inc. | HMS-2000-4T-NA {240V} | N | Y | N | N | N | N | Y* | Y | 1918 W, 240 Vac Grid Support Utility Interactive Microinverter | 1.928 | 240 | 96.5 | CSA Group | [11/10/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-01-29 | 2023-02-21 |  | N | Y | 0.11 |  |  | 34 | 42 | 48 | 0.19277 | 0.38554 | 0.5783 | 0.96384 | 1.4458 | 1.9277 | 94.6771 | 96.0335 | 96.365 | 96.4551 | 96.4982 | 96.0095 | 96.3526 | 94.7177 | 95.7677 | 96.4076 | 96.4336 | 96.4837 | 96.0943 | 96.3382 | 94.1943 | 95.7784 | 96.3611 | 96.4422 | 96.4621 | 96.0832 | 96.302 | 2023-02-21
Hoymiles Power Electronics Inc. | HYS-3.8LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 3.796 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 6.0401 |  |  | 300 | 380 | 480 | 0.37958 | 0.75916 | 1.1387 | 1.8979 | 2.8468 | 3.7958 | 92.5517 | 95.5966 | 96.419 | 96.9105 | 97.0723 | 97.0287 | 96.7032 | 93.2466 | 96.7006 | 97.2174 | 97.4939 | 97.5869 | 97.5544 | 97.3035 | 93.268 | 96.0331 | 96.8384 | 97.1796 | 97.3381 | 97.3158 | 97.0157 | 2024-02-01 | 2025-08-01
Hoymiles Power Electronics Inc. | HYS-4.8LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 4.8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 4.793 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 5.7606 |  |  | 300 | 380 | 480 | 0.47929 | 0.95858 | 1.4379 | 2.3964 | 3.5947 | 4.7929 | 94.0767 | 96.1362 | 96.6912 | 97.0212 | 97.0575 | 96.9337 | 96.8344 | 95.4316 | 97.1034 | 97.3546 | 97.5695 | 97.5695 | 97.4739 | 97.4301 | 94.3738 | 96.5934 | 96.9723 | 97.2727 | 97.3154 | 97.2367 | 97.1075 | 2024-02-01 | 2025-08-01
Hoymiles Power Electronics Inc. | HYS-6.0LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 6.0 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 5.995 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 5.8237 |  |  | 300 | 380 | 480 | 0.59951 | 1.199 | 1.7985 | 2.9976 | 4.4963 | 5.9951 | 94.8234 | 96.5478 | 96.8698 | 97.0713 | 96.9873 | 96.7883 | 96.8723 | 96.0891 | 97.2705 | 97.4671 | 97.5855 | 97.504 | 97.3496 | 97.4407 | 95.3019 | 96.89 | 97.1313 | 97.3238 | 97.2572 | 97.1052 | 97.1519 | 2024-02-01 | 2025-08-01
Hoymiles Power Electronics Inc. | HYS-7.6LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 7.708 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 6.1397 |  |  | 300 | 380 | 480 | 0.77079 | 1.5416 | 2.3124 | 3.8539 | 5.7809 | 7.7079 | 94.8322 | 96.4779 | 96.907 | 97.1091 | 97.0333 | 96.6304 | 96.8981 | 96.482 | 97.3997 | 97.6208 | 97.6611 | 97.5217 | 97.3094 | 97.5045 | 95.5348 | 96.8788 | 97.1848 | 97.3224 | 97.2171 | 97.0689 | 97.1437 | 2024-02-01 | 2025-08-01
Hoymiles Power Electronics Inc. | HYS-9.6LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 9.641 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 6.8588 |  |  | 300 | 380 | 480 | 0.96413 | 1.9283 | 2.8924 | 4.8206 | 7.231 | 9.6413 | 95.7062 | 96.8422 | 97.1011 | 97.1182 | 96.9178 | 96.4094 | 96.9042 | 96.6936 | 97.4649 | 97.6066 | 97.5483 | 97.3476 | 97.0572 | 97.386 | 96.301 | 97.1806 | 97.3628 | 97.3361 | 97.1168 | 96.8368 | 97.149 | 2024-02-01 | 2025-08-01
Hoymiles Power Electronics Inc. | HYS-11.5LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 11.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 11.575 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 6.6304 |  |  | 300 | 380 | 480 | 1.1575 | 2.3151 | 3.4726 | 5.7877 | 8.6815 | 11.5754 | 95.9907 | 97.1161 | 97.298 | 97.2213 | 96.8983 | 96.5184 | 96.9697 | 97.1958 | 97.7715 | 97.7755 | 97.4974 | 97.2422 | 96.8577 | 97.3652 | 96.6169 | 97.42 | 97.5383 | 97.4007 | 97.0634 | 96.7187 | 97.174 | 2024-02-01 | 2025-08-01
Huawei Technologies Co., Ltd. | SUN2000-3.8KTL-USL0 {240V} | N | N | Y | Y | Y | N | N | N | 3.8 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 3.8 | 240 | 99 | No Information Submitted | No Information Submitted | UL | [06/14/2018] | [V100R001D00] | 2019-01-15 | [06/14/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 2.18 |  |  | 370 | 395 | 420 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 96.375 | 98.2332 | 98.6641 | 99.0028 | 99.0572 | 99.0776 | 98.8512 | 96.1637 | 98.1176 | 98.4788 | 98.9469 | 99.0231 | 99.0365 | 98.7828 | 96.0702 | 97.9945 | 98.4563 | 98.8641 | 98.9923 | 98.9967 | 98.7345 | 2018-07-16 | 2019-01-15
Huawei Technologies Co., Ltd. | SUN2000-5KTL-USL0 {240V} | N | N | Y | Y | Y | N | N | N | 5 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 5 | 240 | 99 | No Information Submitted | No Information Submitted | UL | [06/14/2018] | [V100R001D00] | 2019-01-15 | [06/14/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 2.07 |  |  | 370 | 395 | 420 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 97.0703 | 98.3856 | 98.7211 | 99.0239 | 99.0199 | 98.8703 | 98.8677 | 96.8811 | 98.3814 | 98.661 | 98.9319 | 98.966 | 98.8203 | 98.8023 | 96.6926 | 98.2929 | 98.5924 | 98.8825 | 98.8862 | 98.7742 | 98.7272 | 2018-07-16 | 2019-01-15
Huawei Technologies Co., Ltd. | SUN2000-7.6KTL-USL0 {240V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 7.6 | 240 | 99 | No Information Submitted | No Information Submitted | UL | [06/14/2018] | [V100R001D00] | 2019-01-15 | [06/14/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 2.06 |  |  | 370 | 395 | 420 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 98.0246 | 98.8109 | 98.9586 | 98.9973 | 98.9182 | 98.749 | 98.8901 | 97.8253 | 98.7187 | 98.917 | 98.9382 | 98.8674 | 98.7164 | 98.8316 | 97.6925 | 98.6266 | 98.8792 | 98.9113 | 98.8473 | 98.6766 | 98.7988 | 2018-07-16 | 2019-01-15
Huawei Technologies Co., Ltd. | SUN2000-9KTL-USL0 {240V} | N | N | Y | Y | Y | N | N | N | 9 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 9 | 240 | 99 | No Information Submitted | No Information Submitted | UL | [06/14/2018] | [V100R001D00] | 2018-10-15 | [06/14/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.97 |  |  | 370 | 395 | 420 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 97.6847 | 98.6455 | 98.9199 | 99.0618 | 99.0359 | 98.9738 | 98.9507 | 97.5338 | 98.5959 | 98.9052 | 99.0405 | 99.016 | 98.932 | 98.9233 | 97.5773 | 98.5984 | 98.8583 | 99.0241 | 99.0091 | 98.9183 | 98.9118 | 2018-07-16 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-10KTL-USL0 {240V} | N | N | Y | Y | Y | N | N | N | 10 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 10 | 240 | 99 | No Information Submitted | No Information Submitted | UL | [06/14/2018] | [V100R001D00] | 2018-10-15 | [06/14/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.98 |  |  | 370 | 395 | 420 | 1 | 2 | 3 | 5 | 7.5 | 10 | 97.6401 | 98.656 | 98.9366 | 99.0483 | 99.013 | 98.9033 | 98.933 | 97.4485 | 98.548 | 98.8594 | 99.0041 | 98.9773 | 98.8792 | 98.8813 | 97.1851 | 98.4207 | 98.7677 | 98.933 | 98.9378 | 98.845 | 98.8158 | 2018-07-16 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-11.4KTL-USL0 {240V} | N | N | Y | Y | Y | N | N | N | 11.4 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 11.4 | 240 | 99 | No Information Submitted | No Information Submitted | UL | [06/14/2018] | [V100R001D00] | 2018-10-15 | [06/14/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.97 |  |  | 370 | 395 | 420 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 97.8855 | 98.7855 | 98.9735 | 99.0471 | 98.9836 | 98.8375 | 98.9346 | 97.7154 | 98.6539 | 98.9173 | 98.9881 | 98.9407 | 98.8014 | 98.8775 | 97.5395 | 98.5822 | 98.8395 | 98.9436 | 98.9124 | 98.7749 | 98.8319 | 2018-07-16 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-25KTL-US {480V} | N | N | Y | Y | Y | N | N | N | 25kW, 480Vac, 3-phase transformerless Grid Support Utility Interactive Inverter | 25 | 480 | 98 | No Information Submitted | No Information Submitted | CSA Group | [12/29/2018] | [SUN2000 V200 R001] | 2019-05-01 | [12/29/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 560 | 730 | 800 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 95.7 | 97.1 | 97.6 | 97.9 | 97.9 | 97.9 | 97.7 | 96.3 | 97.7 | 98.2 | 98.4 | 98.4 | 98.4 | 98.3 | 95.9 | 97.5 | 98 | 98.3 | 98.3 | 98.3 | 98.1 | 2019-05-01
Huawei Technologies Co., Ltd. | SUN2000-30KTL-US {480V} | N | N | Y | Y | Y | N | N | N | 30kW, 480Vac, 3-phase transformerless Grid Support Utility Interactive Inverter | 30 | 480 | 98 | No Information Submitted | No Information Submitted | CSA Group | [12/29/2018] | [SUN2000 V200 R001] | 2019-05-01 | [12/29/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1 |  |  | 560 | 730 | 800 | 3 | 6 | 9 | 15 | 22.5 | 30 | 96.1 | 97.4 | 97.7 | 97.9 | 97.9 | 97.8 | 97.8 | 96.6 | 97.9 | 98.3 | 98.4 | 98.4 | 98.3 | 98.3 | 96.4 | 97.8 | 98.2 | 98.3 | 98.3 | 98.2 | 98.2 | 2019-05-01
Huawei Technologies Co., Ltd. | SUN2000-33KTL-US {480V} | N | N | Y | Y | Y | N | N | N | 33 kW, 480 Vac, transformerless Grid Support Utility Interactive Inverter | 33 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [3/22/2017] | [SUN2000 V200 R002C20] | 2018-10-15 | [3/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1.8 |  |  | 460 | 720 | 850 | 3.3 | 6.6 | 9.9 | 16.5 | 24.75 | 33 | 95.6305 | 97.31 | 97.6239 | 97.8333 | 97.8889 | 97.7881 | 97.7211 | 97.5169 | 98.6741 | 98.8513 | 98.8841 | 98.8741 | 98.7894 | 98.8049 | 96.9145 | 98.1094 | 98.38 | 98.4576 | 98.4622 | 98.3838 | 98.3679 | 2017-11-01 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-36KTL-US {480V} | N | N | Y | Y | Y | N | N | N | 36 kW, 480 Vac, Transformerlss Grid Support Utility Interactive Inverter | 36 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [3/22/2017] | [SUN2000 V200 R002C20] | 2018-10-15 | [3/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1.8 |  |  | 490 | 720 | 850 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 96.4077 | 97.5458 | 97.8137 | 97.9912 | 97.9878 | 97.8775 | 97.8768 | 97.9739 | 98.7413 | 98.8734 | 98.8955 | 98.8578 | 98.762 | 98.8216 | 97.1101 | 98.2156 | 98.4158 | 98.4713 | 98.4443 | 98.3524 | 98.3771 | 2017-11-01 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-40KTL-US {480V} | N | N | Y | Y | Y | N | N | N | 40 kW, 480 Vac, transformerless Grid Support Utility Interactive Inverter | 40 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [3/22/2017] | [SUN2000 V200 R002C20] | 2018-10-15 | [3/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1.8 |  |  | 530 | 720 | 850 | 4 | 8 | 12 | 20 | 30 | 40 | 96.7485 | 97.7289 | 97.9466 | 98.102 | 98.049 | 97.9087 | 97.9728 | 98.0538 | 98.7273 | 98.7781 | 98.8628 | 98.7907 | 98.8053 | 98.7724 | 97.2662 | 98.2155 | 98.3638 | 98.4571 | 98.3764 | 98.4169 | 98.3414 | 2017-11-01 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-45KTL-US-HV-D0 {600V} | N | N | Y | Y | Y | N | N | N | 45kW, 600 Vac, Transformerlss Grid Support Utility Interactive Inverter | 45.207 | 600 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [9/29/2017] | [SUN2000HA V100R001] | 2018-10-15 | [9/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1.11 |  |  | 800 | 1000 | 1200 | 97.5 | 98.1 | 98.2 | 98.2 | 98.1 | 97.9 | 98.2 | 98.6 | 98.7 | 98.6 | 98.5 | 98.4 | 98.5 | 98.2 | 98.6 | 98.7 | 98.6 | 98.5 | 98.4 | 98.5 | 98.1 | 98.5 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 | 2017-11-15 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-100KTL-USH0 {800V} | N | N | Y | Y | Y | N | N | N | 100 kW, 800 Vac, 3-phase transformerless Grid Support Utility Interactive Inverter | 100 | 800 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [10/16/2018] | [SUN2000HA V200 R001] | 2019-01-15 | [10/16/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.61 |  |  | 880 | 1120 | 1200 | 10 | 20 | 30 | 50 | 75 | 100 | 97.2971 | 98.0491 | 98.3042 | 98.447 | 98.4104 | 98.3164 | 98.338 | 97.6913 | 98.412 | 98.5995 | 98.6923 | 98.6594 | 98.5739 | 98.6037 | 98.2248 | 98.7907 | 98.9363 | 98.9879 | 98.9811 | 98.631 | 98.9199 | 2019-01-15
Huizhou Roypow Technology Co., Ltd | SUN10000S-U {240V} | Y | Y | N | N | N | N | Y* | Y | 10.111 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.111 | 240 | 95.5 | CSA Group | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-10-17 | 2025-01-02 |  | N | N | 36.53 |  |  | 200 | 300 | 440 | 1.011 | 2.022 | 3.033 | 5.055 | 7.583 | 10.111 | 90.13 | 93.91 | 95.02 | 95.42 | 95.26 | 94.75 | 94.97 | 90.3 | 94.11 | 95.3 | 96.04 | 95.95 | 95.76 | 95.56 | 89.9 | 94.14 | 95.42 | 96.26 | 96.36 | 96.21 | 95.85 | 2024-08-01 | 2025-01-02
Huizhou Roypow Technology Co., Ltd | SUN12000S-U {240V} | Y | Y | N | N | N | N | Y* | Y | 12.079 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.079 | 240 | 95.5 | CSA Group | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-10-17 | 2025-01-02 |  | N | N | 36.44 |  |  | 200 | 300 | 440 | 1.208 | 2.416 | 3.624 | 6.039 | 9.059 | 12.079 | 90.6 | 94.4 | 95.16 | 95.39 | 94.99 | 94.49 | 94.87 | 91.02 | 94.65 | 95.66 | 96.13 | 95.9 | 95.58 | 95.65 | 90.95 | 94.82 | 95.86 | 96.36 | 96.29 | 96.16 | 95.96 | 2024-08-01 | 2025-01-02
Huizhou Roypow Technology Co., Ltd | SUN15000S-U {240V} | Y | Y | N | N | N | N | Y* | Y | 14.987 kW, 240 Vac Grid Support Utility Interactive Inverter | 14.987 | 240 | 95.5 | CSA Group | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-10-17 | 2025-01-02 |  | N | N | 35.81 |  |  | 200 | 300 | 440 | 1.499 | 2.997 | 4.496 | 7.493 | 11.24 | 14.987 | 92.8 | 94.52 | 95.48 | 95.57 | 94.76 | 94.12 | 94.9 | 93.5 | 94.74 | 95.41 | 96.14 | 95.86 | 95.53 | 95.7 | 93.63 | 95.21 | 95.59 | 96.03 | 96.19 | 96.05 | 95.93 | 2024-08-01 | 2025-01-02
Hyperian Energy Inc. | ST2-76i {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter Power Conversion System | 7.581 | 240 | 97 | Intertek | [11/9/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.758 | 1.516 | 2.274 | 3.791 | 5.686 | 7.581 | 94.27 | 95.22 | 96.16 | 96.92 | 97.11 | 97.06 | 96.75 | 95.22 | 96.18 | 96.79 | 97.36 | 97.6 | 97.53 | 97.29 | 94.82 | 95.83 | 96.55 | 97.2 | 97.42 | 97.35 | 97.09 | 2024-05-13
Hyperian Energy Inc. | ST2-96i {240V} | Y | Y | N | N | N | N | N | N | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter Power Conversion System | 9.573 | 240 | 97 | Intertek | [11/9/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.957 | 1.915 | 2.872 | 4.787 | 7.18 | 9.573 | 94.32 | 95.43 | 96.47 | 97.01 | 97.09 | 97.01 | 96.8 | 95.76 | 96.41 | 97.04 | 97.48 | 97.57 | 97.4 | 97.35 | 94.89 | 95.98 | 96.84 | 97.31 | 97.39 | 97.23 | 97.13 | 2024-05-13
Hyperian Energy Inc. | ST2-100i {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive Inverter Power Conversion System | 9.956 | 240 | 97 | Intertek | [11/9/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.996 | 1.991 | 2.987 | 4.978 | 7.467 | 9.956 | 94.33 | 95.61 | 96.51 | 97.03 | 97.07 | 96.98 | 96.81 | 95.79 | 96.48 | 97.07 | 97.5 | 97.54 | 97.37 | 97.35 | 95.18 | 96.08 | 96.88 | 97.34 | 97.37 | 97.21 | 97.14 | 2024-05-13
Hyperian Energy Inc. | ST2-114i {240V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter Power Conversion System | 11.371 | 240 | 97 | Intertek | [11/9/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.137 | 2.274 | 3.411 | 5.685 | 8.528 | 11.371 | 94.36 | 96.06 | 96.91 | 97.1 | 97.04 | 96.9 | 96.88 | 95.81 | 96.79 | 97.34 | 97.6 | 97.47 | 97.26 | 97.37 | 95.28 | 96.55 | 97.16 | 97.41 | 97.3 | 97.08 | 97.18 | 2024-05-13
Hyperian Energy Inc. | ST2-120i {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Utility Interactive Inverter Power Conversion System | 11.968 | 240 | 97 | Intertek | [11/9/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.197 | 2.394 | 3.59 | 5.984 | 8.976 | 11.968 | 94.38 | 96.06 | 96.92 | 97.12 | 97.01 | 96.87 | 96.87 | 95.83 | 96.81 | 97.34 | 97.62 | 97.45 | 97.22 | 97.37 | 95.32 | 96.57 | 97.18 | 97.44 | 97.28 | 97.04 | 97.18 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 610TL U B220 {220V} | Y | N | Y | Y | Y | N | N | N | 610 kW, 220 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 610 | 220 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 440 | 590 | 740 | 61 | 122 | 183 | 305 | 457.5 | 610 | 97.11 | 98.06 | 98.25 | 98.17 | 97.74 | 97.1 | 97.85 | 96.37 | 97.64 | 98.01 | 97.9 | 97.48 | 96.73 | 97.56 | 95.53 | 97.29 | 97.68 | 97.72 | 97.45 | 96.53 | 97.41 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 830TL U B300 {300V} | Y | N | Y | Y | Y | N | N | N | 830 kW, 300 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 830 | 300 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 440 | 590 | 740 | 83 | 166 | 249 | 415 | 622.5 | 830 | 97.21 | 98.13 | 98.27 | 98.16 | 97.74 | 97.18 | 97.86 | 96.5 | 97.77 | 97.96 | 97.92 | 97.55 | 97.06 | 97.62 | 95.7 | 97.41 | 97.7 | 97.66 | 97.36 | 96.88 | 97.38 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 915TL U B330 {330V} | Y | N | Y | Y | Y | N | N | N | 915 kW, 330 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 915 | 330 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 485 | 613 | 740 | 91.5 | 183 | 274.5 | 457.5 | 686.25 | 915 | 97.17 | 98.13 | 98.33 | 98.22 | 97.86 | 97.27 | 97.95 | 96.5 | 97.84 | 98.09 | 98.05 | 97.69 | 97.15 | 97.75 | 95.82 | 97.49 | 97.82 | 97.81 | 97.51 | 97.17 | 97.53 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1000TL U B360 {360V} | Y | N | Y | Y | Y | N | N | N | 1000 kW, 360 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1000 | 360 | 98 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 524 | 632 | 740 | 100 | 200 | 300 | 500 | 750 | 1000 | 97.34 | 98.14 | 98.33 | 98.21 | 97.83 | 97.31 | 97.94 | 96.84 | 97.92 | 98.13 | 98.08 | 97.7 | 97.09 | 97.78 | 96.36 | 97.64 | 97.97 | 97.94 | 97.55 | 96.97 | 97.61 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1140TL U B410 {410V} | Y | N | Y | Y | Y | N | N | N | 1136 kVA, 410 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1027.752 | 410 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 2550.2775 |  |  | 595 | 668 | 800 | 102.7752 | 205.5504 | 308.3256 | 513.876 | 770.814 | 1027.752 | 95.8625 | 97.4417 | 97.8113 | 97.8912 | 97.7441 | 97.3829 | 97.6746 | 95.6736 | 97.3781 | 97.7557 | 97.8606 | 97.7193 | 97.3781 | 97.6374 | 95.14 | 97.0801 | 97.524 | 97.6897 | 97.5561 | 97.213 | 97.4427 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1245TL U B480 {480V} | Y | N | Y | Y | Y | N | N | N | 1247 kVA, 480 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1042.22 | 480 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 697 | 949 | 1200 | 104.222 | 208.444 | 312.666 | 521.11 | 781.665 | 1042.22 | 96.9037 | 97.6188 | 97.803 | 97.7395 | 97.5015 | 97.1174 | 97.5504 | 96.4047 | 97.431 | 97.5993 | 97.4719 | 97.2822 | 96.859 | 97.3113 | 96.026 | 97.0747 | 97.3979 | 97.2268 | 96.9903 | 96.5138 | 97.0307 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1190TL U B430 {430V} | Y | N | Y | Y | Y | N | N | N | 1192 kVA, 430 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1048.594 | 430 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 2550.2775 |  |  | 624 | 682 | 800 | 104.8594 | 209.7188 | 314.5782 | 524.297 | 786.4455 | 1048.594 | 96.0041 | 97.4811 | 97.8373 | 97.9231 | 97.7893 | 97.4138 | 97.7176 | 95.8692 | 97.4303 | 97.7966 | 97.9039 | 97.781 | 97.4506 | 97.6982 | 95.3825 | 97.1832 | 97.5935 | 97.7411 | 97.6496 | 97.3174 | 97.5314 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1220TL U B440 {440V} | Y | N | Y | Y | Y | N | N | N | 1217 kVA, 440 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1099.306 | 440 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 2550.2775 |  |  | 638 | 689 | 800 | 109.9306 | 219.8612 | 329.7918 | 549.653 | 824.4795 | 1099.306 | 95.932 | 97.4927 | 97.868 | 97.9487 | 97.8105 | 97.4537 | 97.7375 | 95.8363 | 97.4652 | 97.8509 | 97.9442 | 97.8039 | 97.4677 | 97.7266 | 95.4261 | 97.2395 | 97.6478 | 97.8037 | 97.6832 | 97.3514 | 97.5752 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1110TL U B400 {400V} | Y | N | Y | Y | Y | N | N | N | 1110 kW, 400 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1110 | 400 | 98 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 580 | 660 | 740 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 97.16 | 98.08 | 98.29 | 98.27 | 97.94 | 97.39 | 98 | 96.8 | 97.93 | 98.19 | 98.25 | 97.8 | 97.32 | 97.89 | 96.54 | 97.71 | 98.06 | 98.12 | 97.67 | 97.35 | 97.75 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1250TL U B450 {450V} | Y | N | Y | Y | Y | N | N | N | 1247 kVA, 450 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1114.104 | 450 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 2550.2775 |  |  | 652 | 696 | 800 | 111.4104 | 222.8208 | 334.2312 | 557.052 | 835.578 | 1114.104 | 95.9706 | 97.5016 | 97.8688 | 97.9364 | 97.8103 | 97.4968 | 97.7391 | 95.9001 | 97.4837 | 97.855 | 97.9743 | 97.8316 | 97.5204 | 97.7542 | 95.5073 | 97.2604 | 97.6982 | 97.8443 | 97.7172 | 97.4132 | 97.6152 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1275TL U B460 {460V} | Y | N | Y | Y | Y | N | N | N | 1275 kVA, 460 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1128.476 | 460 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 2550.2775 |  |  | 666 | 703 | 800 | 112.8476 | 225.6952 | 338.5428 | 564.238 | 846.357 | 1128.476 | 95.9938 | 97.508 | 97.8617 | 97.9706 | 97.8442 | 97.6278 | 97.7712 | 95.8888 | 97.4823 | 97.8709 | 97.9916 | 97.8671 | 97.5597 | 97.7799 | 95.5429 | 97.3202 | 97.7334 | 97.9123 | 97.7635 | 97.4905 | 97.6665 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1165TL U B420 {420V} | Y | N | Y | Y | Y | N | N | N | 1165 kW, 420 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1165 | 420 | 98 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 610 | 675 | 740 | 116.5 | 233 | 349.5 | 582.5 | 873.75 | 1165 | 97.28 | 98.08 | 98.28 | 98.26 | 98.01 | 97.47 | 98.04 | 96.99 | 97.92 | 98.18 | 98.24 | 97.91 | 97.53 | 97.95 | 96.74 | 97.75 | 98.03 | 98.15 | 97.85 | 97.42 | 97.87 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1740TL U B670 {670V} | Y | N | Y | Y | Y | N | N | N | 1741 kVA, 670 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1272.412 | 670 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 962 | 1081 | 1200 | 127.2412 | 254.4824 | 381.7236 | 636.206 | 954.309 | 1272.412 | 95.9646 | 97.3748 | 97.6902 | 97.7604 | 97.6287 | 97.348 | 97.5704 | 95.7313 | 97.2879 | 97.5573 | 97.697 | 97.5442 | 97.223 | 97.4764 | 95.3778 | 97.1365 | 97.419 | 97.506 | 97.402 | 97.144 | 97.3188 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1800TL U B690 {690V} | Y | N | Y | Y | Y | N | N | N | 1793 kVA, 690 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1300.644 | 690 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 962 | 1081 | 1200 | 130.0644 | 260.1288 | 390.1932 | 650.322 | 975.483 | 1300.644 | 96.6717 | 97.6652 | 97.8788 | 97.9021 | 97.7538 | 97.399 | 97.7345 | 96.4722 | 97.5961 | 97.804 | 97.828 | 97.6778 | 97.3356 | 97.6551 | 96.3335 | 97.5145 | 97.7082 | 97.7346 | 97.5625 | 97.2579 | 97.5493 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1665TL U B640 {640V} | Y | N | Y | Y | Y | N | N | N | 1663 kVA, 640 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1367.076 | 640 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 919 | 1060 | 1200 | 136.7076 | 273.4152 | 410.1228 | 683.538 | 1025.307 | 1367.076 | 96.2495 | 97.4423 | 97.7204 | 97.755 | 97.6184 | 97.3123 | 97.5805 | 95.9772 | 97.3141 | 97.5906 | 97.6697 | 97.5061 | 97.1929 | 97.4642 | 95.5155 | 97.1401 | 97.4064 | 97.4529 | 97.3426 | 97.0371 | 97.2749 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1690TL U B650 {650V} | Y | N | Y | Y | Y | N | N | N | 1689 kVA, 650 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1375.282 | 650 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 933 | 1067 | 1200 | 137.5282 | 275.0564 | 412.5846 | 687.641 | 1031.4615 | 1375.282 | 96.2881 | 97.5051 | 97.7757 | 97.8183 | 97.6619 | 97.3581 | 97.6304 | 96.0008 | 97.4016 | 97.6638 | 97.7405 | 97.5736 | 97.2501 | 97.5318 | 95.6676 | 97.2627 | 97.5419 | 97.5575 | 97.4238 | 97.0851 | 97.3708 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1715TL U B660 {660V} | Y | N | Y | Y | Y | N | N | N | 1715 kVA, 660 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1390.614 | 660 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 948 | 1074 | 1200 | 139.0614 | 278.1228 | 417.1842 | 695.307 | 1042.9605 | 1390.614 | 96.0622 | 97.4034 | 97.6863 | 97.7536 | 97.622 | 97.3392 | 97.5699 | 95.8419 | 97.2707 | 97.5502 | 97.7009 | 97.5384 | 97.2305 | 97.4773 | 95.3647 | 97.1092 | 97.4005 | 97.5253 | 97.4034 | 97.0865 | 97.3166 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3825TL U C600 {600V} | N | Y | N | N | N | N | N | N | 3095 kW, 600 Vac, Bi-directional, Grid Support Utility Interactive PV Inverter with External Transformer | 3095.3 | 600 | 98 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2892.5248 |  |  | 857 | 1170 | 1300 | 309.53 | 619.06 | 928.59 | 1547.65 | 2321.475 | 3095.3 | 96.29 | 98.06 | 98.51 | 98.67 | 98.58 | 98.31 | 98.46 | 95.35 | 96.93 | 97.24 | 97.5 | 97.48 | 97.29 | 97.33 | 95.6 | 97.16 | 97.6 | 97.77 | 97.69 | 97.42 | 97.57 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3825TL U C615 {615V} | N | Y | N | N | N | N | N | N | 3219 kW, 615 Vac, Bi-directional, Grid Support Utility Interactive PV Inverter with External Transformer | 3219.88 | 615 | 98 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2892.5248 |  |  | 877 | 1180 | 1300 | 321.988 | 643.976 | 965.964 | 1609.94 | 2414.91 | 3219.88 | 97.53 | 98.45 | 98.69 | 98.69 | 98.41 | 97.58 | 98.43 | 96.12 | 97.52 | 97.94 | 98.13 | 98.03 | 97.76 | 97.93 | 95.77 | 97.19 | 97.65 | 97.93 | 97.83 | 97.55 | 97.7 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3825TL U C630 {630V} | N | Y | N | N | N | N | N | N | 3239 kW, 630 Vac, Bi-directional, Grid Support Utility Interactive PV Inverter with External Transformer | 3239.42 | 630 | 98 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2892.5248 |  |  | 894 | 1185 | 1300 | 323.942 | 647.884 | 971.826 | 1619.71 | 2429.565 | 3239.42 | 96.31 | 97.78 | 98.22 | 98.26 | 98.31 | 98.03 | 98.17 | 95.7 | 97.24 | 97.68 | 97.85 | 97.76 | 97.49 | 97.65 | 95.46 | 96.98 | 97.42 | 97.59 | 97.5 | 97.23 | 97.39 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3825TL U C645 {645V} | N | Y | N | N | N | N | N | N | 3304 kW, 645 Vac, Bi-directional, Grid Support Utility Interactive PV Inverter with External Transformer | 3304.62 | 645 | 98 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2892.5248 |  |  | 919 | 1198 | 1300 | 330.462 | 660.924 | 991.386 | 1652.31 | 2478.465 | 3304.62 | 96.32 | 97.88 | 98.4 | 98.59 | 98.67 | 98.56 | 98.48 | 95.87 | 97.42 | 97.86 | 98.03 | 97.94 | 97.66 | 97.82 | 95.66 | 97.22 | 97.66 | 97.83 | 97.74 | 97.46 | 97.63 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3825TL U C660 {660V} | N | Y | N | N | N | N | N | N | 3377 kW, 660 Vac, Bi-directional, Grid Support Utility Interactive PV Inverter with External Transformer | 3377.6 | 660 | 98 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2804.839 |  |  | 940 | 1198 | 1300 | 337.76 | 675.52 | 1013.28 | 1688.8 | 2533.2 | 3377.6 | 96.55 | 98.08 | 98.53 | 98.7 | 98.61 | 98.34 | 98.5 | 96.01 | 97.58 | 98 | 98.18 | 98.09 | 97.81 | 97.97 | 95.82 | 97.37 | 97.81 | 97.98 | 97.89 | 97.57 | 97.77 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3825TL U C675 {675V} | N | Y | N | N | N | N | N | N | 3452 kW, 675 Vac, Bi-directional, Grid Support Utility Interactive PV Inverter with External Transformer | 3452.7 | 675 | 98 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2804.839 |  |  | 960 | 1200 | 1300 | 345.27 | 690.54 | 1035.81 | 1726.35 | 2589.525 | 3452.7 | 96.67 | 98.21 | 98.64 | 98.81 | 98.72 | 98.44 | 98.61 | 96.13 | 98.03 | 98.18 | 98.35 | 98.26 | 97.96 | 98.16 | 95.97 | 97.52 | 97.96 | 98.13 | 98.04 | 97.76 | 97.92 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3825TL U C690 {690V} | N | Y | N | N | N | N | N | N | 3535 kW, 690 Vac, Bi-directional, Grid Support Utility Interactive PV Inverter with External Transformer | 3535.56 | 690 | 98.5 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2804.839 |  |  | 981 | 1200 | 1300 | 353.556 | 707.112 | 1060.668 | 1767.78 | 2651.67 | 3535.56 | 96.8472 | 98.3894 | 98.8191 | 98.9899 | 98.9407 | 98.6271 | 98.8095 | 96.4248 | 97.9781 | 98.4038 | 98.5799 | 98.49 | 98.2174 | 98.3767 | 96.103 | 97.6667 | 98.1004 | 98.2761 | 98.1845 | 97.9132 | 98.0709 | 2024-05-13
Jackery Inc. | GVI-HR-7K6-USG {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.394 | 240 | 97 | CSA Group | [9/8/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-23 | 2025-02-21 |  | N | N | 16.33 |  |  | 175 | 380 | 450 | 0.739 | 1.479 | 2.218 | 3.697 | 5.545 | 7.394 | 95.78 | 96.57 | 97.14 | 97.12 | 97.27 | 97.32 | 97.13 | 95.02 | 96.11 | 97.17 | 97.26 | 97.29 | 97.63 | 97.13 | 94.73 | 96.14 | 96.95 | 97.09 | 97.15 | 97.33 | 96.97 | 2025-02-21
Jackery Inc. | GVI-HR-11K4-USG {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.084 | 240 | 97 | CSA Group | [9/8/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-23 | 2025-02-21 |  | N | N | 15.36 |  |  | 245 | 380 | 450 | 1.108 | 2.217 | 3.325 | 5.542 | 8.313 | 11.084 | 94.77 | 96.19 | 97.09 | 97.38 | 97.26 | 97.27 | 97.11 | 95.99 | 96.88 | 96.88 | 97.03 | 97.23 | 97.34 | 97.08 | 95.55 | 96.65 | 97.05 | 97.18 | 97.22 | 97.63 | 97.11 | 2025-02-21
Jiangsu RCT Power Energy Technology Co., Ltd | Power Storage DC US-8.0 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.015 | 208 | 97 | CSA Group | [4/29/2024] | CSA Group | [3/30/2022];[4/29/2024] | [V54];[V127(2.27.0104-1.44)] | 2022-05-11 | [3/30/2022] | 2022-05-11 | CSA Group | 2022-03-17 | 2022-05-11 |  | N | N | 0.3 |  |  | 220 | 360 | 420 | 0.701 | 1.403 | 2.104 | 3.507 | 5.261 | 7.015 | 93.43 | 95.62 | 96.35 | 96.74 | 96.65 | 96.23 | 96.43 | 93.5 | 96.2 | 96.79 | 97.21 | 97.18 | 96.89 | 96.93 | 93.92 | 96.44 | 97.09 | 97.42 | 97.35 | 97.01 | 97.13 | 2022-05-11 | 2024-08-01
Jiangsu RCT Power Energy Technology Co., Ltd | Power Storage DC US-8.0 PRO {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.015 | 208 | 97 | CSA Group | [4/29/2024] | CSA Group | [3/30/2022];[4/29/2024] | [V54];[V127(2.27.0104-1.44)] | 2024-08-01 | [4/29/2024] | 2024-08-01 | CSA Group | 2024-06-01 | 2024-08-01 |  | N | N | 0.3 |  |  | 220 | 360 | 420 | 0.701 | 1.403 | 2.104 | 3.507 | 5.261 | 7.015 | 93.4321 | 95.6214 | 96.3503 | 96.7391 | 96.6452 | 96.2338 | 96.4293 | 93.4986 | 96.2026 | 96.7947 | 97.209 | 97.1825 | 96.889 | 96.9305 | 93.9173 | 96.445 | 97.0889 | 97.4174 | 97.3475 | 97.0142 | 97.1321 | 2024-08-01
Jiangsu RCT Power Energy Technology Co., Ltd | Power Storage DC US-8.0 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.0322 | 240 | 97 | CSA Group | [4/29/2024] | CSA Group | [3/30/2022];[4/29/2024] | [V54];[V127(2.27.0104-1.44)] | 2022-05-11 | [3/30/2022] | 2022-05-11 | CSA Group | 2022-03-17 | 2022-05-11 |  | N | N | 0.4025 |  |  | 220 | 360 | 420 | 0.80322 | 1.6064 | 2.4097 | 4.0161 | 6.0241 | 8.0322 | 94.4835 | 96.2889 | 96.8676 | 97.1353 | 96.9831 | 96.5638 | 96.8456 | 94.8035 | 96.8257 | 97.2969 | 97.5898 | 97.5257 | 97.2299 | 97.353 | 94.7472 | 96.886 | 97.455 | 97.7157 | 97.636 | 97.3371 | 97.463 | 2022-05-11 | 2024-08-01
Jiangsu RCT Power Energy Technology Co., Ltd | Power Storage DC US-8.0 PRO {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.0322 | 240 | 97 | CSA Group | [4/29/2024] | CSA Group | [3/30/2022];[4/29/2024] | [V54];[V127(2.27.0104-1.44)] | 2024-08-01 | [4/29/2024] | 2024-08-01 | CSA Group | 2024-06-01 | 2024-08-01 |  | N | N | 0.4025 |  |  | 220 | 360 | 420 | 0.80322 | 1.6064 | 2.4097 | 4.0161 | 6.0241 | 8.0322 | 94.4835 | 96.2889 | 96.8676 | 97.1353 | 96.9831 | 96.5638 | 96.8456 | 94.8035 | 96.8257 | 97.2969 | 97.5898 | 97.5257 | 97.2299 | 97.353 | 94.7472 | 96.886 | 97.455 | 97.7157 | 97.636 | 97.3371 | 97.463 | 2024-08-01
Jiangsu Weiheng Intelligent Technology Co., Ltd. | SHD-7.6kW {240V} | Y | Y | N | N | N | N | N | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.572 | 240 | 97 | Intertek | [7/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-08-21 |  | N | N | 10.938 |  |  | 144 | 410 | 550 | 0.757 | 1.514 | 2.271 | 3.786 | 5.679 | 7.572 | 92.67 | 93.99 | 96.25 | 96.74 | 97.23 | 97.29 | 96.67 | 93.45 | 95.89 | 96.63 | 97.13 | 97.44 | 97.17 | 97.03 | 92.88 | 93.74 | 95.81 | 96.67 | 97.51 | 97.41 | 96.75 | 2025-08-21
Jiangsu Weiheng Intelligent Technology Co., Ltd. | SHD-9.6kW {240V} | Y | Y | N | N | N | N | N | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.66 | 240 | 97 | Intertek | [7/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-08-21 |  | N | N | 11.042 |  |  | 180 | 410 | 550 | 0.966 | 1.932 | 2.898 | 4.83 | 7.245 | 9.66 | 95.02 | 95.73 | 96.33 | 97.12 | 97.43 | 96.86 | 97.02 | 94.7 | 96.34 | 96.9 | 97.25 | 97.43 | 97.04 | 97.15 | 93.23 | 95.17 | 96.29 | 97.24 | 97.54 | 97.15 | 97.02 | 2025-08-21
Jiangsu Weiheng Intelligent Technology Co., Ltd. | SHD-11.4kW {240V} | Y | Y | N | N | N | N | N | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.257 | 240 | 97 | Intertek | [7/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-08-21 |  | N | N | 10.379 |  |  | 210 | 410 | 550 | 1.126 | 2.251 | 3.377 | 5.628 | 8.443 | 11.257 | 95.48 | 96.28 | 96.64 | 97.26 | 97.49 | 96.36 | 97.14 | 95.03 | 96.63 | 97.11 | 97.59 | 97.3 | 96.87 | 97.19 | 93.32 | 95.8 | 96.63 | 97.54 | 97.36 | 96.48 | 97.03 | 2025-08-21
Jinko Solar Co., Ltd | JKS-R-7P12-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.604 | 240 | 97 | CSA Group | [5/30/2023] | CSA Group | [5/30/2023] | [A2] | 2023-12-01 | [5/30/2023] | 2023-12-01 | CSA Group | 2023-09-25 | 2023-11-27 |  | N | N | 16.33 |  |  | 175 | 380 | 450 | 0.76 | 1.521 | 2.281 | 3.802 | 5.703 | 7.604 | 95.78 | 96.57 | 97.14 | 97.12 | 97.27 | 97.32 | 97.13 | 95.02 | 96.11 | 97.17 | 97.26 | 97.29 | 97.63 | 97.13 | 94.73 | 96.14 | 96.95 | 97.09 | 97.15 | 97.33 | 96.97 | 2023-12-01 | 2024-01-22
Jinko Solar Co., Ltd | JKS-R-11P12-US {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.406 | 240 | 97 | CSA Group | [5/30/2023] | CSA Group | [5/30/2023] | [A2] | 2023-12-01 | [5/30/2023] | 2023-12-01 | CSA Group | 2023-09-25 | 2023-11-27 |  | N | N | 15.36 |  |  | 245 | 380 | 450 | 1.141 | 2.281 | 3.422 | 5.703 | 8.554 | 11.406 | 94.77 | 96.19 | 97.09 | 97.38 | 97.26 | 97.27 | 97.11 | 95.99 | 96.88 | 96.88 | 97.03 | 97.23 | 97.34 | 97.08 | 95.55 | 96.65 | 97.05 | 97.18 | 97.22 | 97.57 | 97.11 | 2023-12-01 | 2024-01-22
KACO new energy GmbH | KACO blueplanet 110 TL3 M1 WM OD IIK0 {480V} | N | N | Y | Y | Y | N | N | N | 110 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter | 109.765 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/19/2019] | [V 1.07, V 1.09, V 1.11, V 1.13] | 2020-02-11 | [12/19/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5 |  |  | 705 | 854 | 1300 | 10.9765 | 21.9531 | 32.9296 | 54.8827 | 82.324 | 109.7653 | 98.9285 | 99.0714 | 99.0635 | 98.972 | 98.8189 | 98.6338 | 98.8881 | 98.5843 | 98.8565 | 98.883 | 98.797 | 98.6085 | 98.3579 | 98.6799 | 97.5363 | 98.113 | 98.2893 | 98.3433 | 98.2373 | 98.0193 | 98.2207 | 2020-02-11
KACO new energy GmbH | KACO blueplanet 110 TL3 M1 WM OD IIKX {480V} | N | N | Y | Y | Y | N | N | N | 110 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter | 109.765 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [12/19/2019] | [V 1.07, V 1.09, V 1.11, V 1.13] | 2020-02-11 | [12/19/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5 |  |  | 705 | 854 | 1300 | 10.9765 | 21.9531 | 32.9296 | 54.8827 | 82.324 | 109.7653 | 98.9285 | 99.0714 | 99.0635 | 98.972 | 98.8189 | 98.6338 | 98.8881 | 98.5843 | 98.8565 | 98.883 | 98.797 | 98.6085 | 98.3579 | 98.6799 | 97.5363 | 98.113 | 98.2893 | 98.3433 | 98.2373 | 98.0193 | 98.2207 | 2020-02-11
KACO new energy GmbH | KACO blueplanet 125 TL3 M1 WM OD IIP0 {600V} | N | N | Y | Y | Y | N | N | N | 125 kVA Nominal Power, 137 kVA Max Power, 600Vac, 1500Vdc Grid Support Utility Interactive Inverter | 138.663 | 600 | 99 | No Information Submitted | No Information Submitted | Intertek | [12/19/2019] | [V 1.07, V 1.09, V 1.11, V 1.13] | 2020-02-11 | [12/19/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.57 |  |  | 875 | 981 | 1300 | 13.8663 | 27.7327 | 41.599 | 69.3317 | 103.9976 | 138.6635 | 98.8968 | 99.122 | 99.1432 | 99.0815 | 98.9664 | 98.8336 | 99.0101 | 98.6555 | 98.9518 | 99 | 98.9622 | 98.8062 | 98.623 | 98.8543 | 97.9954 | 98.4548 | 98.6119 | 98.6678 | 98.5577 | 98.3931 | 98.5515 | 2020-02-11
KACO new energy GmbH | KACO blueplanet 125 TL3 M1 WM OD IIPX {600V} | N | N | Y | Y | Y | N | N | N | 125 kVA Nominal Power, 137 kVA Max Power, 600Vac, 1500Vdc Grid Support Utility Interactive Inverter | 138.663 | 600 | 99 | No Information Submitted | No Information Submitted | Intertek | [12/19/2019] | [V 1.07, V 1.09, V 1.11, V 1.13] | 2020-02-11 | [12/19/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.57 |  |  | 875 | 981 | 1300 | 13.8663 | 27.7327 | 41.599 | 69.3317 | 103.9976 | 138.6635 | 98.8968 | 99.122 | 99.1432 | 99.0815 | 98.9664 | 98.8336 | 99.0101 | 98.6555 | 98.9518 | 99 | 98.9622 | 98.8062 | 98.623 | 98.8543 | 97.9954 | 98.4548 | 98.6119 | 98.6678 | 98.5577 | 98.3931 | 98.5515 | 2020-02-11
KACO new energy GmbH | KACO blueplanet 137 TL3 M1 WM OD IIP0 {600V} | N | N | Y | Y | Y | N | N | N | 137 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter | 138.663 | 600 | 99 | No Information Submitted | No Information Submitted | Intertek | [12/19/2019] | [V 1.07, V 1.09, V 1.11, V 1.13] | 2020-02-11 | [12/19/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.57 |  |  | 875 | 981 | 1300 | 13.8663 | 27.7327 | 41.599 | 69.3317 | 103.9976 | 138.6635 | 98.8968 | 99.122 | 99.1432 | 99.0815 | 98.9664 | 98.8336 | 99.0101 | 98.6555 | 98.9518 | 99 | 98.9622 | 98.8062 | 98.623 | 98.8543 | 97.9954 | 98.4548 | 98.6119 | 98.6678 | 98.5577 | 98.3931 | 98.5515 | 2020-02-11
KACO new energy GmbH | KACO blueplanet 137 TL3 M1 WM OD IIPX {600V} | N | N | Y | Y | Y | N | N | N | 137 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter | 138.663 | 600 | 99 | No Information Submitted | No Information Submitted | Intertek | [12/19/2019] | [V 1.07, V 1.09, V 1.11, V 1.13] | 2020-02-11 | [12/19/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.57 |  |  | 875 | 981 | 1300 | 13.8663 | 27.7327 | 41.599 | 69.3317 | 103.9976 | 138.6635 | 98.8968 | 99.122 | 99.1432 | 99.0815 | 98.9664 | 98.8336 | 99.0101 | 98.6555 | 98.9518 | 99 | 98.9622 | 98.8062 | 98.623 | 98.8543 | 97.9954 | 98.4548 | 98.6119 | 98.6678 | 98.5577 | 98.3931 | 98.5515 | 2020-02-11
KACO new energy GmbH | KACO blueplanet 150 TL3 M1 WM OD IIQ0 {660V} | N | N | Y | Y | Y | N | N | N | 150 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter | 151.228 | 660 | 99 | No Information Submitted | No Information Submitted | Intertek | [12/19/2019] | [V 1.07, V 1.09, V 1.11, V 1.13] | 2020-02-11 | [12/19/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.25 |  |  | 960 | 1045 | 1300 | 15.1228 | 30.2455 | 45.3683 | 75.6138 | 113.4207 | 151.2276 | 98.8336 | 99.11 | 99.1489 | 99.1038 | 99.0103 | 98.8953 | 99.0387 | 98.6981 | 99.001 | 99.0493 | 99.0136 | 98.8922 | 98.7227 | 98.9258 | 98.1102 | 98.5923 | 98.7418 | 98.7863 | 98.698 | 98.5522 | 98.6857 | 2020-02-11
KACO new energy GmbH | KACO blueplanet 150 TL3 M1 WM OD IIQX {660V} | N | N | Y | Y | Y | N | N | N | 150 kVA, 480 Vac, 1500Vdc Grid Support Utility Interactive Inverter | 151.228 | 660 | 99 | No Information Submitted | No Information Submitted | Intertek | [12/19/2019] | [V 1.07, V 1.09, V 1.11, V 1.13] | 2020-02-11 | [12/19/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.25 |  |  | 960 | 1045 | 1300 | 15.1228 | 30.2455 | 45.3683 | 75.6138 | 113.4207 | 151.2276 | 98.8336 | 99.11 | 99.1489 | 99.1038 | 99.0103 | 98.8953 | 99.0387 | 98.6981 | 99.001 | 99.0493 | 99.0136 | 98.8922 | 98.7227 | 98.9258 | 98.1102 | 98.5923 | 98.7418 | 98.7863 | 98.698 | 98.5522 | 98.6857 | 2020-02-11
Kora Power, Inc. | KP-INV-380-01 {240V} | Y | Y | Y | Y | Y | Y | N |  | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 3.7972 | 240 | 96 | CSA Group | [8/17/2026] | CSA Group | [8/17/2026] | [V1.08, V1.02] | 2026-10-01 | [8/17/2026] | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 13.35 |  |  | 204 | 380 | 500 | 0.37972 | 0.75944 | 1.1392 | 1.8986 | 2.8479 | 3.7972 | 89.6627 | 93.2292 | 94.5681 | 95.9692 | 96.4301 | 96.5483 | 95.685 | 91.725 | 94.6987 | 95.7083 | 96.7501 | 96.9842 | 97.1693 | 96.4665 | 88.9624 | 93.5492 | 95.5387 | 97.0122 | 97.3598 | 97.5206 | 96.5499 | 2026-10-01 |  | N | Y | N | N | N | Y | N | N | N
Kora Power, Inc. | KP-INV-570-01 {240V} | Y | Y | Y | Y | Y | Y | N |  | 5.7 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.6866 | 240 | 97 | CSA Group | [8/17/2026] | CSA Group | [8/17/2026] | [V1.08, V1.02] | 2026-10-01 | [8/17/2026] | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 13.35 |  |  | 204 | 380 | 500 | 0.56866 | 1.1373 | 1.706 | 2.8433 | 4.265 | 5.6866 | 90.9696 | 94.7434 | 95.8003 | 96.4201 | 96.6721 | 96.5359 | 96.1832 | 91.1194 | 95.495 | 96.9717 | 97.7104 | 97.7396 | 97.8212 | 97.2684 | 91.0574 | 96.0199 | 96.4362 | 96.7768 | 97.6862 | 97.512 | 96.9881 | 2026-10-01 |  | N | Y | N | N | N | Y | N | N | N
Kora Power, Inc. | KP-INV-760-01 {240V} | Y | Y | Y | Y | Y | Y | N |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.5857 | 240 | 97.5 | CSA Group | [8/17/2026] | CSA Group | [8/17/2026] | [V1.08, V1.02] | 2026-10-01 | [8/17/2026] | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 13.35 |  |  | 271 | 380 | 500 | 0.75857 | 1.5171 | 2.2757 | 3.7928 | 5.6893 | 7.5857 | 95.214 | 96.6078 | 97.1112 | 97.4349 | 97.5337 | 97.4987 | 97.3214 | 95.8601 | 97.1947 | 97.6786 | 97.8404 | 97.7797 | 97.7298 | 97.6718 | 95.0767 | 96.615 | 97.41 | 97.5037 | 97.6476 | 97.3909 | 97.4216 | 2026-10-01 |  | N | Y | N | N | N | Y | N | N | N
Kora Power, Inc. | KP-INV-960-01 {240V} | Y | Y | Y | Y | Y | Y | N |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.5752 | 240 | 97.5 | CSA Group | [8/17/2026] | CSA Group | [8/17/2026] | [V1.08, V1.02] | 2026-10-01 | [8/17/2026] | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 13.35 |  |  | 257 | 380 | 500 | 0.95752 | 1.915 | 2.8726 | 4.7876 | 7.1814 | 9.5752 | 95.5716 | 96.9652 | 97.2989 | 97.5667 | 97.3513 | 97.0646 | 97.2854 | 96.4655 | 97.5565 | 97.7877 | 97.8147 | 97.7869 | 97.5106 | 97.7147 | 95.5032 | 96.9894 | 97.3765 | 97.569 | 97.4942 | 97.2838 | 97.3804 | 2026-10-01 |  | N | Y | N | N | N | Y | N | N | N
Kora Power, Inc. | KP-INV-114-01 {240V} | Y | Y | Y | Y | Y | Y | N |  | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.3612 | 240 | 97.5 | CSA Group | [8/17/2026] | CSA Group | [8/17/2026] | [V1.08, V1.02] | 2026-10-01 | [8/17/2026] | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 13.35 |  |  | 305 | 380 | 500 | 1.1361 | 2.2722 | 3.4084 | 5.6806 | 8.5209 | 11.3612 | 95.4936 | 97.0984 | 97.3469 | 97.5337 | 97.2494 | 96.9259 | 97.2268 | 96.3704 | 97.3767 | 97.7788 | 97.5807 | 97.5045 | 97.4531 | 97.4991 | 95.4259 | 97.3169 | 97.5648 | 97.6753 | 97.5094 | 97.1914 | 97.442 | 2026-10-01 |  | N | Y | N | N | N | Y | N | N | N
Kowint Energy (Shenzhen) Co., Ltd. | KSL-8KU-A {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 8.111 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 20.205 |  |  | 150 | 360 | 430 | 0.8111 | 1.6222 | 2.4333 | 4.0555 | 6.0832 | 8.111 | 93.836 | 95.318 | 95.642 | 95.8 | 95.492 | 95.582 | 95.5042 | 94.262 | 96.192 | 96.604 | 96.92 | 96.6 | 96.288 | 96.5382 | 94.044 | 96.13 | 96.518 | 96.864 | 96.724 | 96.4 | 96.5756 | 2025-02-03
Kowint Energy (Shenzhen) Co., Ltd. | KSL-8KU-B {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 8.1809 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 19.254 |  |  | 150 | 360 | 430 | 0.81809 | 1.6362 | 2.4543 | 4.0905 | 6.1357 | 8.1809 | 93.944 | 95.376 | 95.752 | 95.916 | 95.522 | 95.56 | 95.5638 | 94.308 | 96.218 | 96.68 | 96.842 | 96.584 | 96.23 | 96.5227 | 93.938 | 96.068 | 96.616 | 96.926 | 96.772 | 96.24 | 96.6105 | 2025-02-03
Kowint Energy (Shenzhen) Co., Ltd. | KSL-12KU-A {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 12.1371 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 19.85 |  |  | 200 | 360 | 430 | 1.2137 | 2.4274 | 3.6411 | 6.0686 | 9.1028 | 12.1371 | 93.694 | 95.54 | 95.7 | 95.864 | 95.498 | 95.304 | 95.5193 | 94.212 | 96.206 | 96.618 | 96.8 | 96.544 | 96.338 | 96.4862 | 94.07 | 96.028 | 96.604 | 96.908 | 96.662 | 96.216 | 96.549 | 2025-02-03
Kowint Energy (Shenzhen) Co., Ltd. | KSL-12KU-B {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 12.2135 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 13.202 |  |  | 200 | 360 | 430 | 1.2214 | 2.4427 | 3.6641 | 6.1068 | 9.1601 | 12.2135 | 93.588 | 95.318 | 95.52 | 95.804 | 95.494 | 95.612 | 95.4831 | 94.262 | 96.132 | 96.662 | 96.872 | 96.622 | 96.294 | 96.544 | 94.002 | 96.18 | 96.74 | 96.876 | 96.678 | 96.362 | 96.5793 | 2025-02-03
Kowint Energy (Shenzhen) Co., Ltd. | KSL-16KU-A {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 16 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 16.1309 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 19.23 |  |  | 220 | 360 | 430 | 1.6131 | 3.2262 | 4.8393 | 8.0655 | 12.0982 | 16.1309 | 93.788 | 95.264 | 95.68 | 95.82 | 95.856 | 95.46 | 95.6952 | 94.188 | 96.134 | 96.65 | 96.838 | 96.602 | 96.238 | 96.5192 | 94.13 | 96.028 | 96.604 | 96.836 | 96.6 | 96.354 | 96.5103 | 2025-02-03
Kowint Energy (Shenzhen) Co., Ltd. | KSL-16KU-B {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 16 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 16.1988 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 20.465 |  |  | 220 | 360 | 430 | 1.6199 | 3.2398 | 4.8596 | 8.0994 | 12.1491 | 16.1988 | 93.662 | 95.358 | 95.802 | 95.93 | 95.51 | 96.18 | 95.5852 | 94.188 | 96.06 | 96.548 | 96.876 | 96.636 | 96.35 | 96.5348 | 94.088 | 95.998 | 96.536 | 96.946 | 96.692 | 96.25 | 96.5657 | 2025-02-03
LeadSolar Energy Co., Ltd | LS600 {240V} | N | N | Y | Y | Y | N | N | N | 500 W, 240 Vac Grid Support Utility Interactive Micro-Inverter | 0.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | CSA Group | [4/26/2019] | [V105] | 2018-10-15 | [4/26/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.09 |  |  | 27 | 36 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 94.6 | 95.4 | 95.6 | 95.6 | 95.4 | 94.9 | 95.4 | 94.2 | 95.6 | 95.2 | 95.9 | 95.7 | 95.3 | 95.6 | 93.7 | 93.8 | 94.8 | 95.9 | 95.7 | 95.5 | 95.5 | 2017-10-13 | 2019-05-01
LeadSolar Energy Co., Ltd | LS700S {208V} | N | N | Y | Y | Y | N | N | N | 600W, 208 Vac Grid Support Utility Interactive Inverter | 0.606 | 208 | 95.5 | No Information Submitted | No Information Submitted | CSA Group | [04/04/2019] | [V105LS700G2] | 2019-05-01 | [04/04/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.21 |  |  | 52 | 54 | 56 | 0.06058 | 0.12116 | 0.18174 | 0.3029 | 0.45435 | 0.60579 | 91.2178 | 94.3165 | 94.9482 | 95.4648 | 95.5662 | 95.3209 | 95.2221 | 90.0557 | 93.6949 | 94.9532 | 95.7014 | 95.816 | 95.5133 | 95.3368 | 90.1569 | 93.9414 | 95.0073 | 95.3558 | 95.8147 | 95.555 | 95.2885 | 2019-05-01
LeadSolar Energy Co., Ltd | LS600X {240V} | N | N | Y | Y | N | N | N | N | 700 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.708 | 240 | 96 | No Information Submitted | No Information Submitted | CSA Group | [03/19/2018] | [V105LS700G2HV1.1_789Boot] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.16 |  |  | 50 | 57 | 64 | 0.0708 | 0.1416 | 0.2124 | 0.354 | 0.531 | 0.708 | 89.3868 | 93.5464 | 95.134 | 96.2627 | 96.5776 | 96.3824 | 95.8893 | 90.1881 | 93.8539 | 95.2694 | 96.306 | 96.5948 | 96.5453 | 95.9793 | 87.474 | 92.8944 | 95.0621 | 96.0676 | 96.4861 | 96.4858 | 95.6873 | 2018-04-16 | 2018-10-15
LG Electronics Inc. | LG315E1K-A5 {208V} | N | N | Y | Y | Y | N | N | N | 315 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG315E1K-A5 {240V} | N | N | Y | Y | Y | N | N | N | 315 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG320E1K-A5 {208V} | N | N | Y | Y | Y | N | N | N | 320 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG320E1K-A5 {240V} | N | N | Y | Y | Y | N | N | N | 320 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1C-A5 {208V} | N | N | Y | Y | Y | N | N | N | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1C-A5 {240V} | N | N | Y | Y | Y | N | N | N | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1K-A5 {208V} | N | N | Y | Y | Y | N | N | N | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1K-A5 {240V} | N | N | Y | Y | Y | N | N | N | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG330E1C-A5 {208V} | N | N | Y | Y | Y | N | N | N | 330 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG330E1C-A5 {240V} | N | N | Y | Y | Y | N | N | N | 330 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.3 | 96.2 | 96.8 | 97.3 | 97.1 | 96.7 | 97 | 94.6 | 95.7 | 96.3 | 97.3 | 97.3 | 97.2 | 97 | 93.9 | 95.1 | 95.7 | 97 | 97.1 | 97 | 96.7 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG335E1C-A5 {208V} | N | N | Y | Y | Y | N | N | N | 335 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6 | 96.3 | 96.9 | 97.4 | 97.1 | 96.6 | 97 | 94.6 | 95.7 | 96.5 | 97.1 | 97.1 | 96.7 | 96.8 | 93.9 | 95 | 96 | 96.9 | 96.9 | 96.6 | 96.6 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG335E1C-A5 {240V} | N | N | Y | Y | Y | N | N | N | 335 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [6/29/2017] | [01.06.03] | 2018-10-15 | [6/29/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.3 | 96.2 | 96.8 | 97.3 | 97.1 | 96.7 | 97 | 94.6 | 95.7 | 96.3 | 97.3 | 97.3 | 97.2 | 97 | 93.9 | 95.1 | 95.7 | 97 | 97.1 | 97 | 96.7 | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG355A1C-A5 {208V} | N | N | Y | N | Y | N | N | N | 355 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG355Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | UL | [12/15/2017] | [A320UD260C] | No Information Submitted | [12/15/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.85 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 96 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 95.9 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8 | 95.7 | 2018-02-15
LG Electronics Inc. | LG355A1C-A5 {240V} | N | N | Y | N | Y | N | N | N | 355 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG355Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [12/15/2017] | [A320UD260C] | No Information Submitted | [12/15/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.16 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 96.9 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8 | 96.6 | 2018-02-15
LG Electronics Inc. | LG360A1C-A5 {208V} | N | N | Y | N | Y | N | N | N | 360 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG360Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | UL | [12/15/2017] | [A320UD260C] | No Information Submitted | [12/15/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.85 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 96 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 95.9 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8 | 95.7 | 2018-02-15
LG Electronics Inc. | LG360A1C-A5 {240V} | N | N | Y | N | Y | N | N | N | 360 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG360Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [12/15/2017] | [A320UD260C] | No Information Submitted | [12/15/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.16 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 96.9 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8 | 96.6 | 2018-02-15
LG Electronics Inc. | LG365A1C-A5 {208V} | N | N | Y | N | Y | N | N | N | 365 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG365Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | UL | [12/15/2017] | [A320UD260C] | No Information Submitted | [12/15/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.85 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 96 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 95.9 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8 | 95.7 | 2018-02-15
LG Electronics Inc. | LG365A1C-A5 {240V} | N | N | Y | N | Y | N | N | N | 365 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG365Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [12/15/2017] | [A320UD260C] | No Information Submitted | [12/15/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.16 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 96.9 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8 | 96.6 | 2018-02-15
LG Electronics Inc. | LG370A1C-A5 {208V} | N | N | Y | N | Y | N | N | N | 370 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG370Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | UL | [12/15/2017] | [A320UD260C] | No Information Submitted | [12/15/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.85 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 96 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 95.9 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8 | 95.7 | 2018-02-15
LG Electronics Inc. | LG370A1C-A5 {240V} | N | N | Y | N | Y | N | N | N | 370 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG370Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [12/15/2017] | [A320UD260C] | No Information Submitted | [12/15/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.16 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 96.9 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8 | 96.6 | 2018-02-15
LG Electronics Inc. | LG340M1K-L5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 340 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG340N1K-L5. Microinverter: LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-24 | [07/22/2020] | 2020-08-24 | UL | 2020-01-31 | 2020-08-24 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2020-08-21
LG Electronics Inc. | LG345M1K-L5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 345 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG345N1K-L5. Microinverter: LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-25 | [07/22/2020] | 2020-08-25 | UL | 2020-01-31 | 2020-08-25 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2020-08-21
LG Electronics Inc. | LG350M1K-L5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 350 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG350N1K-L5. Microinverter: LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-26 | [07/22/2020] | 2020-08-26 | UL | 2020-01-31 | 2020-08-26 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2020-08-21
LG Electronics Inc. | LG355M1C-N5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 355 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG355N1C-N5. Microinverter: LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-21 | [07/22/2020] | 2020-08-21 | UL | 2020-01-31 | 2020-08-21 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2020-08-21
LG Electronics Inc. | LG355M1K-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 355 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG355N1K-A6, Microinverter: LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-05-11
LG Electronics Inc. | LG360A1K-V5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 360 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG360Q1K-V5. Microinverter : LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [03/12/2020] | [A320UD3005] | 2020-05-01 | [03/12/2020] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 |  | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2020-05-01
LG Electronics Inc. | LG360M1C-N5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 360 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG360N1C-N5. Microinverter: LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-21 | [07/22/2020] | 2020-08-21 | UL | 2020-01-31 | 2020-08-21 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2020-08-21
LG Electronics Inc. | LG360M1K-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 360 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG360N1K-A6, Microinverter: LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-05-11
LG Electronics Inc. | LG365A1C-V5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 365 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365Q1C-V5. Microinverter : LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [09/04/2019] | [A320UD3005] | 2019-10-15 | [09/04/2019] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG365A1K-V5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 365 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365Q1K-V5. Microinverter : LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [03/12/2020] | [A320UD3005] | 2020-05-01 | [03/12/2020] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 |  | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2020-05-01
LG Electronics Inc. | LG365M1C-N5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 365 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365N1C-N5. Microinverter: LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-21 | [07/22/2020] | 2020-08-21 | UL | 2020-01-31 | 2020-08-21 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2020-08-21
LG Electronics Inc. | LG365M1K-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 365 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG365N1K-A6, Microinverter: LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-05-11
LG Electronics Inc. | LG370A1C-V5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 370 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG370Q1C-V5. Microinverter : LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [09/04/2019] | [A320UD3005] | 2019-10-15 | [09/04/2019] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG370M1C-N5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 370 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG370N1C-N5. Microinverter: LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-21 | [07/22/2020] | 2020-08-21 | UL | 2020-01-31 | 2020-08-21 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2020-08-21
LG Electronics Inc. | LG370M1K-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 370 W, 240Vac, Grid Support Utility Interactive, Monocrystalline ACPV module, black backsheet. DC Module: LG370N1K-A6, Microinverter: LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-05-11
LG Electronics Inc. | LG375A1C-V5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 375 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG375Q1C-V5. Microinverter : LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [09/04/2019] | [A320UD3005] | 2019-10-15 | [09/04/2019] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG375M1C-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 375 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG375N1C-A6, Microinverter: LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-05-11
LG Electronics Inc. | LG375M1K-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 375 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module : LG375N1K-A6, Microinverter : LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [08/03/2021] | [A320UD260C]; [A320UD3005] | 2021-09-13 | [08/03/2021] | 2021-09-13 | UL | 2020-01-31 | 2021-09-13 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-09-13
LG Electronics Inc. | LG380A1C-V5 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 380 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG380Q1C-V5. Microinverter : LM320UE-A2 {240V}. | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [09/04/2019] | [A320UD3005] | 2019-10-15 | [09/04/2019] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG380M1C-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 380 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG380N1C-A6, Microinverter: LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-05-11
LG Electronics Inc. | LG380M1K-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 380 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module : LG380N1K-A6, Microinverter : LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [08/03/2021] | [A320UD260C]; [A320UD3005] | 2021-09-13 | [08/03/2021] | 2021-09-13 | UL | 2020-01-31 | 2021-09-13 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-09-13
LG Electronics Inc. | LG385M1C-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 385 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG385N1C-A6, Microinverter: LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-05-11
LG Electronics Inc. | LG395A1C-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 395 W, 240Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG395Q1C-A6, Microinverter: LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-05-11
LG Electronics Inc. | LG400A1C-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 400 W, 240Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG400Q1C-A6, Microinverter: LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-05-11
LG Electronics Inc. | LG405A1C-A6 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 405 W, 240Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG405Q1C-A6, Microinverter: LM320UE-A2 {240V} | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2021-05-11
LG Electronics Inc. | LM320UE-A2 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 320 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.321 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [01/04/2018]; [08/23/2019] | [A320UD260C]; [A320UD3005] | 2019-10-01 | [01/04/2018] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 |  | N | Y | 0.15 |  |  | 32 | 35 | 42 | 0.032101 | 0.064203 | 0.096304 | 0.16051 | 0.24076 | 0.32101 | 92.782 | 96.0166 | 96.7121 | 97.2066 | 97.206 | 96.7859 | 96.8894 | 92.78 | 95.94 | 96.6431 | 97.1211 | 97.1514 | 96.8565 | 96.8339 | 92.188 | 95.7058 | 96.4603 | 96.8328 | 96.9735 | 96.7997 | 96.6189 | 2018-02-15 | 2020-05-01
LG Electronics Inc. | LG340M1K-L5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 340 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG340N1K-L5. Microinverter: LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-21 | [07/22/2020] | 2020-08-21 | UL | 2020-01-31 | 2020-08-21 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2020-08-21
LG Electronics Inc. | LG345M1K-L5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 345 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG345N1K-L5. Microinverter: LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-22 | [07/22/2020] | 2020-08-22 | UL | 2020-01-31 | 2020-08-22 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2020-08-21
LG Electronics Inc. | LG350M1K-L5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 350 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG350N1K-L5. Microinverter: LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-23 | [07/22/2020] | 2020-08-23 | UL | 2020-01-31 | 2020-08-23 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2020-08-21
LG Electronics Inc. | LG355M1C-N5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 355 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG355N1C-N5. Microinverter: LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-21 | [07/22/2020] | 2020-08-21 | UL | 2020-01-31 | 2020-08-21 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2020-08-21
LG Electronics Inc. | LG355M1K-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 355 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG355N1K-A6, Microinverter: LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-05-11
LG Electronics Inc. | LG360A1K-V5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 360 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG360Q1K-V5. Microinverter : LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/12/2020] | [A320UD3005] | 2020-05-01 | [03/12/2020] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 |  | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2020-05-01
LG Electronics Inc. | LG360M1C-N5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 360 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG360N1C-N5. Microinverter: LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-21 | [07/22/2020] | 2020-08-21 | UL | 2020-01-31 | 2020-08-21 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2020-08-21
LG Electronics Inc. | LG360M1K-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 360 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG360N1K-A6, Microinverter: LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-05-11
LG Electronics Inc. | LG365A1C-V5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 365 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365Q1C-V5. Microinverter : LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [09/04/2019] | [A320UD3005] | 2019-10-15 | [09/04/2019] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG365A1K-V5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 365 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365Q1K-V5. Microinverter : LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/12/2020] | [A320UD3005] | 2020-05-01 | [03/12/2020] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 |  | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2020-05-01
LG Electronics Inc. | LG365M1C-N5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 365 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG365N1C-N5. Microinverter: LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-21 | [07/22/2020] | 2020-08-21 | UL | 2020-01-31 | 2020-08-21 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2020-08-21
LG Electronics Inc. | LG365M1K-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 365 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module: LG365N1K-A6, Microinverter: LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-05-11
LG Electronics Inc. | LG370A1C-V5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 370 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG370Q1C-V5. Microinverter : LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [09/04/2019] | [A320UD3005] | 2019-10-15 | [09/04/2019] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG370M1C-N5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 370 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG370N1C-N5. Microinverter: LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [07/22/2020] | [A320UD260C, A320UD3005] | 2020-08-21 | [07/22/2020] | 2020-08-21 | UL | 2020-01-31 | 2020-08-21 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2020-08-21
LG Electronics Inc. | LG370M1K-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 370 W, 208Vac, Grid Support Utility Interactive, Monocrystalline ACPV module, black backsheet. DC Module: LG370N1K-A6, Microinverter: LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-05-11
LG Electronics Inc. | LG375A1C-V5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 375 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG375Q1C-V5. Microinverter : LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [09/04/2019] | [A320UD3005] | 2019-10-15 | [09/04/2019] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG375M1C-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 375 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG375N1C-A6, Microinverter: LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-05-11
LG Electronics Inc. | LG375M1K-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 375 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module : LG375N1K-A6, Microinverter : LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [08/03/2021] | [A320UD260C]; [A320UD3005] | 2021-09-13 | [08/03/2021] | 2021-09-13 | UL | 2020-01-31 | 2021-09-13 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-09-13
LG Electronics Inc. | LG380A1C-V5 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 380 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG380Q1C-V5. Microinverter : LM320UE-A2 {208V}. | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [09/04/2019] | [A320UD3005] | 2019-10-15 | [09/04/2019] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2019-10-15 | 2020-05-01
LG Electronics Inc. | LG380M1C-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 380 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG380N1C-A6, Microinverter: LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-05-11
LG Electronics Inc. | LG380M1K-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 380 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, black backsheet. DC Module : LG380N1K-A6, Microinverter : LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [08/03/2021] | [A320UD260C]; [A320UD3005] | 2021-09-13 | [08/03/2021] | 2021-09-13 | UL | 2020-01-31 | 2021-09-13 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-09-13
LG Electronics Inc. | LG385M1C-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 385 W, 208 Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG385N1C-A6, Microinverter: LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-05-11
LG Electronics Inc. | LG395A1C-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 395 W, 208Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG395Q1C-A6, Microinverter: LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-05-11
LG Electronics Inc. | LG400A1C-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 400 W, 208Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG400Q1C-A6, Microinverter: LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-05-11
LG Electronics Inc. | LG405A1C-A6 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 405 W, 208Vac, Grid Support Utility Interactive, monocrystalline ACPV module, white backsheet. DC Module: LG405Q1C-A6, Microinverter: LM320UE-A2 {208V} | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [04/10/2021] | [A320UD3005] | 2021-05-11 | [04/10/2021] | 2021-05-11 | UL | 2020-01-31 | 2021-05-11 | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2021-05-11
LG Electronics Inc. | LM320UE-A2 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 320 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.322 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [01/04/2018]; [08/23/2019] | [A320UD260C]; [A320UD3005] | 2019-10-01 | [01/04/2018] | 2020-05-01 | UL | 2020-01-31 | 2020-05-01 |  | N | Y | 0.11 |  |  | 32 | 35 | 42 | 0.032246 | 0.064491 | 0.096737 | 0.16123 | 0.24184 | 0.32246 | 93.5018 | 96.1192 | 96.2124 | 96.9334 | 96.762 | 95.8233 | 96.5226 | 93.3117 | 95.997 | 95.9932 | 96.8291 | 96.7108 | 96.0173 | 96.4432 | 92.7607 | 95.7248 | 95.5295 | 96.5977 | 96.5678 | 96.0934 | 96.2313 | 2018-02-15 | 2020-05-01
LG Electronics Inc. | D007KEEN261 {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 6656W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 6.656 | 208 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2018] | [1.4.1] | 2018-10-15 | [08/30/2018] | 2020-05-11 | CSA Group | 2020-03-26 | 2020-05-11 |  | Y | N | 1.15 |  |  | 270 | 380 | 450 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 94.5771 | 96.3015 | 96.9963 | 97.3878 | 97.2948 | 96.929 | 97.1019 | 95.9053 | 97.3314 | 97.7633 | 97.8619 | 97.5862 | 97.2138 | 97.5667 | 95.0392 | 96.9541 | 97.466 | 97.7308 | 97.5103 | 97.1462 | 97.4064 | 2018-10-01 | 2020-05-11
LG Electronics Inc. | D007KEEN261 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 7.68 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2018] | [1.4.1] | 2018-10-15 | [08/30/2018] | 2020-05-11 | CSA Group | 2020-03-26 | 2020-05-11 |  | Y | N | 1.19 |  |  | 270 | 380 | 450 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.1418 | 96.5566 | 97.3325 | 97.5972 | 97.5104 | 97.1304 | 97.3459 | 96.4957 | 97.6782 | 98.0328 | 98.0644 | 97.7762 | 97.4311 | 97.7942 | 95.7683 | 97.3217 | 97.8155 | 97.9581 | 97.748 | 97.4471 | 97.6847 | 2018-10-01 | 2020-05-11
Liniotech Energy Inc. | LNT5K0228UL {208V} | Y | Y | N | N | N | N | N | N | 5 kW, 208Vac Grid Support Utility Interactive PV and Battery Inverter | 5.02 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 92.68 | 95.27 | 95.93 | 96.35 | 96.16 | 95.99 | 95.98 | 93.57 | 95.86 | 96.53 | 97.03 | 97.08 | 96.97 | 96.8 | 93.73 | 95.93 | 96.5 | 96.81 | 96.9 | 96.81 | 96.65 | 2024-09-11
Liniotech Energy Inc. | LNT5K0228UL {240V} | Y | Y | N | N | N | N | N | N | 5 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 5.04 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.504 | 1.008 | 1.512 | 2.52 | 3.78 | 5.04 | 92.99 | 95.51 | 96.13 | 96.56 | 96.34 | 96.22 | 96.18 | 93.67 | 95.99 | 96.75 | 97.31 | 97.43 | 97.38 | 97.1 | 93.79 | 96.14 | 96.61 | 96.98 | 97.24 | 97.24 | 96.92 | 2024-09-11
Liniotech Energy Inc. | LNT6K0228UL {208V} | Y | Y | N | N | N | N | N | N | 6 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 6.124 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.612 | 1.225 | 1.837 | 3.062 | 4.593 | 6.124 | 91.51 | 94.38 | 95.44 | 96.15 | 96.2 | 96.02 | 95.81 | 93.61 | 95.95 | 96.7 | 97.16 | 97.14 | 97.02 | 96.88 | 93.01 | 95.45 | 96.32 | 96.9 | 96.93 | 96.76 | 96.61 | 2024-09-11
Liniotech Energy Inc. | LNT6K0228UL {240V} | Y | Y | N | N | N | N | N | N | 6 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 6.149 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.615 | 1.23 | 1.845 | 3.075 | 4.612 | 6.149 | 91.6 | 94.45 | 95.46 | 96.26 | 96.41 | 96.35 | 95.97 | 93.87 | 96.14 | 96.88 | 97.38 | 97.49 | 97.42 | 97.18 | 92.69 | 95.45 | 96.41 | 97.1 | 97.3 | 97.27 | 96.87 | 2024-09-11
Liniotech Energy Inc. | LNT7K0228UL {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 7.647 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.529 | 2.294 | 3.824 | 5.735 | 7.647 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 89.75 | 96.08 | 96.79 | 97.16 | 96.97 | 96.77 | 96.65 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2024-09-11
Liniotech Energy Inc. | LNT7K0228UL {208V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 7.648 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.53 | 2.294 | 3.824 | 5.736 | 7.648 | 92.95 | 95.54 | 96.21 | 96.65 | 96.45 | 96.19 | 96.26 | 93.74 | 96.07 | 96.79 | 97.16 | 96.97 | 96.77 | 96.8 | 94.06 | 96.23 | 96.77 | 97.12 | 96.91 | 96.7 | 96.78 | 2024-09-11
Liniotech Energy Inc. | LNT8K0228UL {240V} | Y | Y | N | N | N | N | N | N | 8 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 8.047 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.805 | 1.609 | 2.414 | 4.024 | 6.035 | 8.047 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 93.75 | 96.08 | 96.8 | 97.17 | 96.97 | 96.77 | 96.81 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2024-09-11
Liniotech Energy Inc. | LNT8K0228UL {208V} | Y | Y | N | N | N | N | N | N | 8 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 8.06 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 17.78 |  |  | 200 | 360 | 480 | 0.806 | 1.612 | 2.418 | 4.03 | 6.045 | 8.06 | 92.85 | 95.45 | 96.11 | 96.55 | 96.35 | 96.09 | 96.17 | 93.65 | 95.98 | 96.69 | 97.06 | 96.87 | 96.67 | 96.71 | 93.97 | 96.14 | 96.67 | 97.02 | 96.81 | 96.55 | 96.68 | 2024-09-11
Liniotech Energy Inc. | LNT12K0228UL {240V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 10.14 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.028 | 3.042 | 5.07 | 7.605 | 10.14 | 93.05 | 95.58 | 96.24 | 96.66 | 96.45 | 96.2 | 96.28 | 93.72 | 96.07 | 96.82 | 97.15 | 96.96 | 96.78 | 96.8 | 94.05 | 96.25 | 96.79 | 97.12 | 96.92 | 96.66 | 96.79 | 2024-09-11
Liniotech Energy Inc. | LNT10K0228UL {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 10.147 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.015 | 2.029 | 3.044 | 5.074 | 7.61 | 10.147 | 93 | 95.58 | 96.22 | 96.66 | 96.46 | 96.2 | 96.28 | 93.79 | 96.1 | 96.81 | 97.16 | 96.97 | 96.77 | 96.81 | 94.11 | 96.27 | 96.78 | 97.13 | 96.92 | 96.66 | 96.79 | 2024-09-11
Liniotech Energy Inc. | LNT10K0228UL {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 10.186 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.89 | 95.48 | 96.13 | 96.56 | 96.36 | 96.1 | 96.18 | 93.7 | 96.01 | 96.71 | 97.07 | 96.88 | 96.67 | 96.72 | 94.02 | 96.16 | 96.68 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-09-11
Liniotech Energy Inc. | LNT12K0228UL {208V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 10.186 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.91 | 95.48 | 96.12 | 96.56 | 96.36 | 96.1 | 96.18 | 93.66 | 96.02 | 96.72 | 97.07 | 96.88 | 96.68 | 96.72 | 94.07 | 96.17 | 96.67 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-09-11
Lion Energy | #50170167 Sanctuary 8K {208V} | Y | Y | Y | Y | Y | N | N | N | 8 kW, 208 Vac, Grid Support Utility Interactive Inverter | 7.827 | 208 | 94.5 | SGS | [3/2/2023] | SGS | [5/27/2021] | [COMM: f23b; MCU: Ver1585] | 2022-07-21 | [5/27/2021] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 14.2 |  |  | 240 | 370 | 425 | 0.78272 | 1.5654 | 2.3482 | 3.9136 | 5.8704 | 7.8272 | 91.5935 | 94.5306 | 94.7008 | 94.8172 | 94.2661 | 93.7306 | 94.3136 | 92.4554 | 95.1969 | 95.3682 | 95.4678 | 94.995 | 94.4074 | 95.0182 | 91.4596 | 94.7987 | 94.9704 | 95.2764 | 94.8404 | 94.2929 | 94.7828 | 2022-07-21 | 2023-04-03
Lion Energy | #50170167 Sanctuary 8K {240V} | Y | Y | Y | Y | Y | N | N | N | 8 kW, 240 Vac, Grid Support Utility Interactive Inverter | 7.898 | 240 | 95 | SGS | [3/2/2023] | SGS | [5/27/2021] | [COMM: f23b; MCU: Ver1585] | 2022-07-21 | [5/27/2021] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 18.8 |  |  | 240 | 370 | 425 | 0.7898 | 1.5796 | 2.3694 | 3.949 | 5.9235 | 7.898 | 91.6179 | 94.6876 | 94.7932 | 95.0759 | 94.5989 | 94.128 | 94.584 | 92.6051 | 95.3425 | 95.4495 | 95.7148 | 95.3412 | 94.8314 | 95.2978 | 91.4912 | 94.8318 | 95.0468 | 95.5105 | 95.268 | 94.8354 | 95.0979 | 2022-07-21 | 2023-04-03
Lion Energy | #50170168 {240V} | Y | Y | Y | Y | Y | Y | N | N | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 8.084 | 240 | 97.5 | SGS | [3/30/2023] | SGS | [3/30/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-05-21 | [3/29/2024] | 2024-05-21 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2023-06-01 | 2024-05-21
Lion Energy | Lion Hybrid Inverter 12kW {240V} | Y | Y | Y | Y | Y | N | N |  | 12 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 8.084 | 240 | 97.5 | SGS | [7/17/2024] | SGS | [6/27/2024] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-22 | [7/17/2024] | 2025-09-22 | CSA Group | 2024-12-16 |  |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.808 | 1.617 | 2.425 | 4.042 | 6.063 | 8.084 | 93.98 | 95.42 | 96.35 | 97.36 | 97.92 | 96.85 | 97.27 | 93.95 | 95.64 | 96.59 | 97.27 | 97.93 | 97.01 | 97.31 | 94.07 | 95.49 | 96.43 | 97.32 | 97.69 | 96.99 | 97.17 | 2025-09-22 | 2026-08-11 | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 12kW {208V} | Y | Y | Y | Y | Y | Y | N |  | 12 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter | 8.138 | 208 | 96.5 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2026-10-01 | 2026-06-24 | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 0.002 |  |  | 150 | 360 | 430 | 0.814 | 1.628 | 2.441 | 4.069 | 6.103 | 8.138 | 94.07 | 95.83 | 96.51 | 96.74 | 96.59 | 96.06 | 96.45 | 94.22 | 96.05 | 96.58 | 96.83 | 96.63 | 96.32 | 96.52 | 94.26 | 96.4 | 96.64 | 96.8 | 96.71 | 96.4 | 96.59 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 12kW {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 12 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 8.181 | 240 | 96 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2025-12-11 | 2025-05-09 | 2025-12-11 | CSA Group | 2025-05-10 |  |  | N | N | 19.254 |  |  | 150 | 360 | 430 | 0.818 | 1.636 | 2.454 | 4.09 | 6.136 | 8.181 | 93.94 | 95.38 | 95.75 | 95.92 | 95.52 | 95.56 | 95.56 | 94.31 | 96.22 | 96.68 | 96.84 | 96.58 | 96.23 | 96.52 | 93.94 | 96.07 | 96.62 | 96.93 | 96.77 | 96.24 | 96.61 | 2025-12-11 | 2026-10-01 | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Lion Hybrid Inverter 15kW {240V} | Y | Y | Y | Y | Y | N | N |  | 15 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 10.177 | 240 | 97 | SGS | [7/17/2024] | SGS | [6/27/2024] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-22 | [7/17/2024] | 2025-09-22 | CSA Group | 2024-12-16 |  |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.018 | 2.035 | 3.053 | 5.088 | 7.632 | 10.177 | 94.69 | 95.94 | 96.4 | 96.8 | 97.34 | 96.75 | 96.91 | 95.39 | 96.33 | 96.85 | 97.45 | 97.97 | 97.37 | 97.51 | 94.93 | 95.96 | 96.65 | 97.01 | 97.56 | 97.03 | 97.12 | 2025-09-22 | 2026-08-11 | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 18kW {208V} | Y | Y | Y | Y | Y | Y | N |  | 18 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter | 12.185 | 208 | 96 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2026-10-01 | 2026-06-24 | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 0.002 |  |  | 200 | 360 | 430 | 1.218 | 2.437 | 3.655 | 6.092 | 9.139 | 12.185 | 93.6 | 95.32 | 95.65 | 95.89 | 95.5 | 95.59 | 95.52 | 94.53 | 96.35 | 96.63 | 96.81 | 96.5 | 96.61 | 96.5 | 94.51 | 96.12 | 96.6 | 96.89 | 96.7 | 96.46 | 96.6 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 18kW {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 18 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 12.214 | 240 | 96 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2025-12-11 | 2025-05-09 | 2025-12-11 | CSA Group | 2025-05-10 |  |  | N | N | 13.202 |  |  | 200 | 360 | 430 | 1.221 | 2.443 | 3.664 | 6.107 | 9.16 | 12.214 | 93.59 | 95.32 | 95.52 | 95.8 | 95.49 | 95.61 | 95.48 | 94.26 | 96.13 | 96.66 | 96.87 | 96.62 | 96.29 | 96.54 | 94 | 96.18 | 96.74 | 96.88 | 96.68 | 96.36 | 96.58 | 2025-12-11 | 2026-10-01 | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 24kW {208V} | Y | Y | Y | Y | Y | Y | N |  | 24 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter | 16.178 | 208 | 96 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2026-10-01 | 2026-06-24 | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 0.002 |  |  | 220 | 360 | 430 | 1.618 | 3.236 | 4.854 | 8.089 | 12.134 | 16.178 | 93.95 | 95.2 | 95.77 | 95.85 | 95.48 | 95.39 | 95.51 | 94.47 | 96.42 | 96.58 | 96.83 | 96.53 | 96.55 | 96.51 | 94.28 | 96.29 | 96.57 | 96.81 | 96.74 | 96.43 | 96.6 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 24kW {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 24 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 16.199 | 240 | 96 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2025-12-11 | 2025-05-09 | 2025-12-11 | CSA Group | 2025-05-10 |  |  | N | N | 20.465 |  |  | 220 | 360 | 430 | 1.62 | 3.24 | 4.86 | 8.099 | 12.149 | 16.199 | 93.66 | 95.36 | 95.8 | 95.93 | 95.51 | 96.18 | 95.59 | 94.19 | 96.06 | 96.55 | 96.88 | 96.64 | 96.35 | 96.53 | 94.09 | 96 | 96.54 | 96.95 | 96.69 | 96.25 | 96.57 | 2025-12-11 | 2026-10-01 | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lite-On Technology Corporation | IN-HP5123US {120V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 120 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.0186 | 120 | 95.5 | Intertek | [12/27/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-11-01 | [9/10/2024] | 2024-11-01 | CSA Group | 2025-04-08 | 2025-04-21 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.846 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.218 | 95.95 | 95.686 | 95.0375 | 2024-11-01 | 2025-04-21
Lite-On Technology Corporation | IN-HP5123US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 9.0186 | 240 | 95.5 | Intertek | [12/27/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2025-01-02 | [9/10/2024] | 2025-01-02 | CSA Group | 2025-04-08 | 2025-04-21 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.846 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.218 | 95.95 | 95.686 | 95.0375 | 2025-01-02 | 2025-04-21
Lite-On Technology Corporation | IN-HP5113US {240V} | Y | Y | N | N | N | N | Y* |  | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality | 11.361 | 240 | 97.5 | CSA Group | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-06-30 |  |  | N | N | 13.3488 |  |  | 257 | 380 | 500 | 1.136 | 2.272 | 3.408 | 5.681 | 8.521 | 11.361 | 95.49 | 97.1 | 97.35 | 97.53 | 97.25 | 96.93 | 97.23 | 96.37 | 97.38 | 97.78 | 97.58 | 97.5 | 97.45 | 97.5 | 95.43 | 97.32 | 97.56 | 97.68 | 97.51 | 97.19 | 97.44 | 2025-09-02
Lunar Energy, Inc. | 10-005025 {240V} | Y | Y | N | N | N | N | Y* | N | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 9.675 | 240 | 95.5 | CSA Group | [1/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-10-23 | No Information Submitted |  | N | N | 29.61 |  |  | 380 | 415 | 450 | 0.967 | 1.935 | 2.902 | 4.837 | 7.256 | 9.675 | 90.73 | 94.46 | 95.73 | 96.51 | 96.64 | 96.43 | 96.15 | 89.53 | 93.61 | 95.12 | 96.09 | 96.32 | 96.16 | 95.71 | 87.44 | 92.74 | 94.32 | 95.59 | 95.91 | 95.83 | 95.15 | 2024-11-21 | 2025-10-21
MANGO POWER TECH INC. | LBZ-PV-400 {240V} | N | Y | Y | Y | Y | Y | N |  | 0.4 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.40012 | 240 | 97 | Intertek | [3/6/2026] | Intertek | [3/6/2026] | [vF003] | 2026-06-11 | [3/6/2026] | 2026-06-11 | No Information Submitted | No Information Submitted |  |  | N | Y | 0.05 |  |  | 36 | 45.5 | 55 | 0.040012 | 0.080024 | 0.12004 | 0.20006 | 0.30009 | 0.40012 | 94.8138 | 96.0122 | 95.4625 | 96.8187 | 96.8551 | 96.3749 | 96.5326 | 94.4454 | 95.8225 | 94.981 | 97.03 | 97.4236 | 97.2839 | 96.8416 | 93.9926 | 95.7869 | 95.9639 | 96.7465 | 97.4298 | 97.4893 | 96.8938 | 2026-06-11 |  | Y | N | N | N | N | N | N | N | N
MANGO POWER TECH INC. | LBZ-PV-400 {208V} | N | Y | Y | Y | Y | Y | N |  | 0.4 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.4002 | 208 | 97 | Intertek | [3/6/2026] | Intertek | [3/6/2026] | [vF003] | 2026-06-11 | [3/6/2026] | 2026-06-11 | No Information Submitted | No Information Submitted |  |  | N | Y | 0.05 |  |  | 36 | 45.5 | 55 | 0.04002 | 0.08004 | 0.12006 | 0.2001 | 0.30015 | 0.4002 | 95.0566 | 96.184 | 95.9216 | 97.0635 | 96.9408 | 96.4195 | 96.705 | 94.7953 | 96.0316 | 95.5563 | 97.1124 | 97.3701 | 97.1616 | 96.9179 | 94.2411 | 95.5982 | 95.1022 | 96.8228 | 97.1711 | 97.0882 | 96.6497 | 2026-06-11 |  | Y | N | N | N | N | N | N | N | N
MANGO POWER TECH INC. | LBZ-PV-500 {208V} | N | Y | Y | Y | Y | Y | N |  | 0.5 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.49918 | 208 | 97 | Intertek | [3/6/2026] | Intertek | [3/6/2026] | [vF003] | 2026-06-11 | [3/6/2026] | 2026-06-11 | No Information Submitted | No Information Submitted |  |  | N | Y | 0.05 |  |  | 36 | 45.5 | 55 | 0.049918 | 0.099836 | 0.14975 | 0.24959 | 0.37439 | 0.49918 | 95.3531 | 96.1577 | 96.6117 | 97.078 | 96.5724 | 95.7564 | 96.573 | 95.0674 | 95.6313 | 96.4449 | 97.3465 | 97.1849 | 96.7441 | 96.9456 | 94.5697 | 94.943 | 96.0472 | 97.0654 | 97.1052 | 96.788 | 96.7445 | 2026-06-11 |  | Y | N | N | N | N | N | N | N | N
MANGO POWER TECH INC. | LBZ-PV-500 {240V} | N | Y | Y | Y | Y | Y | N |  | 0.5 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.50036 | 240 | 97 | Intertek | [3/6/2026] | Intertek | [3/6/2026] | [vF003] | 2026-06-11 | [3/6/2026] | 2026-06-11 | No Information Submitted | No Information Submitted |  |  | N | Y | 0.05 |  |  | 36 | 45.5 | 55 | 0.050036 | 0.10007 | 0.15011 | 0.25018 | 0.37527 | 0.50036 | 95.3975 | 96.3257 | 96.3471 | 96.9544 | 96.5029 | 95.6865 | 96.4851 | 95.3001 | 96.5153 | 96.0113 | 97.3651 | 97.3493 | 96.9192 | 97.0469 | 95.1289 | 96.187 | 95.7047 | 97.1961 | 97.4924 | 97.328 | 97.0476 | 2026-06-11 |  | Y | N | N | N | N | N | N | N | N
MANGO POWER TECH INC. | M Hybrid Inverter 12kW {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.499 | 208 | 96.5 | Intertek | [9/13/2024] | Intertek | [9/13/2024] | [fA1.0] | 2024-12-11 | [8/26/2024] | 2024-12-11 | Intertek | 2022-07-26 | 2024-12-11 |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.05 | 2.1 | 3.15 | 5.25 | 7.875 | 10.499 | 93.48 | 95.27 | 95.93 | 95.85 | 95.61 | 95.29 | 95.58 | 95.07 | 96.66 | 97.03 | 97.31 | 97.1 | 96.41 | 96.99 | 94.29 | 96.71 | 97.16 | 96.95 | 96.77 | 96.47 | 96.74 | 2024-12-11
MANGO POWER TECH INC. | M Hybrid Inverter 12kW {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 11.933 | 240 | 97 | Intertek | [9/13/2024] | Intertek | [9/13/2024] | [fA1.0] | 2024-12-11 | [8/26/2024] | 2024-12-11 | Intertek | 2022-07-26 | 2024-12-11 |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.193 | 2.387 | 3.58 | 5.966 | 8.949 | 11.933 | 95.02 | 96.1 | 96.54 | 96.5 | 96.13 | 95.9 | 96.2 | 96.59 | 97.19 | 97.51 | 97.34 | 97.24 | 97.1 | 97.26 | 95.82 | 97.01 | 97.42 | 97.26 | 97.14 | 97.04 | 97.13 | 2024-12-11
MidNite Power Inc. | MN 15-12KW-AIO {240V} | Y | Y | N | N | N | N | Y* |  | 10.135 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 10.135 | 240 | 96.5 | SGS | [7/28/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-07-15 |  |  | N | N | 19.44 |  |  | 200 | 360 | 480 | 1.014 | 2.027 | 3.041 | 5.068 | 7.601 | 10.135 | 93.07 | 95.57 | 96.3 | 96.64 | 96.44 | 96.21 | 96.28 | 93.68 | 96.04 | 96.8 | 97.14 | 96.95 | 96.78 | 96.79 | 94.05 | 96.32 | 96.82 | 97.12 | 96.93 | 96.65 | 96.8 | 2025-12-22
MidNite Power Inc. | MN 15-12KW-AIO {208V} | Y | Y | N | N | N | N | Y* |  | 10.193 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 10.193 | 208 | 96.5 | SGS | [7/28/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-07-15 |  |  | N | N | 18.56 |  |  | 200 | 360 | 480 | 1.019 | 2.039 | 3.058 | 5.097 | 7.645 | 10.193 | 92.89 | 95.49 | 96.11 | 96.57 | 96.35 | 96.1 | 96.18 | 93.64 | 96.03 | 96.72 | 97.06 | 96.88 | 96.68 | 96.72 | 94.1 | 96.17 | 96.67 | 97 | 96.82 | 96.56 | 96.69 | 2025-12-22
MidNite Solar, Inc. | MN 15-12KW-AIO {240V} | Y | Y | N | N | N | N | Y* | N | 15 kW, 240 Vac Grid Support Interactive Hybrid Inverter with PCS functionality. | 10.135 | 240 | 96.6 | SGS | [5/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | No Information Submitted |  | N | N | 19.44 |  |  | 200 | 360 | 480 | 1.014 | 2.027 | 3.041 | 5.068 | 7.601 | 10.135 | 93.07 | 95.57 | 96.3 | 96.64 | 96.44 | 96.21 | 96.28 | 93.68 | 96.04 | 96.8 | 97.14 | 96.95 | 96.78 | 96.79 | 94.05 | 96.32 | 96.82 | 97.12 | 96.93 | 96.65 | 96.8 | 2024-07-11 | 2025-10-01
MPP SOLAR INC | LVX 12KW WP {120V} | Y | Y | N | N | N | N | N | N | 10 kW, 120 Vac Grid Support Utility Interactive Inverter | 9.0186 | 120 | 95.5 | Intertek | [2/6/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-10-01
MPP SOLAR INC | LVX 12KW WP {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.0186 | 240 | 95.5 | Intertek | [2/6/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-10-01
NeoVolta Inc. | NV7600 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7680 W, 208 Vac, 1-phase hybrid Grid Support Utility Interactive Inverter that works with PV and energy storage. Inverter is capable of PCS functionality. | 7.4473 | 208 | 96.5 | SGS | [7/14/2022] | SGS | [02/18/2019] | [Ver1585] | 2019-03-15 | [02/18/2019] | 2020-08-11 | CSA Group | 2020-06-22 | 2020-08-11 | The NV7600 inverter and batteries are components of the NV14 Energy Storage System. | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.74473 | 1.4895 | 2.2342 | 3.7237 | 5.5855 | 7.4473 | 91.4863 | 94.7602 | 95.3527 | 97.2963 | 97.1851 | 96.8599 | 96.6231 | 91.7 | 94.9639 | 95.4957 | 97.4288 | 97.2316 | 96.9297 | 96.715 | 91.9073 | 94.929 | 95.3698 | 97.3187 | 96.9256 | 97.0631 | 96.5278 | 2019-03-15 | 2022-12-01
NeoVolta Inc. | NV7600 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7680W, 240 Vac, 1-phase hybrid Grid Support Utility Interactive Inverter that works with PV and energy storage. Inverter is capable of PCS functionality. | 7.657 | 240 | 96.5 | SGS | [7/14/2022] | SGS | [02/18/2019] | [Ver1585] | 2019-03-15 | [02/18/2019] | 2020-08-11 | CSA Group | 2020-06-22 | 2020-08-11 | The NV7600 inverter and batteries are components of the NV14 Energy Storage System. | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.76571 | 1.5314 | 2.2971 | 3.8286 | 5.7428 | 7.6571 | 91.8196 | 94.911 | 95.5205 | 97.0796 | 96.988 | 97.1305 | 96.5277 | 91.6709 | 95.0008 | 95.7077 | 97.5465 | 97.4459 | 97.0835 | 96.8871 | 91.5513 | 95.0717 | 95.8584 | 97.6006 | 97.274 | 97.0868 | 96.8243 | 2019-03-15 | 2022-12-01
NeoVolta Inc. | NV12KAC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 12.0 kW, 240Vac, 1-Phase & 3-Phase Grid Support Utility Interactive Hybrid Inverter that works with PV and energy storage | 12.2135 | 240 | 96 | SGS | [8/18/2025] | SGS | [8/18/2025] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2025-11-21 | [8/18/2025] | 2025-11-21 | SGS | 2025-08-18 |  |  | N | N | 13.2 |  |  | 200 | 360 | 430 | 1.2214 | 2.4427 | 3.6641 | 6.1068 | 9.1601 | 12.2135 | 93.588 | 95.318 | 95.52 | 95.804 | 95.494 | 95.612 | 95.4831 | 94.262 | 96.132 | 96.662 | 96.872 | 96.622 | 96.294 | 96.544 | 94.002 | 96.18 | 96.74 | 96.876 | 96.678 | 96.362 | 96.5793 | 2025-11-21
NeoVolta Inc. | NV16KAC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 16.0 kW, 240Vac, 1-Phase & 3-Phase Grid Support Utility Interactive Hybrid Inverter that works with PV and energy storage | 16.199 | 240 | 96 | SGS | [8/18/2025] | SGS | [8/18/2025] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2025-11-21 | [8/18/2025] | 2025-11-21 | SGS | 2025-08-18 |  |  | N | N | 20.47 |  |  | 220 | 360 | 430 | 1.62 | 3.24 | 4.86 | 8.099 | 12.149 | 16.199 | 93.66 | 95.36 | 95.8 | 95.93 | 95.51 | 96.18 | 95.59 | 94.19 | 96.06 | 96.55 | 96.88 | 96.64 | 96.35 | 96.53 | 94.09 | 96 | 96.54 | 96.95 | 96.69 | 96.25 | 96.57 | 2025-11-21
NEXTRACKER LLC | NXPCS800K-HUD {800V} | Y | Y | N | N | N | N | N | N | 800 kW, 800 Vac Grid Support Power Conversion System with a 800 kVA liquid-immersed distribution transformer. | 801.42 | 800 | 98 | Intertek | [11/4/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 222.84 |  |  | 1200 | 1350 | 1500 | 80.142 | 160.284 | 240.426 | 400.71 | 601.065 | 801.42 | 96.8652 | 98.0112 | 98.3614 | 98.3467 | 98.2464 | 97.9889 | 98.2014 | 96.7678 | 97.9399 | 98.2903 | 98.3257 | 98.1778 | 97.9753 | 98.1439 | 96.6558 | 97.8785 | 98.2331 | 98.2773 | 98.1877 | 97.9314 | 98.1224 | 2023-05-11
NEXTRACKER LLC | NXPCS1670K-HUD {800V} | Y | Y | N | N | N | N | N | N | 1670 kW, 800 Vac Grid Support Power Conversion System with a 1670 kVA liquid-immersed distribution transformer | 1673.4 | 800 | 98.5 | Intertek | [11/4/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 223.1 |  |  | 1200 | 1350 | 1500 | 167.34 | 334.68 | 502.02 | 836.7 | 1255.05 | 1673.4 | 97.1002 | 98.1991 | 98.4358 | 98.4485 | 98.3052 | 98.1498 | 98.2897 | 96.9903 | 98.1322 | 98.3783 | 98.4244 | 98.2715 | 98.1189 | 98.2506 | 96.8708 | 98.0743 | 98.3233 | 98.3951 | 98.2361 | 98.0867 | 98.2098 | 2023-05-11
NEXTRACKER LLC | NXPCS3340K-HUD {800V} | Y | Y | N | N | N | N | N | N | 3340 kW, 800 Vac Grid Support Power Conversion System with a 3340 kVA liquid-immersed distribution transformer | 3347.8 | 800 | 98.5 | Intertek | [11/4/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 443.65 |  |  | 1200 | 1350 | 1500 | 334.78 | 669.56 | 1004.34 | 1673.9 | 2510.85 | 3347.8 | 97.3162 | 98.2973 | 98.567 | 98.5482 | 98.4398 | 98.2414 | 98.4158 | 97.1663 | 98.2314 | 98.5122 | 98.5619 | 98.4077 | 98.1954 | 98.3835 | 97.0754 | 98.1596 | 98.4893 | 98.4686 | 98.3606 | 98.1888 | 98.3287 | 2023-05-11
NEXTRACKER LLC | NXPCS5000K-HUD {800V} | Y | Y | N | N | N | N | N | N | 5000 kW, 800 Vac Grid Support Power Conversion System a 5000 kVA liquid-immersed distribution transformer | 5004.9 | 800 | 98.5 | Intertek | [11/4/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 638.04 |  |  | 1200 | 1350 | 1500 | 500.49 | 1000.98 | 1501.47 | 2502.45 | 3753.675 | 5004.9 | 97.3771 | 98.3426 | 98.6085 | 98.6082 | 98.4969 | 98.2626 | 98.4695 | 97.2268 | 98.269 | 98.5468 | 98.5963 | 98.4512 | 98.2467 | 98.4248 | 97.1517 | 98.2154 | 98.507 | 98.5246 | 98.4233 | 98.2089 | 98.3826 | 2023-05-11
Northern Electric & Power Co. Ltd | BDM-300-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 300 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.255 | 208 | 96.5 | Intertek | [2/8/2024] | Intertek | [2/2/2024] | [4200] | 2024-05-01 | [2/2/2024] | 2024-05-01 | Intertek | 2024-04-15 | 2024-05-01 |  | N | Y | 1.2 |  |  | 22 | 35 | 55 | 0.026 | 0.051 | 0.077 | 0.128 | 0.191 | 0.255 | 93.5 | 95.57 | 96.83 | 96.91 | 96.78 | 96.34 | 96.6 | 94.01 | 96.51 | 96.88 | 96.51 | 96.33 | 96.7 | 96.37 | 91.65 | 96.13 | 96.89 | 96.76 | 96.55 | 96.6 | 96.42 | 2024-05-01
Northern Electric & Power Co. Ltd | BDM-300-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 300 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.289 | 240 | 96.5 | Intertek | [2/8/2024] | Intertek | [2/2/2024] | [4200] | 2024-05-01 | [2/2/2024] | 2024-05-01 | Intertek | 2024-04-15 | 2024-05-01 |  | N | Y | 1.5 |  |  | 22 | 35 | 55 | 0.029 | 0.058 | 0.087 | 0.145 | 0.217 | 0.289 | 93.88 | 96.21 | 96.51 | 96.16 | 96.66 | 96.8 | 96.41 | 94.08 | 96.69 | 96.35 | 96.76 | 96.26 | 96.36 | 96.32 | 91.56 | 96.34 | 96.7 | 96.37 | 96.3 | 96.48 | 96.18 | 2024-05-01
Northern Electric & Power Co. Ltd | BDM-350-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 350 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.303 | 208 | 96.5 | Intertek | [2/8/2024] | Intertek | [2/2/2024] | [4200] | 2024-05-01 | [2/2/2024] | 2024-05-01 | Intertek | 2024-04-15 | 2024-05-01 |  | N | Y | 0.2 |  |  | 22 | 35 | 55 | 0.03 | 0.061 | 0.091 | 0.152 | 0.227 | 0.303 | 93.65 | 95.58 | 97.05 | 96.79 | 96.59 | 96.45 | 96.51 | 92.67 | 96.13 | 96.9 | 96.82 | 96.68 | 96.11 | 96.52 | 93.33 | 94.83 | 97.27 | 96.87 | 96.68 | 96.41 | 96.55 | 2024-05-01
Northern Electric & Power Co. Ltd | BDM-400-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 400 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.343 | 208 | 96.5 | Intertek | [2/8/2024] | Intertek | [2/2/2024] | [4200] | 2024-05-01 | [2/2/2024] | 2024-05-01 | Intertek | 2024-04-15 | 2024-05-01 |  | N | Y | 0.2 |  |  | 22 | 35 | 55 | 0.034 | 0.069 | 0.103 | 0.171 | 0.257 | 0.343 | 93.64 | 95.63 | 96.89 | 96.8 | 96.6 | 96.48 | 96.5 | 92.73 | 96.22 | 96.83 | 96.89 | 96.68 | 96.14 | 96.53 | 93.22 | 94.85 | 97.24 | 96.87 | 96.66 | 96.42 | 96.53 | 2024-05-01
Northern Electric & Power Co. Ltd | BDM-350-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 350 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.346 | 240 | 96.5 | Intertek | [2/8/2024] | Intertek | [2/2/2024] | [4200] | 2024-05-01 | [2/2/2024] | 2024-05-01 | Intertek | 2024-04-15 | 2024-05-01 |  | N | Y | 0.3 |  |  | 22 | 35 | 55 | 0.035 | 0.069 | 0.104 | 0.173 | 0.26 | 0.346 | 94.2 | 96.12 | 96.84 | 97.1 | 96.58 | 96.13 | 96.58 | 93.96 | 96.82 | 96.73 | 97.04 | 96.96 | 96.41 | 96.79 | 91.25 | 96.02 | 96.91 | 96.78 | 96.61 | 96.43 | 96.43 | 2024-05-01
Northern Electric & Power Co. Ltd | BDM-400-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 400 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.398 | 240 | 96.5 | Intertek | [2/8/2024] | Intertek | [2/2/2024] | [4200] | 2024-05-01 | [2/2/2024] | 2024-05-01 | Intertek | 2024-04-15 | 2024-05-01 |  | N | Y | 0.3 |  |  | 22 | 35 | 55 | 0.04 | 0.08 | 0.12 | 0.199 | 0.299 | 0.398 | 94.28 | 96.24 | 96.87 | 97.07 | 96.58 | 96.09 | 96.59 | 94 | 96.86 | 96.64 | 97.05 | 96.99 | 96.42 | 96.8 | 91.29 | 96.09 | 96.93 | 96.75 | 96.64 | 96.41 | 96.45 | 2024-05-01
Northern Electric & Power Co. Ltd | BDM-550 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 548 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.547 | 240 | 96.5 | Intertek | [3/23/2023] | Intertek | [3/23/2023] | [9200] | 2022-12-12 | [3/23/2023] | 2022-12-12 | Intertek | 2021-06-01 | 2022-12-12 |  | N | Y | 0.134 |  |  | 22 | 35 | 55 | 0.0547 | 0.1094 | 0.1641 | 0.2735 | 0.41025 | 0.547 | 93.1389 | 94.3133 | 96.1814 | 96.8312 | 96.8466 | 96.7662 | 96.4846 | 93.3029 | 95.3434 | 96.471 | 96.9361 | 96.8849 | 96.9119 | 96.627 | 92.586 | 94.433 | 96.4139 | 96.897 | 97.0204 | 96.9916 | 96.6135 | 2022-12-12 | 2023-05-11
Northern Electric & Power Co. Ltd | BDM-300X2-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 600 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.576 | 240 | 96.5 | Intertek | [4/2/2024] | Intertek | [3/25/2024] | [9200] | 2024-05-13 | [3/25/2024] | 2024-05-13 | Intertek | 2024-03-15 | 2024-05-13 |  | N | Y | 0.3 |  |  | 22 | 35 | 55 | 0.058 | 0.115 | 0.173 | 0.288 | 0.432 | 0.576 | 94.36 | 96.09 | 96.68 | 97.1 | 96.47 | 96.04 | 96.51 | 93.62 | 96.87 | 96.57 | 97.13 | 97.09 | 96.47 | 96.85 | 91.53 | 96.08 | 96.99 | 96.66 | 96.7 | 96.44 | 96.48 | 2024-05-13 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-300X2-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 600 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.59 | 208 | 96.5 | Intertek | [4/2/2024] | Intertek | [3/25/2024] | [9200] | 2024-05-13 | [3/25/2024] | 2024-05-13 | Intertek | 2024-03-15 | 2024-05-13 |  | N | Y | 0.2 |  |  | 22 | 35 | 55 | 0.059 | 0.118 | 0.177 | 0.295 | 0.443 | 0.59 | 93.22 | 95.48 | 97.05 | 96.81 | 96.68 | 96.58 | 96.55 | 92.61 | 96.81 | 96.86 | 96.87 | 96.67 | 95.95 | 96.55 | 93.38 | 94.58 | 96.81 | 96.83 | 96.83 | 96.29 | 96.55 | 2024-05-13 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-650 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 639 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.639 | 240 | 96.5 | Intertek | [3/23/2023] | Intertek | [3/23/2023] | [9200] | 2023-01-03 | [3/23/2023] | 2023-01-03 | Intertek | 2022-10-13 | 2023-01-03 |  | N | Y | 0.12 |  |  | 22 | 35 | 55 | 0.0639 | 0.1278 | 0.1917 | 0.3195 | 0.47925 | 0.639 | 93.3445 | 94.5083 | 96.7841 | 96.7477 | 96.473 | 96.6549 | 96.3537 | 93.6538 | 95.2673 | 96.554 | 96.9965 | 96.9256 | 96.7623 | 96.674 | 94.3935 | 95.7149 | 96.4688 | 96.8479 | 97.011 | 97.0235 | 96.7428 | 2023-01-03 | 2023-05-11
Northern Electric & Power Co. Ltd | BDM-800-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 700 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.707 | 208 | 96.5 | Intertek | [3/23/2023] | Intertek | [3/23/2023] | [9200] | 2021-08-11 | [3/23/2023] | 2021-08-11 | Intertek | 2021-06-01 | 2021-08-11 |  | N | Y | 0.1 |  |  | 22 | 35 | 55 | 0.0707 | 0.1414 | 0.2121 | 0.3535 | 0.53025 | 0.707 | 93.6599 | 95.599 | 96.961 | 96.8296 | 96.6237 | 96.4904 | 96.5309 | 92.606 | 96.1692 | 96.8496 | 96.8689 | 96.6824 | 96.1217 | 96.5249 | 93.4666 | 94.8875 | 97.0612 | 96.8756 | 96.6955 | 96.4379 | 96.5448 | 2021-08-11 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-800-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 768 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.772 | 240 | 96.5 | Intertek | [3/23/2023] | Intertek | [3/23/2023] | [9200] | 2021-08-11 | [3/23/2023] | 2021-08-11 | Intertek | 2021-06-01 | 2021-08-11 |  | N | Y | 0.1 |  |  | 22 | 35 | 55 | 0.0772 | 0.1544 | 0.2316 | 0.386 | 0.579 | 0.772 | 94.2089 | 95.8335 | 96.8654 | 97.0732 | 96.5892 | 96.0902 | 96.566 | 93.9535 | 96.8628 | 96.6484 | 97.0781 | 96.979 | 96.4291 | 96.8058 | 93.4666 | 95.9837 | 96.7742 | 96.7578 | 96.6548 | 96.416 | 96.5177 | 2021-08-11 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-800-277A {277V} | N | Y | Y | Y | Y | Y | Y* | Y | 800 VA, 277 Vac Grid Support Utility Interactive Microinverter | 0.79872 | 277 | 96.5 | Intertek | [11/11/2024] | Intertek | [11/11/2024] | [9200] | 2025-05-01 | [11/11/2024] | 2025-05-01 | Intertek | 2021-06-01 | 2025-05-01 |  | N | Y | 0.5 |  |  | 22 | 35 | 55 | 0.079872 | 0.15974 | 0.23962 | 0.39936 | 0.59904 | 0.79872 | 94.2058 | 96.1652 | 96.8645 | 97.076 | 96.5916 | 96.098 | 96.5846 | 93.9703 | 96.8612 | 96.6451 | 97.037 | 96.9898 | 96.4365 | 96.8035 | 91.2156 | 96.0087 | 96.9329 | 96.7421 | 97.0374 | 96.4303 | 96.6482 | 2025-05-01 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-1000-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 1000 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.819 | 208 | 96.5 | Intertek | [4/2/2024] | Intertek | [3/25/2024] | [9200] | 2024-05-13 | [3/25/2024] | 2024-05-13 | Intertek | 2024-03-15 | 2024-05-13 |  | N | Y | 0.1 |  |  | 22 | 35 | 55 | 0.082 | 0.164 | 0.246 | 0.409 | 0.614 | 0.819 | 94.17 | 96.57 | 96.78 | 96.65 | 96.23 | 96.55 | 96.34 | 94.36 | 96.57 | 96.94 | 96.9 | 96.62 | 96.56 | 96.62 | 93.51 | 95.11 | 96.91 | 96.81 | 96.56 | 96.74 | 96.47 | 2024-05-13 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-1000-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 1000 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.934 | 240 | 96.5 | Intertek | [4/2/2024] | Intertek | [3/25/2024] | [9200] | 2024-05-13 | [3/25/2024] | 2024-05-13 | Intertek | 2024-03-15 | 2024-05-13 |  | N | Y | 0.1 |  |  | 22 | 35 | 55 | 0.093 | 0.187 | 0.28 | 0.467 | 0.7 | 0.934 | 94.01 | 96.21 | 96.48 | 96.84 | 96.91 | 96.36 | 96.67 | 94.19 | 96.57 | 96.49 | 96.91 | 96.76 | 96.02 | 96.61 | 91.87 | 96.02 | 96.67 | 96.73 | 96.71 | 96.59 | 96.47 | 2024-05-13 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-1200-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 1200 VA, 208 Vac Grid Support Utility Interactive Microinverter | 1.07 | 208 | 96.5 | Intertek | [3/22/2024] | Intertek | [3/22/2024] | [4200] | 2024-06-03 | [3/15/2024] | 2024-06-03 | Intertek | 2024-03-15 | 2024-06-03 |  | N | Y | 0.1 |  |  | 22 | 35 | 55 | 0.107 | 0.214 | 0.321 | 0.535 | 0.803 | 1.07 | 93.89 | 95.72 | 96.97 | 96.66 | 96.46 | 96.66 | 96.44 | 92.71 | 96.19 | 96.74 | 96.86 | 96.46 | 96.44 | 96.41 | 93.56 | 94.79 | 96.92 | 96.7 | 96.69 | 96.45 | 96.48 | 2024-06-03 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-1200-LV {120V} | N | Y | Y | Y | Y | Y | Y* |  | 1.2 kW, 120 Vac Grid Support Utility Interactive Microinverter | 1.1935 | 120 | 96.5 | Intertek | [8/1/2025] | Intertek | [8/1/2025] | [4200] | 2025-09-22 | [8/1/2025] | 2025-09-22 | Intertek | 2025-07-31 |  |  | N | Y | 13.6 |  |  | 22 | 35 | 55 | 0.11935 | 0.2387 | 0.35805 | 0.59675 | 0.89512 | 1.1935 | 94.2978 | 96.0402 | 96.6533 | 97.1107 | 96.3945 | 96.0053 | 96.4549 | 93.5753 | 96.705 | 96.5438 | 97.101 | 97.0932 | 96.4098 | 96.8346 | 91.5907 | 95.9662 | 96.8222 | 96.6073 | 96.6452 | 96.3496 | 96.4076 | 2025-09-22 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-1200-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 1200 VA, 240 Vac Grid Support Utility Interactive Microinverter | 1.22 | 240 | 96.5 | Intertek | [3/22/2024] | Intertek | [3/22/2024] | [4200] | 2024-06-03 | [3/15/2024] | 2024-06-03 | Intertek | 2024-03-15 | 2024-06-03 |  | N | Y | 0.1 |  |  | 22 | 35 | 55 | 0.122 | 0.244 | 0.366 | 0.61 | 0.915 | 1.22 | 93.96 | 96.29 | 96.8 | 96.85 | 96.62 | 96.36 | 96.55 | 93.94 | 96.63 | 96.44 | 96.94 | 96.8 | 96.43 | 96.64 | 92.38 | 96.16 | 96.85 | 96.67 | 96.56 | 96.45 | 96.43 | 2024-06-03 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-1600-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 1600 VA, 208 Vac Grid Support Utility Interactive Microinverter | 1.331 | 208 | 96.5 | Intertek | [3/22/2024] | Intertek | [3/22/2024] | [4200] | 2024-06-03 | [3/15/2024] | 2024-06-03 | Intertek | 2024-03-15 | 2024-06-03 |  | N | Y | 0.2 |  |  | 22 | 35 | 55 | 0.133 | 0.266 | 0.399 | 0.666 | 0.998 | 1.331 | 93.52 | 95.52 | 96.92 | 96.87 | 96.84 | 96.43 | 96.63 | 92.72 | 96.16 | 96.9 | 96.76 | 96.56 | 95.88 | 96.43 | 93.48 | 94.93 | 97.42 | 96.57 | 96.84 | 96.28 | 96.6 | 2024-06-03 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-1600-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 1600 VA, 240 Vac Grid Support Utility Interactive Microinverter | 1.533 | 240 | 96.5 | Intertek | [3/22/2024] | Intertek | [3/22/2024] | [4200] | 2024-06-03 | [3/15/2024] | 2024-06-03 | Intertek | 2024-03-15 | 2024-06-03 |  | N | Y | 0.3 |  |  | 22 | 35 | 55 | 0.153 | 0.307 | 0.46 | 0.766 | 1.149 | 1.533 | 94.61 | 96.06 | 96.98 | 97.09 | 96.63 | 95.69 | 96.61 | 93.89 | 96.83 | 96.6 | 97.04 | 96.91 | 96.23 | 96.74 | 95.94 | 96.09 | 96.96 | 96.84 | 96.75 | 96.37 | 96.71 | 2024-06-03 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-1600-LV {120V} | N | Y | Y | Y | Y | Y | Y* |  | 1.6 kW, 120 Vac Grid Support Utility Interactive Microinverter | 1.597 | 120 | 96.5 | Intertek | [8/1/2025] | Intertek | [8/1/2025] | [4200] | 2025-09-22 | [8/1/2025] | 2025-09-22 | Intertek | 2025-07-31 |  |  | N | Y | 9.7 |  |  | 22 | 35 | 55 | 0.1597 | 0.3194 | 0.4791 | 0.7985 | 1.1978 | 1.597 | 94.4741 | 96.0795 | 96.7206 | 97.0844 | 96.5454 | 96.1172 | 96.5521 | 93.6185 | 96.745 | 96.8284 | 97.1173 | 97.0612 | 96.4398 | 96.8605 | 91.5295 | 96.0651 | 96.9791 | 96.6504 | 96.6837 | 96.458 | 96.4638 | 2025-09-22 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-2000-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 2000 VA, 208 Vac Grid Support Utility Interactive Microinverter | 1.663 | 208 | 96.5 | Intertek | [3/22/2024] | Intertek | [3/22/2024] | [4200] | 2024-06-03 | [3/15/2024] | 2024-06-03 | Intertek | 2024-03-15 | 2024-06-03 |  | N | Y | 0.2 |  |  | 22 | 35 | 55 | 0.166 | 0.333 | 0.499 | 0.831 | 1.247 | 1.663 | 93.41 | 95.78 | 96.55 | 97.07 | 96.82 | 96.59 | 96.64 | 92.95 | 96.34 | 96.71 | 96.94 | 96.62 | 96.18 | 96.52 | 93.9 | 94.25 | 97.1 | 96.85 | 96.7 | 96.52 | 96.53 | 2024-06-03 | 2025-11-12
Northern Electric & Power Co. Ltd | BDM-2000-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 2000 VA, 240 Vac Grid Support Utility Interactive Microinverter | 1.998 | 240 | 96.5 | Intertek | [3/22/2024] | Intertek | [3/22/2024] | [4200] | 2024-06-03 | [3/15/2024] | 2024-06-03 | Intertek | 2024-03-15 | 2024-06-03 |  | N | Y | 0.4 |  |  | 22 | 35 | 55 | 0.2 | 0.4 | 0.599 | 0.999 | 1.499 | 1.998 | 94.42 | 96.15 | 96.87 | 97.22 | 96.64 | 96.21 | 96.65 | 94.07 | 96.86 | 97.86 | 96.96 | 97.03 | 96.58 | 96.97 | 91.12 | 96.14 | 97.12 | 96.91 | 96.8 | 96.57 | 96.59 | 2024-06-03 | 2025-11-12
Northern Electric & Power Co. Ltd | BDHX-2000T-208 {208V} | Y | Y | N | N | N | N | Y* |  | 2.078 kW, 208 Vac Grid Support Utility Interactive Microinverter | 2.078 | 208 | 95.5 | Intertek | [4/3/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2026-03-19 |  |  | N | Y | 0.54 |  |  | 22 | 37 | 55 | 0.208 | 0.416 | 0.624 | 1.039 | 1.559 | 2.078 | 95.48 | 95.55 | 95.36 | 95.92 | 95.57 | 95.7 | 95.62 | 95.59 | 95.51 | 95.67 | 95.92 | 95.57 | 95.69 | 95.66 | 95.59 | 95.81 | 95.7 | 95.92 | 95.57 | 95.78 | 95.68 | 2026-07-21 |  | Y | N | N | N | N | N | Y | N | N
Northern Electric & Power Co. Ltd | BDH-8KSP-LB {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 8 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 6.9318 | 208 | 96.5 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.26 |  |  | 220 | 360 | 500 | 0.69318 | 1.3864 | 2.0795 | 3.4659 | 5.1989 | 6.9318 | 94.8824 | 95.1559 | 96.3164 | 96.1494 | 95.5083 | 95.3277 | 95.6882 | 95.5148 | 96.247 | 97.1412 | 96.7237 | 96.2569 | 96.1172 | 96.4239 | 96.9461 | 97.549 | 98.4544 | 98.0507 | 97.2182 | 97.2592 | 97.5491 | 2025-10-13
Northern Electric & Power Co. Ltd | BDH-8KSP-LB {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 8 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.99 | 240 | 97 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.56 |  |  | 220 | 360 | 500 | 0.799 | 1.598 | 2.397 | 3.995 | 5.993 | 7.99 | 95.48 | 96.12 | 96.98 | 96.71 | 96.05 | 95.48 | 96.25 | 95.99 | 97.25 | 98.05 | 97.46 | 96.95 | 96.48 | 97.14 | 96.37 | 97.29 | 98.33 | 98.08 | 97.88 | 97.11 | 97.85 | 2025-10-13
Northern Electric & Power Co. Ltd | BDH-10KSP-LB {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 8.671 | 208 | 96.5 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.22 |  |  | 220 | 360 | 500 | 0.867 | 1.734 | 2.601 | 4.336 | 6.503 | 8.671 | 94.64 | 95.52 | 96.33 | 95.96 | 95.58 | 95.35 | 95.7 | 95.54 | 96.3 | 97.06 | 96.86 | 96.55 | 96.2 | 96.61 | 96.16 | 97.09 | 97.88 | 97.5 | 97.52 | 96.94 | 97.45 | 2025-10-13
Northern Electric & Power Co. Ltd | BDH-10KSP-LB {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.9914 | 240 | 97 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.53 |  |  | 220 | 360 | 500 | 0.99914 | 1.9983 | 2.9974 | 4.9957 | 7.4936 | 9.9914 | 95.4308 | 96.2429 | 97.1609 | 96.681 | 96.131 | 95.6355 | 96.3229 | 96.0699 | 96.9269 | 97.9414 | 97.4965 | 97.0743 | 96.7243 | 97.202 | 96.7257 | 97.6788 | 98.5843 | 98.2362 | 97.8247 | 97.2475 | 97.9222 | 2025-10-13
Northern Electric & Power Co. Ltd | BDH-12KSP-LB {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 12 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.517 | 208 | 96.5 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.25 |  |  | 220 | 360 | 500 | 1.1517 | 2.3034 | 3.4551 | 5.7585 | 8.6378 | 11.517 | 94.5637 | 95.0747 | 96.2219 | 95.9651 | 95.651 | 95.6393 | 95.7126 | 95.8105 | 96.2916 | 97.011 | 96.9717 | 96.4131 | 96.0207 | 96.5523 | 96.2546 | 96.9778 | 98.424 | 97.2969 | 97.1415 | 96.943 | 97.2745 | 2025-10-13
Northern Electric & Power Co. Ltd | BDH-12KSP-LB {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 12 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.969 | 240 | 97 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.48 |  |  | 220 | 360 | 500 | 1.1969 | 2.3938 | 3.5907 | 5.9845 | 8.9767 | 11.969 | 95.5377 | 96.4105 | 97.2613 | 96.6277 | 96.3047 | 95.9192 | 96.4427 | 96.1402 | 97.3142 | 97.9948 | 97.5526 | 96.9976 | 96.7655 | 97.2038 | 96.9953 | 97.7455 | 98.6046 | 98.4266 | 97.9344 | 97.2686 | 98.0379 | 2025-10-13
Northern Electric & Power Co. Ltd | Neptune25K {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 25 kW, 480 Vac Grid Support Utility Interactive Inverter | 24.888 | 480 | 98.5 | CSA Group | [10/31/2023] | CSA Group | [10/31/2023] | [A2] | 2024-02-12 | [10/31/2023] | 2024-02-12 | CSA Group | 2023-11-14 | 2024-02-12 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 2.489 | 4.978 | 7.466 | 12.444 | 18.666 | 24.888 | 98.31 | 98.52 | 98.58 | 98.6 | 98.48 | 98.31 | 98.51 | 98.28 | 98.54 | 98.61 | 98.58 | 98.51 | 98.43 | 98.52 | 98.32 | 98.49 | 98.53 | 98.53 | 98.44 | 98.38 | 98.46 | 2024-02-12
Northern Electric & Power Co. Ltd | Neptune30K-LV {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 30 kW, 208 Vac Grid Support Utility Interactive Inverter | 29.878 | 208 | 97 | CSA Group | [10/31/2023] | CSA Group | [10/31/2023] | [A2] | 2024-02-12 | [10/31/2023] | 2024-02-12 | CSA Group | 2023-11-14 | 2024-02-12 |  | N | N | 1.394 |  |  | 340 | 580 | 680 | 2.988 | 5.976 | 8.963 | 14.939 | 22.408 | 29.878 | 96.25 | 97.44 | 97.69 | 97.55 | 96.93 | 96.47 | 97.13 | 96.06 | 97.23 | 97.54 | 97.46 | 96.84 | 96.41 | 97.02 | 96.09 | 97.08 | 97.42 | 97.36 | 96.81 | 96.36 | 96.96 | 2024-02-12
Northern Electric & Power Co. Ltd | Neptune30K {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac Grid Support Utility Interactive Inverter | 29.883 | 480 | 98.5 | CSA Group | [10/31/2023] | CSA Group | [10/31/2023] | [A2] | 2024-02-12 | [10/31/2023] | 2024-02-12 | CSA Group | 2023-11-14 | 2024-02-12 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 2.988 | 5.977 | 8.965 | 14.941 | 22.412 | 29.883 | 97.84 | 98.48 | 98.58 | 98.53 | 98.48 | 98.23 | 98.47 | 98.05 | 98.49 | 98.59 | 98.53 | 98.44 | 98.29 | 98.46 | 98 | 98.44 | 98.58 | 98.56 | 98.49 | 98.31 | 98.48 | 2024-02-12
Northern Electric & Power Co. Ltd | Neptune33K {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 33 kW, 480 Vac Grid Support Utility Interactive Inverter | 32.865 | 480 | 98.5 | CSA Group | [10/31/2023] | CSA Group | [10/31/2023] | [A2] | 2024-02-12 | [10/31/2023] | 2024-02-12 | CSA Group | 2023-11-14 | 2024-02-12 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 3.287 | 6.573 | 9.86 | 16.433 | 24.649 | 32.865 | 98.21 | 98.56 | 98.6 | 98.54 | 98.46 | 98.33 | 98.48 | 98.38 | 98.63 | 98.63 | 98.62 | 98.53 | 98.38 | 98.55 | 98.23 | 98.6 | 98.62 | 98.58 | 98.51 | 98.35 | 98.52 | 2024-02-12
Northern Electric & Power Co. Ltd | Neptune36K {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac Grid Support Utility Interactive Inverter | 35.866 | 480 | 98.5 | CSA Group | [10/31/2023] | CSA Group | [10/31/2023] | [A2] | 2024-02-12 | [10/31/2023] | 2024-02-12 | CSA Group | 2023-11-14 | 2024-02-12 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 3.587 | 7.173 | 10.76 | 17.933 | 26.899 | 35.866 | 98.07 | 98.58 | 98.63 | 98.53 | 98.42 | 98.19 | 98.45 | 98.47 | 98.61 | 98.67 | 98.62 | 98.5 | 98.28 | 98.54 | 98.18 | 98.54 | 98.61 | 98.53 | 98.46 | 98.12 | 98.47 | 2024-02-12
Northern Electric & Power Co. Ltd | Neptune40K {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 40 kW, 480 Vac Grid Support Utility Interactive Inverter | 39.841 | 480 | 98.5 | CSA Group | [10/31/2023] | CSA Group | [10/31/2023] | [A2] | 2024-02-12 | [10/31/2023] | 2024-02-12 | CSA Group | 2023-11-14 | 2024-02-12 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 3.984 | 7.968 | 11.952 | 19.92 | 29.88 | 39.841 | 97.47 | 98.22 | 98.59 | 98.59 | 98.58 | 98.15 | 98.5 | 98.08 | 98.33 | 98.61 | 98.55 | 98.53 | 97.96 | 98.48 | 97.93 | 98.3 | 98.55 | 98.59 | 98.54 | 97.84 | 98.48 | 2024-02-12
Northern Electric & Power Co. Ltd | Neptune50K {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter | 49.848 | 480 | 98.5 | CSA Group | [10/31/2023] | CSA Group | [10/31/2023] | [A2] | 2024-02-12 | [10/31/2023] | 2024-02-12 | CSA Group | 2023-11-14 | 2024-02-12 |  | N | N | 3.2724 |  |  | 580 | 720 | 850 | 4.985 | 9.97 | 14.955 | 24.924 | 37.386 | 49.848 | 97.74 | 98.52 | 98.55 | 98.63 | 98.46 | 98.16 | 98.46 | 97.43 | 98.38 | 98.69 | 98.73 | 98.57 | 98.36 | 98.55 | 97.5 | 98.2 | 98.53 | 98.64 | 98.51 | 98.34 | 98.47 | 2024-02-12
Northern Electric & Power Co. Ltd | Neptune60K {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 59.898 | 480 | 98.5 | CSA Group | [10/31/2023] | CSA Group | [10/31/2023] | [A2] | 2024-02-12 | [10/31/2023] | 2024-02-12 | CSA Group | 2023-11-14 | 2024-02-12 |  | N | N | 3.1623 |  |  | 580 | 720 | 850 | 5.99 | 11.98 | 17.969 | 29.949 | 44.923 | 59.898 | 97.76 | 98.42 | 98.58 | 98.57 | 98.47 | 98.17 | 98.46 | 97.62 | 98.48 | 98.69 | 98.71 | 98.58 | 98.38 | 98.56 | 97.48 | 98.31 | 98.5 | 98.63 | 98.49 | 98.22 | 98.46 | 2024-02-12
Northern Electric & Power Co. Ltd | Neptune75K {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive Inverter | 74.574 | 480 | 98.5 | CSA Group | [9/19/2023] | CSA Group | [9/19/2023] | [1C] | 2024-03-01 | [9/19/2023] | 2024-03-01 | CSA Group | 2023-09-22 | 2024-03-01 |  | N | N | 2 |  |  | 550 | 730 | 850 | 7.4574 | 14.9148 | 22.3723 | 37.2871 | 55.9306 | 74.5742 | 97.1519 | 97.7396 | 97.9756 | 98.0455 | 97.9997 | 97.7577 | 97.9474 | 98.2493 | 98.6811 | 98.7466 | 98.7034 | 98.5655 | 98.3686 | 98.5995 | 97.9069 | 98.3276 | 97.9953 | 98.5443 | 98.3567 | 98.2661 | 98.3288 | 2024-03-01
Northern Electric & Power Co. Ltd | Neptune100K {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac, 3-Phase Transformerless Grid Support Utility Interactive PV Inverter | 99.368 | 480 | 98 | CSA Group | [9/19/2023] | CSA Group | [9/19/2023] | [1C] | 2024-03-01 | [9/19/2023] | 2024-03-01 | CSA Group | 2023-09-22 | 2024-03-01 |  | N | N | 2 |  |  | 550 | 730 | 850 | 9.9368 | 19.8736 | 29.8105 | 49.6841 | 74.5262 | 99.3682 | 97.2872 | 97.736 | 97.7798 | 97.8454 | 97.733 | 97.4318 | 97.7295 | 98.5174 | 98.7659 | 98.7368 | 98.6111 | 98.3712 | 98.1531 | 98.4801 | 98.2563 | 98.5521 | 98.5681 | 98.4642 | 98.2153 | 98.045 | 98.3199 | 2024-03-01
ONE SUN, MEXICO S.A. DE C.V. | 1S480-10k {480V} | N | N | Y | Y | Y | N | N | N | 10 kW, 480 Vac, Grid Support Utility Interactive Inverter | 9.975 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [10/26/2018] | [0.28] | 2018-11-15 | [10/26/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 8.3 |  |  | 450 | 750 | 850 | 0.9975 | 1.995 | 2.9925 | 4.9875 | 7.4812 | 9.975 | 94.1157 | 96.7771 | 97.3429 | 97.7271 | 97.6957 | 97.5171 | 97.4619 | 94.11 | 96.8457 | 97.6443 | 98.1614 | 98.22 | 98.14 | 97.9015 | 93.1871 | 96.46 | 97.4557 | 98.1029 | 98.2386 | 98.2 | 97.8232 | 2018-11-15
OutBack Power | SBX5048-120/240 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac, Multimode Grid Support Utility Interactive PV and Battery Inverter with PCS Functionality | 4.985 | 240 | 94 | No Information Submitted | No Information Submitted | UL | [08/08/2018];[08/08/2018];[01/28/2021] | [NPC:0.0.0.2.2.0.9352,PBM:0.3.1.0.0.0.9359];[NPC:0.0.0.3.0.2.10015,PBM:0.3.1.0.0.6.10006];[NPC:0.0.0.3.0.2.10164,PMB:0.3.1.0.0.6.10482] | 2019-04-02 | [08/08/2018];[08/08/2018];[01/28/2021] | 2021-03-11 | SunSpec Alliance | 2020-01-28 | 2020-03-23 |  | Y | N | 24.85 |  |  | 250 | 420 | 550 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 85.9112 | 91.8786 | 93.404 | 94.206 | 94.0833 | 93.7751 | 93.575 | 87.0418 | 92.4308 | 94.1918 | 94.8976 | 95.0953 | 94.8942 | 94.4799 | 85.3624 | 91.926 | 93.5091 | 94.4779 | 94.7418 | 94.6173 | 94.0163 | 2018-09-17 | 2021-03-11
OutBack Power | PHXL480-10k {480V} | N | N | Y | Y | Y | N | N | N | 10 kW, 480 Vac, 3 phase Grid Support Utility Interactive Inverter | 9.975 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [11/27/2018] | [0.28] | 2019-02-15 | [11/27/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 8.3 |  |  | 450 | 750 | 850 | 0.9975 | 1.995 | 2.9925 | 4.9875 | 7.4812 | 9.975 | 94.1157 | 96.7771 | 97.3429 | 97.7271 | 97.6957 | 97.5171 | 97.4619 | 94.11 | 96.8457 | 97.6443 | 98.1614 | 98.22 | 98.14 | 97.9015 | 93.1871 | 96.46 | 97.4557 | 98.1029 | 98.2386 | 98.2 | 97.8232 | 2019-02-15
Oxford Intelligent Energy Co., Ltd. | OE 5KHS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 5.02 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 92.68 | 95.27 | 95.93 | 96.35 | 96.16 | 95.99 | 95.98 | 93.57 | 95.86 | 96.53 | 97.03 | 97.08 | 96.97 | 96.8 | 93.73 | 95.93 | 96.5 | 96.81 | 96.9 | 96.81 | 96.65 | 2024-03-11 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 5KHS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 5.04 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.504 | 1.008 | 1.512 | 2.52 | 3.78 | 5.04 | 92.99 | 95.51 | 96.13 | 96.56 | 96.34 | 96.22 | 96.18 | 93.67 | 95.99 | 96.75 | 97.31 | 97.43 | 97.38 | 97.1 | 93.79 | 96.14 | 96.61 | 96.98 | 97.24 | 97.24 | 96.92 | 2024-03-11 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 6KHS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 6.124 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.612 | 1.225 | 1.837 | 3.062 | 4.593 | 6.124 | 91.51 | 94.38 | 95.44 | 96.15 | 96.2 | 96.02 | 95.81 | 93.61 | 95.95 | 96.7 | 97.16 | 97.14 | 97.02 | 96.88 | 93.01 | 95.45 | 96.32 | 96.9 | 96.93 | 96.76 | 96.61 | 2024-03-11 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 6KHS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 6.149 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.615 | 1.23 | 1.845 | 3.075 | 4.612 | 6.149 | 91.6 | 94.45 | 95.46 | 96.26 | 96.41 | 96.35 | 95.97 | 93.87 | 96.14 | 96.88 | 97.38 | 97.49 | 97.42 | 97.18 | 92.69 | 95.45 | 96.41 | 97.1 | 97.3 | 97.27 | 96.87 | 2024-03-11 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 7K6HS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 7.647 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.529 | 2.294 | 3.824 | 5.735 | 7.647 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 89.75 | 96.08 | 96.79 | 97.16 | 96.97 | 96.77 | 96.65 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2023-12-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 7K6HS-T2/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 7.647 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.529 | 2.294 | 3.824 | 5.735 | 7.647 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 89.75 | 96.08 | 96.79 | 97.16 | 96.97 | 96.77 | 96.65 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2024-11-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 7K6HS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 7.648 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.53 | 2.294 | 3.824 | 5.736 | 7.648 | 92.95 | 95.54 | 96.21 | 96.65 | 96.45 | 96.19 | 96.26 | 93.74 | 96.07 | 96.79 | 97.16 | 96.97 | 96.77 | 96.8 | 94.06 | 96.23 | 96.77 | 97.12 | 96.91 | 96.7 | 96.78 | 2024-03-11 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 7K6HS-T2/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 7.648 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.53 | 2.294 | 3.824 | 5.736 | 7.648 | 92.95 | 95.54 | 96.21 | 96.65 | 96.45 | 96.19 | 96.26 | 93.74 | 96.07 | 96.79 | 97.16 | 96.97 | 96.77 | 96.8 | 94.06 | 96.23 | 96.77 | 97.12 | 96.91 | 96.7 | 96.78 | 2024-11-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 8KHS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 8.047 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.805 | 1.609 | 2.414 | 4.024 | 6.035 | 8.047 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 93.75 | 96.08 | 96.8 | 97.17 | 96.97 | 96.77 | 96.81 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2023-12-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 8KHS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 8.06 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 17.78 |  |  | 200 | 360 | 480 | 0.806 | 1.612 | 2.418 | 4.03 | 6.045 | 8.06 | 92.85 | 95.45 | 96.11 | 96.55 | 96.35 | 96.09 | 96.17 | 93.65 | 95.98 | 96.69 | 97.06 | 96.87 | 96.67 | 96.71 | 93.97 | 96.14 | 96.67 | 97.02 | 96.81 | 96.55 | 96.68 | 2023-12-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 11K4HS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 10.14 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.028 | 3.042 | 5.07 | 7.605 | 10.14 | 93.05 | 95.58 | 96.24 | 96.66 | 96.45 | 96.2 | 96.28 | 93.72 | 96.07 | 96.82 | 97.15 | 96.96 | 96.78 | 96.8 | 94.05 | 96.25 | 96.79 | 97.12 | 96.92 | 96.66 | 96.79 | 2024-11-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 10KHS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 10.147 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.015 | 2.029 | 3.044 | 5.074 | 7.61 | 10.147 | 93 | 95.58 | 96.22 | 96.66 | 96.46 | 96.2 | 96.28 | 93.79 | 96.1 | 96.81 | 97.16 | 96.97 | 96.77 | 96.81 | 94.11 | 96.27 | 96.78 | 97.13 | 96.92 | 96.66 | 96.79 | 2023-12-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 10KHS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 10.186 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.89 | 95.48 | 96.13 | 96.56 | 96.36 | 96.1 | 96.18 | 93.7 | 96.01 | 96.71 | 97.07 | 96.88 | 96.67 | 96.72 | 94.02 | 96.16 | 96.68 | 96.99 | 96.82 | 96.56 | 96.68 | 2023-12-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 11K4HS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 10.186 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.91 | 95.48 | 96.12 | 96.56 | 96.36 | 96.1 | 96.18 | 93.66 | 96.02 | 96.72 | 97.07 | 96.88 | 96.68 | 96.72 | 94.07 | 96.17 | 96.67 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-11-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
PANASONIC CORPORATION OF NORTH AMERICA | EVHB-I7 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid support utility-interactive Power Conversion System. Capable of PCS functionality. | 7.6082 | 240 | 96.5 | CSA Group | [5/30/2024] | CSA Group | [5/30/2024] | [V1.05, V1.03, V1.10] | 2023-07-21 | [5/10/2023] | 2023-07-21 | Intertek | 2023-05-22 | 2023-07-21 |  | N | N | 7.3 |  |  | 234.1 | 365.5 | 498.4 | 0.756 | 1.512 | 2.267 | 3.779 | 5.668 | 7.558 | 95.53 | 96.94 | 97.21 | 97.32 | 96.95 | 96.71 | 96.99 | 96.67 | 97.84 | 97.97 | 97.94 | 97.77 | 97.53 | 97.78 | 96.06 | 97.25 | 97.82 | 97.87 | 97.75 | 97.62 | 97.68 | 2023-07-21 | 2025-02-03
PhaseGreen Technology Inc. | PhG-P5K0LNA-M {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 5.0897 | 240 | 97 | SGS | [10/23/2023] | SGS | [10/23/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-01-02 | [10/23/2023] | 2024-01-02 | SGS | 2023-10-20 | 2024-01-02 |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2023-05-11 | 2026-03-11 | N | N | N | N | N | N | Y | N | No Information Submitted
PhaseGreen Technology Inc. | PhG-P6K0LNA-M {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 6.117 | 240 | 97 | SGS | [10/23/2023] | SGS | [10/23/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-01-02 | [10/23/2023] | 2024-01-02 | SGS | 2023-10-20 | 2024-01-02 |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2023-05-11 | 2026-03-11 | N | N | N | N | N | N | Y | N | No Information Submitted
PhaseGreen Technology Inc. | PhG-P7K6LNA-M {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 7.765 | 240 | 97 | SGS | [10/23/2023] | SGS | [10/23/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-01-02 | [10/23/2023] | 2024-01-02 | SGS | 2023-10-20 | 2024-01-02 |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2023-05-11 | 2026-03-11 | N | N | N | N | N | N | Y | N | No Information Submitted
PhaseGreen Technology Inc. | PhG-P8K0LNA-M {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 8.084 | 240 | 97.5 | SGS | [10/23/2023] | SGS | [10/23/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-01-02 | [10/23/2023] | 2024-01-02 | SGS | 2023-10-20 | 2024-01-02 |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2023-05-11 | 2026-03-11 | N | N | N | N | N | N | Y | N | No Information Submitted
PhaseGreen Technology Inc. | PhG-P10K0LNA-M {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 10.177 | 240 | 97 | SGS | [10/23/2023] | SGS | [10/23/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-01-02 | [10/23/2023] | 2024-01-02 | SGS | 2023-10-20 | 2024-01-02 |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2023-05-11 | 2026-03-11 | N | N | N | N | N | N | Y | N | No Information Submitted
Pika Energy | X7603 {240V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.585 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [11/22/2017] | [11430] | 2018-10-15 | [11/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1.29 |  |  | 390 | 400 | 420 | 0.76 | 1.52 | 2.28 | 3.79 | 5.69 | 7.59 | 91.7 | 95.9 | 96.6 | 97.3 | 97.2 | 97 | 96.9 | 91 | 95.4 | 96.5 | 97.3 | 97.1 | 97 | 96.8 | 90.5 | 95.2 | 96.3 | 96.9 | 97 | 96.9 | 96.5 | 2018-04-02 | 2018-10-15
Pika Energy | X7601 {240V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.587 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [11/22/2017] | [11430] | 2018-10-15 | [11/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.29 |  |  | 390 | 400 | 420 | 0.76 | 1.52 | 2.28 | 3.79 | 5.69 | 7.59 | 91.7 | 95.9 | 96.6 | 97.3 | 97.2 | 97 | 96.9 | 91 | 95.4 | 96.5 | 97.3 | 97.1 | 97 | 96.8 | 90.5 | 95.2 | 96.3 | 96.9 | 97 | 96.9 | 96.5 | 2017-12-15 | 2018-10-15
Pika Energy | X7602 {240V} | Y | N | Y | Y | Y | Y | Y | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.587 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [11/11/2019] | [12982] | 2018-10-15 | [11/11/2019] | 2020-03-23 | SunSpec Alliance | 2019-11-26 | 2020-03-23 |  | N | N | 1.29 |  |  | 390 | 400 | 420 | 0.759 | 1.517 | 2.276 | 3.793 | 5.689 | 7.586 | 91.67 | 95.89 | 96.62 | 97.26 | 97.24 | 97.04 | 96.87 | 91.01 | 95.4 | 96.52 | 97.26 | 97.15 | 97.01 | 96.75 | 90.48 | 95.21 | 96.33 | 96.86 | 97.02 | 96.91 | 96.55 | 2017-12-15 | 2020-03-23
Pika Energy | X11403 {208V} | N | N | Y | Y | Y | N | N | N | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.18 | 208 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [11/22/2017] | [11430] | 2018-10-15 | [11/22/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 0.13 |  |  | 390 | 400 | 420 | 1.12 | 2.24 | 3.35 | 5.59 | 8.39 | 11.18 | 97.2 | 97.4 | 97.6 | 97.6 | 97.4 | 97.1 | 97.5 | 97 | 97.3 | 97.7 | 97.5 | 97.3 | 96.9 | 97.3 | 95.8 | 97.2 | 97.3 | 97.4 | 97.1 | 96.9 | 97.1 | 2018-04-02 | 2018-10-15
Pika Energy | X11402 {208V} | Y | N | Y | Y | Y | Y | Y | Y | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.187 | 208 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [11/11/2019] | [12982] | 2018-10-15 | [11/11/2019] | 2020-03-23 | SunSpec Alliance | 2019-11-26 | 2020-03-23 |  | N | N | 0.13 |  |  | 390 | 400 | 420 | 1.12 | 2.24 | 3.36 | 5.59 | 8.39 | 11.19 | 97.2 | 97.4 | 97.6 | 97.6 | 97.4 | 97.1 | 97.5 | 97 | 97.3 | 97.7 | 97.5 | 97.3 | 96.9 | 97.3 | 95.8 | 97.2 | 97.3 | 97.4 | 97.1 | 96.9 | 97.1 | 2017-12-15 | 2020-03-23
PointGuard Energy Inc. | PG Controller 3.8 {240V} | Y | Y | N | N | N | N | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 3.843 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-09-03 |  | N | N | 3.26 |  |  | 270 | 360 | 480 | 0.384 | 0.769 | 1.153 | 1.922 | 2.882 | 3.843 | 93 | 95.49 | 96.34 | 96.87 | 97 | 97.03 | 96.66 | 94.25 | 96.34 | 97.04 | 97.48 | 97.56 | 97.51 | 97.29 | 92.95 | 95.41 | 96.34 | 96.99 | 97.17 | 97.19 | 96.78 | 2024-09-03 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
PointGuard Energy Inc. | PG Controller 4.8 {240V} | Y | Y | N | N | N | N | Y* | Y | 4.8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 4.808 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-09-03 |  | N | N | 3.32 |  |  | 270 | 360 | 480 | 0.481 | 0.962 | 1.442 | 2.404 | 3.606 | 4.808 | 93.93 | 96.05 | 96.64 | 96.96 | 97.03 | 96.96 | 96.79 | 95.12 | 96.82 | 97.3 | 97.54 | 97.54 | 97.41 | 97.37 | 93.95 | 96.02 | 96.71 | 97.11 | 97.2 | 97.14 | 96.93 | 2024-09-03 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
PointGuard Energy Inc. | PG Controller 5.7 {240V} | Y | Y | N | N | N | N | Y* | Y | 5.7 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 5.776 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-09-03 |  | N | N | 3.37 |  |  | 270 | 360 | 480 | 0.578 | 1.155 | 1.733 | 2.888 | 4.332 | 5.776 | 94.61 | 96.34 | 96.8 | 97 | 97 | 96.89 | 96.84 | 95.59 | 97.05 | 97.42 | 97.55 | 97.46 | 97.32 | 97.37 | 94.49 | 96.33 | 96.88 | 97.16 | 97.16 | 97.05 | 96.97 | 2024-09-03 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
PointGuard Energy Inc. | PG Controller 7.6 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 7.689 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-09-03 |  | N | N | 3.36 |  |  | 270 | 360 | 480 | 0.769 | 1.538 | 2.307 | 3.844 | 5.767 | 7.689 | 95.46 | 96.7 | 96.9 | 97.03 | 96.89 | 96.69 | 96.84 | 96.37 | 97.33 | 97.52 | 97.51 | 97.32 | 97.2 | 97.34 | 95.42 | 96.76 | 97.07 | 97.18 | 97.04 | 96.87 | 96.98 | 2024-09-03 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
PointGuard Energy Inc. | PG Controller 9.6 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 9.653 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-09-03 |  | N | N | 3.35 |  |  | 270 | 360 | 480 | 0.965 | 1.931 | 2.896 | 4.827 | 7.24 | 9.653 | 96 | 96.87 | 96.99 | 96.96 | 96.72 | 96.46 | 96.77 | 96.79 | 97.48 | 97.55 | 97.39 | 97.23 | 97.1 | 97.29 | 95.96 | 96.98 | 97.16 | 97.12 | 96.91 | 96.78 | 96.94 | 2024-09-03 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
PointGuard Energy Inc. | PG Controller 11.4 {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 11.4601 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-06-21 |  | N | N | 3.3 |  |  | 270 | 360 | 480 | 1.146 | 2.292 | 3.438 | 5.7301 | 8.5951 | 11.4601 | 96.1745 | 96.9088 | 97.1227 | 97.0709 | 96.8249 | 96.4944 | 96.874 | 96.8655 | 97.5022 | 97.6109 | 97.5252 | 97.1814 | 97.1326 | 97.3061 | 96.1379 | 97.0621 | 97.2015 | 97.1814 | 97.0036 | 96.6911 | 97.0174 | 2024-06-21 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
POMCube Inc. | PNZ-10K1N2-NA0 {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 10 kW, 240 Vac Split Phase, Transformerless Grid Support Utility Interactive Hybrid Inverter for PV and Energy Storage Application. The inverter is capable of PCS functionality. | 9.92 | 240 | 94 | Intertek | [12/1/2023] | Intertek | [12/1/2023] | ARM/10010, pv/10050, pcs/10025 | 2021-03-22 | [04/14/2021] | 2021-05-21 | SunSpec Alliance | 2021-03-23 | 2021-05-21 |  | N | N | 21.92 |  |  | 250 | 360 | 530 | 0.99227 | 1.9845 | 2.9768 | 4.9613 | 7.442 | 9.9227 | 91.2728 | 93.8665 | 92.8466 | 93.9818 | 94.1882 | 93.8918 | 93.8364 | 94.433 | 94.2287 | 93.579 | 93.0905 | 94.0391 | 94.2974 | 93.8229 | 93.3697 | 95.1764 | 93.7928 | 94.5765 | 94.8844 | 95.1581 | 94.6565 | 2021-03-22 | 2024-02-21
Power Center | D350-M1A-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 350 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.303 | 208 | 96.5 | Intertek | [11/14/2024] | Intertek | [11/14/2024] | [4200] | 2025-02-03 | [11/14/2024] | 2025-02-03 | Intertek | 2024-12-04 | 2025-02-03 |  | N | Y | 0.2 |  |  | 22 | 35 | 55 | 0.03 | 0.061 | 0.091 | 0.152 | 0.227 | 0.303 | 93.65 | 95.58 | 97.05 | 96.79 | 96.59 | 96.45 | 96.51 | 92.67 | 96.13 | 96.9 | 96.82 | 96.68 | 96.11 | 96.52 | 93.33 | 94.83 | 97.27 | 96.87 | 96.68 | 96.41 | 96.55 | 2025-02-03
Power Center | D400-M1A-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 400 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.343 | 208 | 96.5 | Intertek | [11/14/2024] | Intertek | [11/14/2024] | [4200] | 2025-02-03 | [11/14/2024] | 2025-02-03 | Intertek | 2024-12-04 | 2025-02-03 |  | N | Y | 0.2 |  |  | 22 | 35 | 55 | 0.034 | 0.069 | 0.103 | 0.171 | 0.257 | 0.343 | 93.64 | 95.63 | 96.89 | 96.8 | 96.6 | 96.48 | 96.5 | 92.73 | 96.22 | 96.83 | 96.89 | 96.68 | 96.14 | 96.53 | 93.22 | 94.85 | 97.24 | 96.87 | 96.66 | 96.42 | 96.53 | 2025-02-03
Power Center | D350-M1A-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 350 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.346 | 240 | 96.5 | Intertek | [11/14/2024] | Intertek | [11/14/2024] | [4200] | 2025-02-03 | [11/14/2024] | 2025-02-03 | Intertek | 2024-12-04 | 2025-02-03 |  | N | Y | 0.3 |  |  | 22 | 35 | 55 | 0.035 | 0.069 | 0.104 | 0.173 | 0.26 | 0.346 | 94.2 | 96.12 | 96.84 | 97.1 | 96.58 | 96.13 | 96.58 | 93.96 | 96.82 | 96.73 | 97.04 | 96.96 | 96.41 | 96.79 | 91.25 | 96.02 | 96.91 | 96.78 | 96.61 | 96.43 | 96.43 | 2025-02-03
Power Center | D350-M1 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.3495 | 240 | 96.5 | CSA Group | [3/17/2023] | CSA Group | [05/13/2022] | [V01.01.00] | 2022-09-12 | [05/13/2022] | 2022-09-12 | CSA Group | 2022-05-05 | 2022-09-01 |  | N | Y | 0.105 |  |  | 33 | 40 | 48 | 0.03495 | 0.069899 | 0.10485 | 0.17475 | 0.26212 | 0.3495 | 95.7117 | 96.1284 | 96.1965 | 96.4329 | 96.6064 | 96.1053 | 96.436 | 95.9087 | 95.9847 | 96.3587 | 96.3192 | 96.625 | 96.449 | 96.4594 | 95.3735 | 95.831 | 96.4129 | 96.1844 | 96.6999 | 96.5412 | 96.4528 | 2022-09-12 | 2023-05-01
Power Center | D400-M1A-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 400 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.398 | 240 | 96.5 | Intertek | [11/14/2024] | Intertek | [11/14/2024] | [4200] | 2025-02-03 | [11/14/2024] | 2025-02-03 | Intertek | 2024-12-04 | 2025-02-03 |  | N | Y | 0.3 |  |  | 22 | 35 | 55 | 0.04 | 0.08 | 0.12 | 0.199 | 0.299 | 0.398 | 94.28 | 96.24 | 96.87 | 97.07 | 96.58 | 96.09 | 96.59 | 94 | 96.86 | 96.64 | 97.05 | 96.99 | 96.42 | 96.8 | 91.29 | 96.09 | 96.93 | 96.75 | 96.64 | 96.41 | 96.45 | 2025-02-03
Power Center | D600-M2A-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 600 VA, 240 Vac Grid Support Utility Interactive | 0.576 | 240 | 96.5 | Intertek | [11/11/2024] | Intertek | [11/11/2024] | [9200] | 2025-02-03 | [11/11/2024] | 2025-02-03 | Intertek | 2024-12-04 | 2025-02-03 |  | N | Y | 0.3 |  |  | 22 | 35 | 55 | 0.058 | 0.115 | 0.173 | 0.288 | 0.432 | 0.576 | 94.36 | 96.09 | 96.68 | 97.1 | 96.47 | 96.04 | 96.51 | 93.62 | 96.87 | 96.57 | 97.13 | 97.09 | 96.47 | 96.85 | 91.53 | 96.08 | 96.99 | 96.66 | 96.7 | 96.44 | 96.48 | 2025-02-03
Power Center | D600-M2A-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 600 VA, 208 Vac Grid Support Utility Interactive | 0.59 | 208 | 96.5 | Intertek | [11/11/2024] | Intertek | [11/11/2024] | [9200] | 2025-02-03 | [11/11/2024] | 2025-02-03 | Intertek | 2024-12-04 | 2025-02-03 |  | N | Y | 0.2 |  |  | 22 | 35 | 55 | 0.059 | 0.118 | 0.177 | 0.295 | 0.443 | 0.59 | 93.22 | 95.48 | 97.05 | 96.81 | 96.68 | 96.58 | 96.55 | 92.61 | 96.81 | 96.86 | 96.87 | 96.67 | 95.95 | 96.55 | 93.38 | 94.58 | 96.81 | 96.83 | 96.83 | 96.29 | 96.55 | 2025-02-03
Power Center | D700-M2 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 696 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.697 | 240 | 96.5 | CSA Group | [3/17/2023] | CSA Group | [05/13/2022] | [V01.01.00] | 2022-09-12 | [05/13/2022] | 2022-09-12 | CSA Group | 2022-05-05 | 2022-09-01 |  | N | Y | 0.11 |  |  | 33 | 42 | 48 | 0.06975 | 0.1395 | 0.20925 | 0.34875 | 0.52312 | 0.6975 | 95.4666 | 96.1751 | 96.2274 | 96.4896 | 96.53 | 96.1505 | 96.406 | 95.7929 | 96.0559 | 96.3859 | 96.3322 | 96.632 | 96.4896 | 96.47 | 95.7024 | 95.901 | 96.3897 | 96.3322 | 96.5935 | 96.5753 | 96.443 | 2022-09-12 | 2023-05-01
Power Center | D800-M2A-208A {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 700 VA, 208 Vac Grid Support Utility Interactive Inverter | 0.707 | 208 | 96.5 | Intertek | [11/11/2024] | Intertek | [11/11/2024] | [9200] | 2025-02-03 | [11/11/2024] | 2025-02-03 | Intertek | 2024-12-04 | 2025-02-03 |  | N | Y | 0.1 |  |  | 22 | 35 | 55 | 0.0707 | 0.1414 | 0.2121 | 0.3535 | 0.53025 | 0.707 | 93.6599 | 95.599 | 96.961 | 96.8296 | 96.6237 | 96.4904 | 96.5309 | 92.606 | 96.1692 | 96.8496 | 96.8689 | 96.6824 | 96.1217 | 96.5249 | 93.4666 | 94.8875 | 97.0612 | 96.8756 | 96.6955 | 96.4379 | 96.5448 | 2025-02-03
Power Center | D800-M2A-240A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 768 VA, 240 Vac Grid Support Utility Interactive Inverter | 0.772 | 240 | 96.5 | Intertek | [11/11/2024] | Intertek | [11/11/2024] | [9200] | 2025-02-03 | [11/11/2024] | 2025-02-03 | Intertek | 2024-12-04 | 2025-02-03 |  | N | Y | 0.1 |  |  | 22 | 35 | 55 | 0.0772 | 0.1544 | 0.2316 | 0.386 | 0.579 | 0.772 | 94.2089 | 95.8335 | 96.8654 | 97.0732 | 96.5892 | 96.0902 | 96.566 | 93.9535 | 96.8628 | 96.6484 | 97.0781 | 96.979 | 96.4291 | 96.8058 | 93.4666 | 95.9837 | 96.7742 | 96.7578 | 96.6548 | 96.416 | 96.5177 | 2025-02-03
Power Center | D1500-M4 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 1.438 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.439 | 240 | 96.5 | CSA Group | [7/20/2023] | CSA Group | [05/13/2022] | [V01.01.00] | 2022-09-12 | [05/13/2022] | 2022-09-12 | CSA Group | 2022-05-05 | 2022-09-01 |  | N | Y | 0.11 |  |  | 36 | 42 | 48 | 0.1439 | 0.2878 | 0.4317 | 0.7195 | 1.0793 | 1.439 | 95.475 | 96.1751 | 96.2272 | 96.4894 | 96.5302 | 96.1507 | 96.4064 | 95.7865 | 96.0559 | 96.3858 | 96.332 | 96.6319 | 96.4894 | 96.4696 | 95.703 | 95.9005 | 96.3909 | 96.1942 | 96.5937 | 96.5755 | 96.4142 | 2022-09-12 | 2023-10-23
Power Center | Essential Hybrid 5 {120V} | Y | Y | N | N | N | N | N | N | 5 kW, 120 Vac Grid Support Utility Interactive PV and Battery Inverter | 4.7871 | 120 | 96.5 | TUV Rheinland | [8/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 11.7 |  |  | 200 | 312.5 | 425 | 0.47871 | 0.95742 | 1.4361 | 2.3935 | 3.5903 | 4.7871 | 94.422 | 96.792 | 97.112 | 96.518 | 95.908 | 95.576 | 96.1487 | 94.832 | 97.148 | 97.55 | 96.838 | 96.532 | 95.88 | 96.6486 | 94.292 | 96.732 | 97.052 | 96.49 | 95.946 | 95.406 | 96.1391 | 2024-05-13
Power Center | Essential Hybrid 5 {240V} | Y | Y | N | N | N | N | N | N | 8 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 7.9703 | 240 | 96.5 | TUV Rheinland | [8/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 19.3 |  |  | 200 | 312.5 | 425 | 0.79703 | 1.5941 | 2.3911 | 3.9851 | 5.9777 | 7.9703 | 94.432 | 96.79 | 97.304 | 96.606 | 96.184 | 95.546 | 96.3353 | 94.82 | 97.058 | 97.568 | 96.802 | 96.458 | 95.99 | 96.6045 | 94.374 | 96.7 | 97.082 | 96.412 | 95.828 | 95.31 | 96.0607 | 2024-05-13
Power Center | Flex 10 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, Grid Support Utility Interactive Inverter | 8.671 | 208 | 96.5 | Intertek | [5/28/2026] | Intertek | [5/28/2026] | [V0.1] | 46245 | [5/28/2026] | 46245 | Intertek | 46119 |  |  | N | N | 16.22 |  |  | 220 | 360 | 500 | 0.8671 | 1.7342 | 2.6013 | 4.3355 | 6.5032 | 8.671 | 94.6399 | 95.5162 | 96.3259 | 95.9573 | 95.5771 | 95.3524 | 95.695 | 95.5409 | 96.299 | 97.0577 | 96.8606 | 96.5499 | 96.1987 | 96.6056 | 96.1644 | 97.0926 | 97.8805 | 97.4985 | 97.5164 | 96.9415 | 97.4523 | 2026-08-11 |  | Y | N | N | N | N | N | Y | N | N
Power Center | Flex 10 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, Grid Support Utility Interactive Inverter | 9.9914 | 240 | 97 | Intertek | [5/28/2026] | Intertek | [5/28/2026] | [V0.1] | 46245 | [5/28/2026] | 46245 | Intertek | 46119 |  |  | N | N | 16.53 |  |  | 220 | 360 | 500 | 0.99914 | 1.9983 | 2.9974 | 4.9957 | 7.4936 | 9.9914 | 95.4308 | 96.2429 | 97.1609 | 96.681 | 96.131 | 95.6355 | 96.3229 | 96.0699 | 96.9269 | 97.9414 | 97.4965 | 97.0743 | 96.7243 | 97.202 | 96.7257 | 97.6788 | 98.5843 | 98.2362 | 97.8247 | 97.2475 | 97.9222 | 2026-08-11 |  | Y | N | N | N | N | N | Y | N | N
Power Center | Flex 12 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 12 kW, Grid Support Utility Interactive Inverter | 11.517 | 208 | 96.5 | Intertek | [5/28/2026] | Intertek | [5/28/2026] | [V0.1] | 46245 | [5/28/2026] | 46245 | Intertek | 46119 |  |  | N | N | 16.25 |  |  | 220 | 360 | 500 | 1.1517 | 2.3034 | 3.4551 | 5.7585 | 8.6378 | 11.517 | 94.5637 | 95.0747 | 96.2219 | 95.9651 | 95.651 | 95.6393 | 95.7126 | 95.8105 | 96.2916 | 97.011 | 96.9717 | 96.4131 | 96.0207 | 96.5523 | 96.2546 | 96.9778 | 98.424 | 97.2969 | 97.1415 | 96.943 | 97.2745 | 2026-08-11 |  | Y | N | N | N | N | N | Y | N | N
Power Center | Flex 12 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 12 kW, Grid Support Utility Interactive Inverter | 11.969 | 240 | 97 | Intertek | [5/28/2026] | Intertek | [5/28/2026] | [V0.1] | 46245 | [5/28/2026] | 46245 | Intertek | 46119 |  |  | N | N | 16.48 |  |  | 220 | 360 | 500 | 1.1969 | 2.3938 | 3.5907 | 5.9845 | 8.9767 | 11.969 | 95.5377 | 96.4105 | 97.2613 | 96.6277 | 96.3047 | 95.9192 | 96.4427 | 96.1402 | 97.3142 | 97.9948 | 97.5526 | 96.9976 | 96.7655 | 97.2038 | 96.9953 | 97.7455 | 98.6046 | 98.4266 | 97.9344 | 97.2686 | 98.0379 | 2026-08-11 |  | Y | N | N | N | N | N | Y | N | N
Power Center | Max Hybrid 15 {208V} | Y | Y | N | N | N | N | Y* | N | 15 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 13.01 | 208 | 96.5 | SGS | [7/19/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-01-12 | No Information Submitted |  | N | N | 21.2 |  |  | 200 | 320 | 425 | 1.3014 | 2.6029 | 3.9043 | 6.5072 | 9.7608 | 13.0145 | 93.374 | 95.8088 | 97.681 | 96.9864 | 96.551 | 96.3162 | 96.6021 | 93.6666 | 95.9928 | 97.712 | 97.172 | 96.6578 | 96.4328 | 96.7281 | 93.469 | 95.9614 | 97.63 | 97.0532 | 96.5632 | 96.3156 | 96.6279 | 2023-11-13 | 2024-11-01
Power Center | Max Hybrid 15 {240V} | Y | Y | N | N | N | N | Y* | N | 15 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 15.04 | 240 | 96.5 | SGS | [7/19/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-01-12 | No Information Submitted |  | N | N | 21.2 |  |  | 200 | 320 | 425 | 1.5044 | 3.0087 | 4.5131 | 7.5219 | 11.2828 | 15.0437 | 93.582 | 95.8704 | 97.6968 | 97.062 | 96.661 | 96.4142 | 96.6945 | 93.693 | 96.1402 | 97.7394 | 97.2496 | 96.7728 | 96.4702 | 96.819 | 93.6154 | 95.9584 | 97.6952 | 97.089 | 96.7006 | 96.4 | 96.726 | 2023-11-13 | 2024-11-01
Power Center | Max Hybrid 30 (208V) {120V} | Y | Y | N | N | N | N | Y* | N | 30 kW, 120 Vac Grid Support Interactive Hybrid Inverter with PCS functionality. | 30.025 | 120 | 96.5 | TUV Rheinland of North America | [3/5/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-09-16 | No Information Submitted |  | N | N | 31.9 |  |  | 270 | 385 | 500 | 3.0025 | 6.005 | 9.0076 | 15.0126 | 22.5189 | 30.0252 | 94.448 | 96.852 | 97.246 | 96.534 | 96.014 | 95.534 | 96.2263 | 94.814 | 97.092 | 97.534 | 96.824 | 96.44 | 95.92 | 96.5935 | 94.344 | 96.68 | 97.14 | 96.444 | 95.836 | 95.342 | 96.078 | 2024-06-11 | 2025-03-21
Power Center | Max Hybrid 60 {277V} | Y | Y | N | N | N | N | Y* | N | 60 kW, 277 Vac Grid Support Interactive Hybrid Inverter with PCS functionality. | 60.05 | 277 | 97.5 | TUV Rheinland | [3/5/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-09-16 | No Information Submitted |  | N | N | 5.29 |  |  | 540 | 695 | 850 | 6.005 | 12.01 | 18.015 | 30.025 | 45.0375 | 60.05 | 94.422 | 98.066 | 98.602 | 97.896 | 97.376 | 96.784 | 97.5191 | 94.748 | 98.504 | 98.834 | 98.228 | 97.77 | 97.26 | 97.8842 | 94.32 | 98.036 | 98.376 | 97.826 | 97.196 | 96.688 | 97.3715 | 2024-06-11 | 2025-03-21
Power Electronics | FS1050CU15 {565V} | N | N | Y | y | N | N | N | N | 1050 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box | 1163.5 | 565 | 97 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 15 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 338.51 |  |  | 800 | 900 | 1200 | 116 | 233 | 349 | 582 | 873 | 1164 | 93 | 96.2 | 96.7 | 97.5 | 97.6 | 97.5 | 97.2 | 93 | 96.1 | 96.7 | 97.4 | 97.5 | 97.3 | 97.1 | 93.2 | 96.2 | 96.6 | 97.4 | 97.6 | 97.3 | 97.2 | 2018-05-15 | 2018-10-15
Power Electronics | FS1100CU15O3 {600V} | N | N | Y | y | N | N | N | N | 1100 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 1176.44 | 600 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 11 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 358.91 |  |  | 849 | 940 | 1200 | 118 | 235 | 353 | 588 | 882 | 1176 | 95.9 | 97.5 | 97.7 | 98 | 98 | 98 | 97.9 | 95.8 | 97.4 | 97.7 | 98 | 97.9 | 97.9 | 97.8 | 95.8 | 97.4 | 97.7 | 98 | 97.9 | 97.9 | 97.8 | 2018-05-15 | 2018-10-15
Power Electronics | FS1100CU15 {600V} | N | N | Y | y | N | N | N | N | 1100 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box | 1209.25 | 600 | 97 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 11 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 347.22 |  |  | 849 | 940 | 1200 | 121 | 242 | 363 | 605 | 907 | 1209 | 93.1 | 96.2 | 96.8 | 97.5 | 97.8 | 97.7 | 97.3 | 93.1 | 96.1 | 96.8 | 97.5 | 97.6 | 97.6 | 97.2 | 93.2 | 96.2 | 96.7 | 97.5 | 97.7 | 97.5 | 97.2 | 2018-05-15 | 2018-10-15
Power Electronics | FS1200CU15 {645V} | N | N | Y | y | N | N | N | N | 1200 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 1300.9 | 645 | 97.5 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 12 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 348.45 |  |  | 913 | 980 | 1200 | 130 | 260 | 390 | 650 | 976 | 1301 | 93.5 | 96.5 | 97 | 97.7 | 97.8 | 97.7 | 97.5 | 93.5 | 96.5 | 96.9 | 97.6 | 97.7 | 97.6 | 97.4 | 93.5 | 96.5 | 96.9 | 97.6 | 97.8 | 97.6 | 97.4 | 2018-05-15 | 2018-10-15
Power Electronics | FS1275CU15 {690V} | N | N | Y | y | N | N | N | N | 1275 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 1389.08 | 690 | 97 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 1275 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 353.05 |  |  | 976 | 1030 | 1200 | 139 | 278 | 417 | 695 | 1042 | 1389 | 91.8 | 95.5 | 96.2 | 97.7 | 97.9 | 97.8 | 97.3 | 91.7 | 95.5 | 96.3 | 97.6 | 97.8 | 97.6 | 97.2 | 91.9 | 95.6 | 96.3 | 97.6 | 97.8 | 97.6 | 97.2 | 2018-05-15 | 2018-10-15
Power Electronics | FS1400CU15 {565V} | N | N | Y | y | N | N | N | N | 1400 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box | 1517.09 | 565 | 97.5 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 14 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 359.56 |  |  | 800 | 900 | 1200 | 152 | 303 | 455 | 759 | 1138 | 1517 | 94.3 | 96.5 | 97.3 | 97.7 | 97.8 | 97.6 | 97.5 | 94.3 | 96.4 | 97.2 | 97.7 | 97.7 | 97.5 | 97.4 | 94.4 | 96.5 | 97.2 | 97.6 | 97.7 | 97.5 | 97.5 | 2018-05-15 | 2018-10-15
Power Electronics | FS1500CU15O3 {600V} | N | N | Y | Y | N | N | N | N | 1500 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 1594.72 | 600 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 15 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 379.71 |  |  | 849 | 940 | 1200 | 159 | 319 | 478 | 797 | 1196 | 1595 | 96.9 | 97.6 | 97.9 | 98.1 | 98 | 97.9 | 97.9 | 96.6 | 97.5 | 97.8 | 98 | 98 | 97.8 | 97.9 | 96.7 | 97.5 | 97.8 | 98 | 98 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS1475CU15 {600V} | N | N | Y | Y | N | N | N | N | 1475 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box | 1610.37 | 600 | 97.5 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 1475 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 368.71 |  |  | 849 | 940 | 1200 | 161 | 322 | 483 | 805 | 1208 | 1610 | 94.5 | 96.7 | 97.5 | 97.8 | 97.9 | 97.6 | 97.6 | 94.5 | 96.6 | 97.4 | 97.8 | 97.8 | 97.6 | 97.5 | 94.6 | 96.6 | 97.4 | 97.7 | 97.8 | 97.5 | 97.5 | 2018-05-15 | 2018-10-15
Power Electronics | FS1600CU15 {645V} | N | N | Y | Y | N | N | N | N | 1600 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 1734.81 | 645 | 97.5 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 16 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 373.96 |  |  | 913 | 980 | 1200 | 173 | 347 | 520 | 867 | 1301 | 1735 | 94.7 | 96.8 | 97.5 | 98 | 98 | 97.8 | 97.7 | 94.7 | 96.8 | 97.5 | 97.9 | 97.9 | 97.7 | 97.6 | 94.7 | 96.8 | 97.5 | 97.8 | 97.9 | 97.7 | 97.6 | 2018-05-15 | 2018-10-15
Power Electronics | FS1700CU15 {690V} | N | N | Y | Y | N | N | N | N | 1700 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 1850.63 | 690 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 17 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 368.51 |  |  | 976 | 1030 | 1200 | 185 | 370 | 555 | 925 | 1388 | 1851 | 95 | 97 | 97.7 | 98.1 | 98.2 | 97.9 | 97.9 | 94.9 | 97 | 97.6 | 98.1 | 98 | 97.9 | 97.8 | 94.9 | 96.9 | 97.6 | 98 | 98.1 | 97.8 | 97.8 | 2018-05-15 | 2018-10-15
Power Electronics | FS1750CU15 {565V} | N | N | Y | Y | N | N | N | N | 1750 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box | 1896.53 | 565 | 97.5 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 175 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 378.47 |  |  | 800 | 900 | 1200 | 190 | 379 | 569 | 948 | 1422 | 1897 | 94.8 | 96.6 | 97.4 | 98 | 97.9 | 97.7 | 97.6 | 94.8 | 96.5 | 97.3 | 97.8 | 97.8 | 97.6 | 97.5 | 94.7 | 96.4 | 97.3 | 97.8 | 97.8 | 97.5 | 97.5 | 2018-05-15 | 2018-10-15
Power Electronics | FS1850CU15O3 {600V} | N | N | Y | Y | N | N | N | N | 1850 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 1974.29 | 600 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 185 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 397.3 |  |  | 849 | 940 | 1200 | 197 | 395 | 592 | 987 | 1481 | 1974 | 96.9 | 97.7 | 97.9 | 98.1 | 98.1 | 97.9 | 98 | 96.7 | 97.5 | 97.8 | 98 | 98 | 97.8 | 97.9 | 96.8 | 97.6 | 97.9 | 98 | 98 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS1850CU15 {600V} | N | N | Y | Y | N | N | N | N | 1850 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box | 2020.96 | 600 | 97.5 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 185 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 388.77 |  |  | 849 | 940 | 1200 | 202 | 404 | 606 | 1010 | 1516 | 2021 | 95.1 | 96.7 | 97.5 | 98 | 98 | 97.8 | 97.8 | 95 | 96.6 | 97.5 | 97.9 | 97.9 | 97.7 | 97.7 | 95 | 96.6 | 97.4 | 97.9 | 97.9 | 97.6 | 97.7 | 2018-05-15 | 2018-10-15
Power Electronics | FS2000K {600V} | N | N | Y | Y | Y | N | N | N | 2100 kW, 600 Vac Grid Support Utility Interactive Inverter | 2103.416 | 600 | 98 | No Information Submitted | No Information Submitted | MET | [05/23/2018] | [1.0.0.] | 2019-04-02 | [05/23/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 21 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. The inverter is central control composed by 4 modules. | N | N | 442.59 |  |  | 849 | 940 | 1200 | 210.3416 | 420.6832 | 631.0248 | 1051.708 | 1577.562 | 2103.416 | 96.0919 | 97.5238 | 97.9704 | 98.3806 | 98.2078 | 97.9134 | 98.082 | 96.1235 | 97.504 | 97.9438 | 98.2085 | 98.1306 | 97.7279 | 97.9928 | 96.1964 | 97.4535 | 97.9859 | 98.3557 | 98.141 | 97.7477 | 98.0356 | 2019-04-02
Power Electronics | FS2000CU15 {645V} | N | N | Y | Y | N | N | N | N | 2000 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 2162.42 | 645 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 2 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 388.97 |  |  | 913 | 980 | 1200 | 216 | 432 | 649 | 1081 | 1622 | 2162 | 95.2 | 96.9 | 97.6 | 98.1 | 98.1 | 97.9 | 97.9 | 95.2 | 96.8 | 97.5 | 98 | 98 | 97.8 | 97.8 | 95.2 | 96.8 | 97.5 | 98 | 98 | 97.8 | 97.7 | 2018-05-15 | 2018-10-15
Power Electronics | FS2000M {34000V} | N | N | Y | Y | Y | N | N | N | 2000 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer | 2178.068 | 34500 | 97 | No Information Submitted | No Information Submitted | MET | [05/23/2018] | [1.0.0.] | 2019-03-15 | [05/23/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%). | N | N | 5970 |  |  | 849 | 940 | 1200 | 217.8068 | 435.6136 | 653.4204 | 1089.034 | 1633.551 | 2178.068 | 93.4983 | 95.9935 | 96.8011 | 97.4581 | 97.6572 | 97.5548 | 97.258 | 93.3492 | 95.8983 | 96.8261 | 97.396 | 97.5629 | 97.4223 | 97.1806 | 93.4114 | 95.9287 | 96.709 | 97.3923 | 97.6181 | 97.4835 | 97.2021 | 2019-03-15
Power Electronics | FS2125K {600V} | N | N | Y | Y | Y | N | N | N | 2200 kW, 600 Vac Grid Support Utility Interactive Inverter | 2201.52 | 600 | 98 | No Information Submitted | No Information Submitted | SGS North America | [03/10/2020] | [1.9.1] | 2020-05-21 | [03/10/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is central control composed by 4 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on 2225 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 302.3 |  |  | 849 | 940 | 1200 | 220.152 | 440.304 | 660.456 | 1100.76 | 1651.14 | 2201.52 | 95.8049 | 97.3563 | 97.9723 | 98.3071 | 98.258 | 98.0579 | 98.0808 | 95.7119 | 97.2529 | 97.8692 | 98.2153 | 98.1268 | 97.9016 | 97.9629 | 95.6723 | 97.2384 | 97.8428 | 98.218 | 98.1248 | 97.8825 | 97.956 | 2020-05-21
Power Electronics | FS2180K {615V} | N | N | Y | Y | Y | N | N | N | 2255 kW, 615 Vac Grid Support Utility Interactive Inverter | 2259.5 | 615 | 98 | No Information Submitted | No Information Submitted | SGS North America | [03/10/2020] | [1.9.1] | 2020-05-21 | [03/10/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is central control composed by 4 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on PROLEC GE PAD-MOUNTED KNAN - 2255KVA - 12.47kV. | N | N | 302.3 |  |  | 870 | 950 | 1200 | 225.95 | 451.9 | 677.85 | 1129.75 | 1694.625 | 2259.5 | 95.8228 | 97.3376 | 97.9902 | 98.3143 | 98.2785 | 98.0989 | 98.0972 | 95.7355 | 97.2693 | 97.8894 | 98.26 | 98.2178 | 97.9983 | 98.0295 | 95.7021 | 97.2507 | 97.8775 | 98.2343 | 98.2056 | 97.9913 | 98.0136 | 2020-05-21
Power Electronics | FS2100CU15 {565V} | N | N | Y | Y | N | N | N | N | 2100 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box | 2275.89 | 565 | 97.5 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 21 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 398.85 |  |  | 800 | 900 | 1200 | 228 | 455 | 683 | 1138 | 1707 | 2276 | 95.4 | 97.2 | 97.6 | 98 | 98 | 97.7 | 97.8 | 95.2 | 97.1 | 97.6 | 97.9 | 97.8 | 97.6 | 97.7 | 95.3 | 97 | 97.5 | 97.9 | 97.8 | 97.6 | 97.7 | 2018-05-15 | 2018-10-15
Power Electronics | FS2125CU15 {690V} | N | N | Y | Y | N | N | N | N | 2125 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 2306.41 | 690 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 2125 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 390.63 |  |  | 976 | 1030 | 1200 | 231 | 461 | 692 | 1153 | 1730 | 2306 | 95.6 | 97.1 | 97.8 | 98.2 | 98.2 | 98 | 98 | 95.6 | 97.1 | 97.7 | 98.1 | 98.1 | 97.9 | 97.9 | 95.5 | 97 | 97.6 | 98.1 | 98.1 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS2225CU15 {600V} | N | N | Y | Y | N | N | N | N | 2225 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box | 2417.08 | 600 | 97.5 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 2225 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 403.32 |  |  | 849 | 940 | 1200 | 242 | 483 | 725 | 1209 | 1813 | 2417 | 95.5 | 97.2 | 97.7 | 98.1 | 98.1 | 97.8 | 97.9 | 95.5 | 97.2 | 97.7 | 98 | 98 | 97.7 | 97.8 | 95.4 | 97.1 | 97.6 | 98 | 98 | 97.7 | 97.8 | 2018-05-15 | 2018-10-15
Power Electronics | FS2250CU15O3 {600V} | N | N | Y | Y | N | N | N | N | 2250 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 2420.37 | 600 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 225 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 416.47 |  |  | 849 | 940 | 1200 | 242 | 484 | 726 | 1210 | 1815 | 2420 | 97.2 | 97.8 | 98 | 98.2 | 98.1 | 97.9 | 98 | 96.9 | 97.8 | 98 | 98 | 98 | 97.7 | 97.9 | 96.9 | 97.7 | 97.9 | 98.1 | 98 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS2150CU15 {645V} | N | N | Y | Y | N | N | N | N | 2150 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 2558.48 | 645 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 215 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 409.99 |  |  | 913 | 980 | 1200 | 256 | 512 | 768 | 1279 | 1919 | 2558 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 97.9 | 97.9 | 95.6 | 97.3 | 97.8 | 98.1 | 98.1 | 97.8 | 97.9 | 95.6 | 97.3 | 97.7 | 98.1 | 98.1 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS2400CU15 {645V} | N | N | Y | Y | N | N | N | N | 2400 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 2583.76 | 645 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 24 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 407.44 |  |  | 913 | 980 | 1200 | 258 | 517 | 775 | 1292 | 1938 | 2584 | 95.8 | 97.4 | 97.9 | 98.1 | 98.1 | 97.9 | 98 | 95.8 | 97.4 | 97.7 | 98.1 | 98.1 | 97.8 | 97.9 | 95.7 | 97.3 | 97.7 | 98.1 | 98 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS2450CU15 {565V} | N | N | Y | Y | N | N | N | N | 2450 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box | 2664.07 | 565 | 97.5 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 245 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 417.35 |  |  | 800 | 900 | 1200 | 266 | 533 | 799 | 1332 | 1998 | 2664 | 95.7 | 97.3 | 97.6 | 98 | 98 | 97.7 | 97.8 | 95.6 | 97.2 | 97.6 | 97.9 | 97.9 | 97.6 | 97.7 | 95.6 | 97.2 | 97.5 | 97.9 | 97.9 | 97.6 | 97.7 | 2018-05-15 | 2018-10-15
Power Electronics | FS2550CU15 {690V} | N | N | Y | Y | N | N | N | N | 2250 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 2759.39 | 690 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 255 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 408.29 |  |  | 976 | 1030 | 1200 | 276 | 552 | 828 | 1380 | 2070 | 2759 | 96 | 97.5 | 97.9 | 98.2 | 98.2 | 97.9 | 98 | 95.9 | 97.4 | 97.8 | 98.2 | 98.1 | 97.8 | 97.9 | 95.9 | 97.4 | 97.8 | 98.1 | 98.1 | 97.9 | 98 | 2018-05-15 | 2018-10-15
Power Electronics | FS2300CU15 {690V} | N | N | Y | Y | N | N | N | N | 2300 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 2759.49 | 690 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 23 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 408.67 |  |  | 976 | 1030 | 1200 | 276 | 552 | 828 | 1380 | 2070 | 2759 | 95.9 | 97.5 | 97.9 | 98.2 | 98.2 | 98 | 98 | 95.8 | 97.4 | 97.8 | 98.1 | 98.2 | 97.9 | 98 | 95.8 | 97.4 | 97.8 | 98.2 | 98.1 | 97.9 | 98 | 2018-05-15 | 2018-10-15
Power Electronics | FS2600CU15O3 {600V} | N | N | Y | Y | N | N | N | N | 2600 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 2770.2 | 600 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 26 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 433.54 |  |  | 849 | 940 | 1200 | 277 | 554 | 831 | 1385 | 2078 | 2770 | 97.2 | 97.9 | 98.1 | 98.2 | 98.1 | 97.9 | 98 | 97.1 | 97.8 | 98 | 98 | 98 | 97.8 | 98 | 97.1 | 97.8 | 98 | 98.1 | 98 | 97.8 | 98 | 2018-05-15 | 2018-10-15
Power Electronics | FS2600CU15 {600V} | N | N | Y | Y | N | N | N | N | 2600 kW, 600 Vac Grid SupportUtility Interactive Inverter with combiner box | 2821.84 | 600 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 26 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 423.67 |  |  | 849 | 940 | 1200 | 282 | 564 | 847 | 1411 | 2116 | 2822 | 95.7 | 97.4 | 97.9 | 98.1 | 98 | 97.8 | 97.9 | 95.7 | 97.3 | 97.8 | 98.1 | 98 | 97.7 | 97.8 | 95.7 | 97.2 | 97.7 | 98 | 98 | 97.7 | 97.8 | 2018-05-15 | 2018-10-15
Power Electronics | FS2840M {34000V} | N | N | Y | Y | Y | N | N | N | 2840 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer | 2844.7 | 34500 | 97.5 | No Information Submitted | No Information Submitted | MET | [05/23/2018] | [1.0.0.] | 2019-03-15 | [05/23/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%). | N | N | 5970 |  |  | 849 | 940 | 1200 | 284.47 | 568.94 | 853.41 | 1422.35 | 2133.525 | 2844.7 | 94.4413 | 96.5602 | 97.2233 | 97.6279 | 97.7507 | 97.6516 | 97.4648 | 94.3535 | 96.4533 | 97.1235 | 97.5301 | 97.6348 | 97.5292 | 97.3559 | 94.3096 | 96.5127 | 97.1355 | 97.5968 | 97.707 | 97.5485 | 97.4118 | 2019-03-15
POWER ELECTRONICS | FS2865K {600V} | N | N | Y | Y | Y | N | N | N | 2865 kW, 600 Vac, Grid Support Utility Interactive Inverter with a 2250 kVA liquid-immersed distribution transformer. | 2858.63 | 600 | 98 | No Information Submitted | No Information Submitted | MET | [1/12/2023] | [2.1.0] | 2023-08-01 | [1/12/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is central control composed by 3 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on 2250 kVA liquid-immersed distribution transformer DOE tables. | N | N | 623.5 |  |  | 849 | 1024 | 1200 | 285.863 | 571.726 | 857.589 | 1429.315 | 2143.9725 | 2858.63 | 95.6911 | 97.2417 | 97.8861 | 98.2673 | 98.1431 | 97.9896 | 97.9875 | 95.1767 | 97.138 | 97.8066 | 98.1625 | 98.2727 | 97.8781 | 97.9933 | 95.2082 | 97.1238 | 97.8162 | 98.2216 | 98.1721 | 97.8889 | 97.9547 | 2023-08-01
Power Electronics | FS3001M {34000V} | N | N | Y | Y | Y | N | N | N | 3000 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer | 3017.848 | 34500 | 97.5 | No Information Submitted | No Information Submitted | MET | [05/23/2018] | [1.0.0.] | 2019-03-15 | [05/23/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%). | N | N | 6084 |  |  | 849 | 940 | 1200 | 301.7848 | 603.5696 | 905.3544 | 1508.924 | 2263.386 | 3017.848 | 94.6253 | 96.6462 | 97.2747 | 97.6765 | 97.7113 | 97.5625 | 97.4675 | 94.5552 | 96.5905 | 97.182 | 97.5764 | 97.6672 | 97.4448 | 97.4005 | 94.5184 | 96.5838 | 97.1884 | 97.6148 | 97.7037 | 97.4863 | 97.4289 | 2019-03-15
Power Electronics | FS2800CU15 {645V} | N | N | Y | Y | N | N | N | N | 2800 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 3024.91 | 645 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 28 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 427.54 |  |  | 913 | 940 | 1200 | 302 | 605 | 907 | 1512 | 2269 | 3025 | 96 | 97.4 | 97.9 | 98.1 | 98.1 | 97.9 | 98 | 95.9 | 97.4 | 97.8 | 98.1 | 98.1 | 97.8 | 97.9 | 95.9 | 97.3 | 97.7 | 98.1 | 98 | 97.8 | 97.9 | 2018-05-15 | 2018-10-15
Power Electronics | FS3000M {34000V} | N | N | Y | Y | Y | N | N | N | 3000 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer | 3109.266 | 34500 | 97.5 | No Information Submitted | No Information Submitted | MET | [05/23/2018] | [1.0.0.] | 2019-03-15 | [05/23/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%). | N | N | 6056 |  |  | 849 | 940 | 1200 | 310.9266 | 621.8532 | 932.7798 | 1554.633 | 2331.9495 | 3109.266 | 94.9749 | 96.8471 | 97.3723 | 97.6775 | 97.6602 | 97.3399 | 97.4652 | 94.9428 | 96.7736 | 97.3237 | 97.6181 | 97.528 | 97.2027 | 97.365 | 94.9123 | 96.8194 | 97.3539 | 97.6385 | 97.5917 | 97.2755 | 97.4114 | 2019-03-15
Power Electronics | FS3000K {600V} | N | N | Y | Y | Y | N | N | N | 3300 kW, 600 Vac, Grid Support Utility Interactive Inverter | 3121.31 | 600 | 98 | No Information Submitted | No Information Submitted | MET | [6/25/2019] | [1.0.0] | 2020-05-21 | [6/25/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is central control composed by 6 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on 2550 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 324.8 |  |  | 849 | 940 | 1200 | 312.131 | 624.262 | 936.393 | 1560.655 | 2340.983 | 3121.31 | 96.5626 | 97.8243 | 98.1437 | 98.3712 | 98.2469 | 97.9269 | 98.1561 | 96.4544 | 97.7066 | 98.0639 | 98.269 | 98.1285 | 97.8352 | 98.0475 | 96.4381 | 97.7135 | 98.047 | 98.2775 | 98.1268 | 97.8519 | 98.0469 | 2020-05-21
Power Electronics | FS3000CU15 {690V} | N | N | Y | Y | N | N | N | N | 3000 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 3201.17 | 690 | 98 | No Information Submitted | No Information Submitted | SGS North America | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 3 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 426.4 |  |  | 976 | 1030 | 1200 | 320 | 640 | 960 | 1601 | 2401 | 3201 | 96.1 | 97.5 | 97.9 | 98.2 | 98.3 | 98.1 | 98.1 | 96 | 97.5 | 97.9 | 98.1 | 98.2 | 98 | 98 | 95.9 | 97.5 | 97.9 | 98.2 | 98.2 | 97.9 | 98 | 2018-05-15 | 2018-10-15
Power Electronics | FS3150K {630V} | N | N | Y | Y | Y | N | N | N | 3465 kW, 630 Vac, Grid Support Utility Interactive Inverter | 3279.87 | 630 | 98 | No Information Submitted | No Information Submitted | MET | [6/25/2019] | [1.0.0] | 2020-05-21 | [6/25/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is central control composed by 6 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on PROLEC GE PAD-MOUNTED KNAN - 3094KVA - 34500V. | N | N | 324.8 |  |  | 891 | 970 | 1200 | 327.987 | 655.974 | 983.961 | 1639.935 | 2459.903 | 3279.87 | 96.7726 | 97.5708 | 97.8887 | 98.1284 | 97.8074 | 97.6727 | 97.8246 | 96.6921 | 97.4868 | 97.8106 | 98.0403 | 97.7237 | 97.5984 | 97.7412 | 96.643 | 97.4589 | 97.7961 | 98.0568 | 97.874 | 97.5903 | 97.8188 | 2020-05-21
Power Electronics | FS3190K {600V} | N | N | Y | Y | Y | N | N | N | 3300 kW, 630 Vac Grid Support Utility Interactive Inverter | 3303.82 | 630 | 98 | No Information Submitted | No Information Submitted | SGS North America | [03/10/2020] | [1.9.1] | 2020-05-21 | [03/10/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is central control composed by 6 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on 3000 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 324.8 |  |  | 849 | 940 | 1200 | 330.382 | 660.764 | 991.146 | 1651.91 | 2477.865 | 3303.82 | 96.4208 | 97.7616 | 98.1336 | 98.3863 | 98.2416 | 97.9793 | 98.1491 | 96.3008 | 97.6527 | 98.0358 | 98.2753 | 98.16 | 97.8879 | 98.056 | 96.335 | 97.6759 | 98.0457 | 98.2887 | 98.1634 | 97.9124 | 98.0655 | 2020-05-21
Power Electronics | FS3150M {34000V} | N | N | Y | Y | Y | N | N | N | 3150 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer | 3307.98 | 34500 | 97.5 | No Information Submitted | No Information Submitted | MET | [05/23/2018] | [1.0.0.] | 2019-03-15 | [05/23/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%). | N | N | 6880 |  |  | 891 | 970 | 1200 | 330.798 | 661.596 | 992.394 | 1653.99 | 2480.985 | 3307.98 | 95.0211 | 96.9027 | 97.4342 | 97.7515 | 97.6422 | 97.3662 | 97.4845 | 94.9579 | 96.7802 | 97.3562 | 97.6708 | 97.5884 | 97.2348 | 97.4145 | 94.9742 | 96.7828 | 97.3475 | 97.6939 | 97.6 | 97.309 | 97.429 | 2019-03-15
Power Electronics | FS3225M {34000V} | N | N | Y | Y | Y | N | N | N | 3225 kW, 34 kV, Grid Support Utility Interactive Inverter with internal transformer | 3367.326 | 34500 | 97.5 | No Information Submitted | No Information Submitted | MET | [05/23/2018] | [1.0.0.] | 2019-03-15 | [05/23/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Inverters are modular and can be composed by 4 or 6 modules. No differences between modules, they use the same components. Each module can have a different internal working voltage (6V, 615V, 63V, 645V, 66V) but the equipment always incorporates internal Medium Voltage transformer (ABB Model: 1LES518-), in order to provide the same maximum output voltage (34.5 kV + or - 1%). | N | N | 7640 |  |  | 913 | 980 | 1200 | 336.7326 | 673.4652 | 1010.1978 | 1683.663 | 2525.4945 | 3367.326 | 95.0183 | 96.8928 | 97.3979 | 97.7634 | 97.7231 | 96.9255 | 97.503 | 94.9704 | 96.8221 | 97.331 | 97.6393 | 97.6318 | 96.8405 | 97.4108 | 94.9604 | 96.7692 | 97.3276 | 97.6807 | 97.6328 | 97.003 | 97.4246 | 2019-03-15
Power Electronics | FS3270K {615V} | N | N | Y | Y | Y | N | N | N | 3380 kW, 615 Vac, Grid Support Utility Interactive Battery Inverter with Medium Voltage Transformer | 3376.294 | 615 | 98 | No Information Submitted | No Information Submitted | SGS | [3/10/2020] | [1.9.1] | 2023-04-03 | [3/10/2020] | 2023-04-03 | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is central control composed by 6 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on 3400 kVA Medium Voltage transformers table in DOE 2016. | N | N | 332.9 |  |  | 870 | 950 | 1200 | 337.6294 | 675.2588 | 1012.8882 | 1688.147 | 2532.2205 | 3376.294 | 96.2958 | 97.5916 | 97.9955 | 98.2161 | 98.0434 | 97.6501 | 97.9618 | 96.2093 | 97.5271 | 97.9064 | 98.1644 | 97.9737 | 97.5931 | 97.8937 | 96.1876 | 97.5029 | 97.9126 | 98.1376 | 97.9717 | 97.5822 | 97.8852 | 2023-04-03
POWER ELECTRONICS | FS3820K {600V} | N | N | Y | Y | Y | N | N | N | 3820 kW, 600 Vac, Grid Support Utility Interactive Inverter with Medium Voltage Transformer | 3825.8 | 600 | 97.5 | No Information Submitted | No Information Submitted | MET | [1/5/2024] | [2.1.0] | 2024-12-23 | [1/5/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 623.5 |  |  | 851 | 1026 | 1200 | 382.58 | 765.16 | 1147.74 | 1912.9 | 2869.35 | 3825.8 | 95.26 | 97.13 | 97.68 | 97.74 | 98.04 | 97.79 | 97.77 | 95.04 | 96.99 | 97.59 | 97.89 | 98.04 | 97.88 | 97.77 | 94.62 | 96.8 | 97.42 | 97.72 | 98.08 | 97.86 | 97.71 | 2024-12-23
Power Electronics | FS4010K {630V} | N | N | Y | Y | Y | N | N | N | 4010 kW, 630 Vac Grid Support Utility Interactive Inverter with Medium Voltage Transformer | 4058.537 | 630 | 98 | No Information Submitted | No Information Submitted | MET | [1/5/2024] | [2.1.0] | 2022-12-22 | [1/5/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 623.5 |  |  | 891 | 1046 | 1200 | 405.854 | 811.707 | 1217.561 | 2029.269 | 3043.903 | 4058.537 | 95.32 | 97.2 | 97.71 | 98.02 | 98.07 | 97.8 | 97.85 | 94.84 | 96.85 | 97.32 | 97.96 | 98.09 | 97.82 | 97.77 | 94.52 | 96.62 | 97.27 | 97.93 | 97.95 | 97.81 | 97.65 | 2025-02-21
Power Electronics | FS4200M {34500V} | N | N | Y | Y | Y | N | N | N | 4200 kW, 34,500 Vac, Grid Support Utility Interactive Inverter with internal transformer | 4198.715 | 34500 | 97.5 | No Information Submitted | No Information Submitted | MET | [1/12/2023] | [2.1.0] | 2023-10-11 | [1/12/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is a central control composed by 4 modules with internal transformer. | N | N | 7033 |  |  | 934 | 1067 | 1200 | 419.872 | 839.743 | 1259.615 | 2099.358 | 3149.036 | 4198.715 | 93.68 | 96.69 | 97.54 | 98.12 | 98.23 | 97.98 | 97.85 | 93.43 | 96.63 | 97.42 | 97.92 | 98.03 | 97.93 | 97.67 | 93.32 | 96.39 | 97.25 | 97.89 | 97.97 | 97.85 | 97.6 | 2023-10-11
Princeton Power Systems, Inc. | GTIB-480-30-WZZZZZZ-G1.3 {480V} | Y | N | Y | Y | Y | N | N | N | 30 kVA, 480 Vac, 830Vdc, Non-isolated, Bi-directional, Grid Support Utility Interactive PV or Battery Inverter; where Z can be -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or blank. Cannot accept PV and Battery DC input simultaneously. | 29.444 | 480 | 93.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/09/2019] | [V2.4.2] | 2019-06-17 | [05/09/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 35.14 |  |  | 540 | 750 | 830 | 2.9444 | 5.8889 | 8.8333 | 14.7222 | 22.0832 | 29.4443 | 86.7633 | 92.621 | 93.1032 | 93.8163 | 93.2421 | 92.0854 | 92.998 | 87.6485 | 93.2657 | 93.53 | 94.1163 | 93.4041 | 92.9205 | 93.3074 | 88.6063 | 92.4924 | 94.6691 | 94.5469 | 93.6549 | 93.0472 | 93.6735 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-30-ZZZZZZ-G1.3 {480V} | Y | N | Y | Y | Y | N | N | N | 30 kVA, 480 Vac, 830Vdc, Transformerless, Non-isolated, Bi-directional, Grid Support Utility Interactive PV or Battery Inverter; where Z can be -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or blank (Z≠-W). Cannot accept PV and Battery DC input simultaneously. | 29.956 | 480 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/09/2019] | [V2.4.2] | 2019-06-17 | [05/09/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 46.3 |  |  | 540 | 750 | 830 | 2.9956 | 5.9911 | 8.9867 | 14.9778 | 22.4667 | 29.9557 | 92.6541 | 95.1194 | 96.0767 | 96.8464 | 96.977 | 96.8538 | 96.5696 | 93.7759 | 95.2415 | 96.5013 | 97.1768 | 97.3758 | 97.3985 | 96.9795 | 92.7942 | 94.8855 | 96.3887 | 97.0579 | 97.1908 | 97.4251 | 96.7872 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-125XXXXXX-G1.5 {480V} | Y | N | Y | Y | Y | N | N | N | 125 kVA, 480 Vac, 830Vdc, Transformerless, Non-isolated, Grid Support Utility Interactive PV or Battery Inverter; where X can be -B, -D, -DH, -DA, -DD, -GN, -M, -OV, -V, or blank. Cannot accept PV and Battery DC input simultaneously. | 124.964 | 480 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/07/2019] | [V2.72] | 2019-06-17 | [05/07/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 68 |  |  | 350 | 710 | 830 | 12.4964 | 24.9928 | 37.4892 | 62.482 | 93.723 | 124.964 | 87.1196 | 92.9413 | 94.9723 | 95.2179 | 95.6593 | 95.2115 | 94.9843 | 91.9189 | 95.3761 | 95.8979 | 96.6258 | 96.8865 | 96.649 | 96.427 | 91.5596 | 95.713 | 96.4245 | 96.9684 | 96.936 | 96.8929 | 96.6031 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-125XXXXXX-W-G1.5 {480V} | Y | N | Y | Y | Y | N | N | N | 125 kVA, 480 Vac, 830Vdc, Non-isolated, Grid Support Utility Interactive PV or Battery Inverter; where X can be -B, -D, -DH, -DA, -DD, -GN, -M, -OV, -V, or blank. Cannot accept PV and Battery DC input simultaneously. | 124.964 | 480 | 94.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/07/2019] | [V2.7.2] | 2019-06-17 | [05/07/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 125 kVA Jefferson Electric 423-D7-13 distribution transformer. | N | N | 68 |  |  | 350 | 710 | 830 | 12.4964 | 24.9928 | 37.4892 | 62.482 | 93.723 | 124.964 | 84.9387 | 91.6494 | 93.8422 | 94.0171 | 94.1574 | 93.2247 | 93.5493 | 89.6179 | 94.0504 | 94.7567 | 95.4072 | 95.3654 | 94.6322 | 94.9688 | 89.2675 | 94.3826 | 95.2771 | 95.7455 | 95.4141 | 94.8711 | 95.1427 | 2019-06-17
Qcells North America | Q.PEAK DUO BLK-G10+/AC 360 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 360 W, 240 Vac, Grid Support Utility Interactive monocrystalline ACPV, black backsheet. DC module: Q.PEAK DUO BLK-G10+ 360. Microinverter: IQ7PLUS-72-ACM-US {240V} | 0.29 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07] | 2022-04-11 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021] | 2022-04-11 | UL | 2020-03-18 | 2022-04-11 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2022-04-11 | 2024-04-02
Qcells North America | Q.PEAK DUO BLK-G10+/AC 365 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 365 W, 240 Vac, Grid Support Utility Interactive monocrystalline ACPV, black backsheet. DC module: Q.PEAK DUO BLK-G10+ 365. Microinverter: IQ7PLUS-72-ACM-US {240V} | 0.29 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07] | 2022-04-11 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021] | 2022-04-11 | UL | 2020-03-18 | 2022-04-11 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2022-04-11 | 2024-04-02
Qcells North America | Q.PEAK DUO BLK-G10+/AC 370 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 370 W, 240 Vac, Grid Support Utility Interactive monocrystalline ACPV, black backsheet. DC module: Q.PEAK DUO BLK-G10+ 370. Microinverter: IQ7PLUS-72-ACM-US {240V} | 0.29 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021] | [V02.10.00];[V02.12.00];[V02.14.02];[V04.18.02];[V04.20.03];[V04.26.09];[V04.27.04];[V04.28.07] | 2022-04-11 | [10/30/2017];[05/25/2018];[06/26/2018];[02/12/2020];[07/15/2020];[10/09/2020];[11/06/2020];[07/12/2021] | 2022-04-11 | UL | 2020-03-18 | 2022-04-11 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2022-04-11 | 2024-04-02
Qcells North America | Q.PEAK DUO BLK-G6+/AC 340 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 340 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Q.PEAK DUO BLK-G6+ 340. Microinverter: IQ7PLUS-72-x-ACM-US-y {240V} | 0.29 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/16/2020] | [V04.18.02] | 2020-07-13 | [06/16/2020] | 2020-07-13 | UL | 2020-03-18 | 2020-07-13 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2020-07-13 | 2024-04-02
Qcells North America | Q.PEAK DUO BLK-G6+/AC 345 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 345 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Q.PEAK DUO BLK-G6+ 345. Microinverter: IQ7PLUS-72-x-ACM-US-y {240V} | 0.29 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/16/2020] | [V04.18.02] | 2020-07-13 | [06/16/2020] | 2020-07-13 | UL | 2020-03-18 | 2020-07-13 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2020-07-13 | 2024-04-02
Qcells North America | Q.MI.380C-G2 {208V} | N | Y | Y | Y | Y | Y | Y* |  | 330 W, 208 Vac Grid Support Utility Interactive Standalone Microinverter | 0.3302 | 208 | 97 | UL | [4/15/2026] | UL | [4/15/2026] | [MI20US0202] | 2026-06-22 | [4/15/2026] | 2026-06-22 | UL | 2026-05-06 |  |  | Y | Y | 0.015 |  |  | 29.5 | 32.5 | 41 | 0.03302 | 0.06604 | 0.09906 | 0.1651 | 0.24765 | 0.3302 | 94.806 | 96.6344 | 96.9714 | 97.3671 | 97.244 | 96.5813 | 97.076 | 94.7821 | 96.5857 | 96.9247 | 97.2871 | 97.2163 | 96.7476 | 97.0438 | 94.3691 | 96.3939 | 96.7244 | 97.025 | 97.0597 | 96.7743 | 96.857 | 2026-06-22 |  | N | N | Y | N | N | N | N | N | N
Qcells North America | Q.MICRO.380C-G2 {208V} | N | Y | Y | Y | Y | Y | Y* |  | 330 W, 208 Vac Grid Support Utility Interactive Standalone Microinverter | 0.3302 | 208 | 97 | UL | [4/15/2026] | UL | [4/15/2026] | [MI20US0202] | 2026-06-22 | [4/15/2026] | 2026-06-22 | UL | 2026-05-06 |  |  | Y | Y | 0.015 |  |  | 29.5 | 32.5 | 41 | 0.03302 | 0.06604 | 0.09906 | 0.1651 | 0.24765 | 0.3302 | 94.806 | 96.6344 | 96.9714 | 97.3671 | 97.244 | 96.5813 | 97.076 | 94.7821 | 96.5857 | 96.9247 | 97.2871 | 97.2163 | 96.7476 | 97.0438 | 94.3691 | 96.3939 | 96.7244 | 97.025 | 97.0597 | 96.7743 | 96.857 | 2026-06-22 |  | N | N | Y | N | N | N | N | N | N
Qcells North America | Q.MI.349B-G1 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Inverter for ACPV module application and with PCS functionality. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-05-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 | 2024-08-01 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2024-05-01 | 2025-02-21
Qcells North America | Q.PEAK DUO BLK ML-G10.C1+/AC 395 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 395 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.PEAK DUO BLK ML-G10+ 395. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-21 | [2/29/2024] | 2026-01-21 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-21 | 2026-05-01 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Qcells North America | Q.PEAK DUO BLK ML-G10.C1+/AC 400 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 400 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.PEAK DUO BLK ML-G10+ 400. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-21 | [2/29/2024] | 2026-01-21 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-21 | 2026-05-01 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Qcells North America | Q.PEAK DUO BLK ML-G10.C1+/AC 405 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 405 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.PEAK DUO BLK ML-G10+ 405. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-21 | [2/29/2024] | 2026-01-21 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-21 | 2026-05-01 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Qcells North America | Q.PEAK DUO BLK ML-G10.C1+/AC 410 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 410 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.PEAK DUO BLK ML-G10+ 410. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-21 | [2/29/2024] | 2026-01-21 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-21 | 2026-05-01 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Qcells North America | Q.PEAK DUO BLK ML-G10.C1+/AC 415 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 415 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.PEAK DUO BLK ML-G10+ 415. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-21 | [2/29/2024] | 2026-01-21 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-21 | 2026-05-01 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Qcells North America | Q.PEAK DUO BLK ML-G10.D1+/AC 395 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 395 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.PEAK DUO BLK ML-G10+ 395. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-05-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-03 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.PEAK DUO BLK ML-G10.D1+/AC 400 {240V} | N | Y | Y | Y | Y | N | Y* |  | 400 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.PEAK DUO BLK ML-G10+ 400. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-05-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-03 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.PEAK DUO BLK ML-G10.D1+/AC 405 {240V} | N | Y | Y | Y | Y | N | Y* |  | 405 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.PEAK DUO BLK ML-G10+ 405. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-05-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-03 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.PEAK DUO BLK ML-G10.D1+/AC 410 {240V} | N | Y | Y | Y | Y | N | Y* |  | 410 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.PEAK DUO BLK ML-G10+ 410. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-05-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-03 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.PEAK DUO BLK ML-G10.D1+/AC 415 {240V} | N | Y | Y | Y | Y | N | Y* |  | 415 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.PEAK DUO BLK ML-G10+ 415. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-05-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-03 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.TRON BLK M-G2.C1+/AC 415 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 415 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 415. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-02 | [2/29/2024] | 2026-01-02 | UL | 2024-06-27 |  |  | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-02
Qcells North America | Q.TRON BLK M-G2.C1+/AC 420 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 420 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 420. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-02 | [2/29/2024] | 2026-01-02 | UL | 2024-06-27 |  |  | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-02
Qcells North America | Q.TRON BLK M-G2.C1+/AC 425 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 425 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 425. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-02 | [2/29/2024] | 2026-01-02 | UL | 2024-06-27 |  |  | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-02
Qcells North America | Q.TRON BLK M-G2.C1+/AC 430 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 430 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 430. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-02 | [2/29/2024] | 2026-01-02 | UL | 2024-06-27 |  |  | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-02
Qcells North America | Q.TRON BLK M-G2.C1+/AC 435 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 435 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 435. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-02 | [2/29/2024] | 2026-01-02 | UL | 2024-06-27 |  |  | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-02
Qcells North America | Q.TRON BLK M-G2.C1+/AC 440 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 440 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 440. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-02 | [2/29/2024] | 2026-01-02 | UL | 2024-06-27 |  |  | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-02
Qcells North America | Q.TRON BLK M-G2.C1+/AC 445 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 445 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 445. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2026-01-02 | [2/29/2024] | 2026-01-02 | UL | 2024-06-27 |  |  | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-01-02
Qcells North America | Q.TRON BLK M-G2.D1+/AC 415 | N | Y | Y | Y | Y | N | Y* |  | 415 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 415. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 45413 | [2/29/2024] | 45505 | UL | 45470 | This component is specific to ACPV modules and is not available as an individual unit. | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-11 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.TRON BLK M-G2.D1+/AC 420 | N | Y | Y | Y | Y | N | Y* |  | 420 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 420. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 45413 | [2/29/2024] | 45505 | UL | 45470 | This component is specific to ACPV modules and is not available as an individual unit. | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-11 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.TRON BLK M-G2.D1+/AC 425 | N | Y | Y | Y | Y | N | Y* |  | 425 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 425. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 45413 | [2/29/2024] | 45505 | UL | 45470 | This component is specific to ACPV modules and is not available as an individual unit. | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-11 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.TRON BLK M-G2.D1+/AC 430 | N | Y | Y | Y | Y | N | Y* |  | 430 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 430. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 45413 | [2/29/2024] | 45505 | UL | 45470 | This component is specific to ACPV modules and is not available as an individual unit. | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-11 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.TRON BLK M-G2.D1+/AC 435 | N | Y | Y | Y | Y | N | Y* |  | 435 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 435. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 45413 | [2/29/2024] | 45505 | UL | 45470 | This component is specific to ACPV modules and is not available as an individual unit. | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-11 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.TRON BLK M-G2.D1+/AC 440 | N | Y | Y | Y | Y | N | Y* |  | 440 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 440. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 45413 | [2/29/2024] | 45505 | UL | 45470 | This component is specific to ACPV modules and is not available as an individual unit. | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-11 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.TRON BLK M-G2.D1+/AC 445 | N | Y | Y | Y | Y | N | Y* |  | 445 W, 240 Vac, Grid Support Utility Interactive, Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 445. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 45413 | [2/29/2024] | 45505 | UL | 45470 | This component is specific to ACPV modules and is not available as an individual unit. | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2026-08-11 |  | N | N | N | N | N | Y | N | N | N
Qcells North America | Q.TRON BLK M-G2.F1+/AC 405 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 405 W, 240 Vac, Grid Support Utility Interactive Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 405. Microinverter: Q.MI.349B-G1 | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-12-22 | [2/29/2024] | 2025-12-22 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.F1+/AC 410 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 410 W, 240 Vac, Grid Support Utility Interactive Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 410. Microinverter: Q.MI.349B-G1 | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-12-22 | [2/29/2024] | 2025-12-22 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.F1+/AC 415 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 415 W, 240 Vac, Grid Support Utility Interactive Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 415. Microinverter: Q.MI.349B-G1 | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-12-22 | [2/29/2024] | 2025-12-22 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.F1+/AC 420 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 420 W, 240 Vac, Grid Support Utility Interactive Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 420. Microinverter: Q.MI.349B-G1 | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-12-22 | [2/29/2024] | 2025-12-22 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.F1+/AC 425 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 425 W, 240 Vac, Grid Support Utility Interactive Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 425. Microinverter: Q.MI.349B-G1 | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-12-22 | [2/29/2024] | 2025-12-22 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.F1+/AC 430 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 430 W, 240 Vac, Grid Support Utility Interactive Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 430. Microinverter: Q.MI.349B-G1 | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-12-22 | [2/29/2024] | 2025-12-22 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.F1+/AC 435 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 435 W, 240 Vac, Grid Support Utility Interactive Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 435. Microinverter: Q.MI.349B-G1 | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-12-22 | [2/29/2024] | 2025-12-22 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.F1+/AC 440 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 440 W, 240 Vac, Grid Support Utility Interactive Monocrystalline ACPV, black backsheet. DC Module: Q.TRON BLK M-G2+ 440. Microinverter: Q.MI.349B-G1 | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-12-22 | [2/29/2024] | 2025-12-22 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.H1+/AC 405 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 405 W, 108 half-cut cell monocrystalline, black backsheet, ACPV Module. DC Module: Q.TRON BLK M-G2.H1+ 405. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-04-21 | [2/29/2024] | 2025-04-21 | UL | 2024-06-27 | 2025-04-21 |  | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-04-21
Qcells North America | Q.TRON BLK M-G2.H1+/AC 410 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 410 W, 108 half-cut cell monocrystalline, black backsheet, ACPV Module. DC Module: Q.TRON BLK M-G2.H1+ 410. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-04-21 | [2/29/2024] | 2025-04-21 | UL | 2024-06-27 | 2025-04-21 |  | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-04-21
Qcells North America | Q.TRON BLK M-G2.H1+/AC 415 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 415 W, 108 half-cut cell monocrystalline, black backsheet, ACPV Module. DC Module: Q.TRON BLK M-G2.H1+ 415. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-04-21 | [2/29/2024] | 2025-04-21 | UL | 2024-06-27 | 2025-04-21 |  | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-04-21 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.H1+/AC 420 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 420 W, 108 half-cut cell monocrystalline, black backsheet, ACPV Module. DC Module: Q.TRON BLK M-G2.H1+ 420. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-04-21 | [2/29/2024] | 2025-04-21 | UL | 2024-06-27 | 2025-04-21 |  | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-04-21 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.H1+/AC 425 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 425 W, 108 half-cut cell monocrystalline, black backsheet, ACPV Module. DC Module: Q.TRON BLK M-G2.H1+ 425. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-04-21 | [2/29/2024] | 2025-04-21 | UL | 2024-06-27 | 2025-04-21 |  | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-04-21 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.H1+/AC 430 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 430 W, 108 half-cut cell monocrystalline, black backsheet, ACPV Module. DC Module: Q.TRON BLK M-G2.H1+ 430. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-04-21 | [2/29/2024] | 2025-04-21 | UL | 2024-06-27 | 2025-04-21 |  | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-04-21 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.H1+/AC 435 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 435 W, 108 half-cut cell monocrystalline, black backsheet, ACPV Module. DC Module: Q.TRON BLK M-G2.H1+ 435. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-04-21 | [2/29/2024] | 2025-04-21 | UL | 2024-06-27 | 2025-04-21 |  | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-04-21 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.H1+/AC 440 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 440 W, 108 half-cut cell monocrystalline, black backsheet, ACPV Module. DC Module: Q.TRON BLK M-G2.H1+ 440. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-04-21 | [2/29/2024] | 2025-04-21 | UL | 2024-06-27 | 2025-04-21 |  | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-04-21 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2.H1+/AC 445 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 445 W, 108 half-cut cell monocrystalline ACPV Module. Black Backsheet. DC Module: Q.TRON BLK M-G2+ 445W. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-12-22 | [2/29/2024] | 2025-12-22 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2+/AC 405 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 405 W, 108 half-cut cell monocrystalline ACPV Module. Black Backsheet. DC Module: Q.TRON BLK M-G2+ 405W. Microinverter: Q.MI.349B-G1. ACPV with PCS functionality. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-08-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 | 2024-08-01 | This component is specific to ACPV modules and is not available as an individual unit. | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2024-08-01 | 2025-04-11
Qcells North America | Q.TRON BLK M-G2+/AC 410 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 410 W, 108 half-cut cell monocrystalline ACPV Module. Black Backsheet. DC Module: Q.TRON BLK M-G2+ 410W. Microinverter: Q.MI.349B-G1. ACPV with PCS functionality. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-08-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 | 2024-08-01 | This component is specific to ACPV modules and is not available as an individual unit. | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2024-08-01 | 2025-04-11
Qcells North America | Q.TRON BLK M-G2+/AC 415 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 415 W, 108 half-cut cell monocrystalline ACPV Module. Black Backsheet. DC Module: Q.TRON BLK M-G2+ 415W. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-08-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 | 2024-08-01 | This component is specific to ACPV modules and is not available as an individual unit. | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2024-08-01 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2+/AC 420 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 420 W, 108 half-cut cell monocrystalline ACPV Module. Black Backsheet. DC Module: Q.TRON BLK M-G2+ 420W. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-08-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 | 2024-08-01 | This component is specific to ACPV modules and is not available as an individual unit. | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2024-08-01 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2+/AC 425 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 425 W, 108 half-cut cell monocrystalline ACPV Module. Black Backsheet. DC Module: Q.TRON BLK M-G2+ 425W. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-08-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 | 2024-08-01 | This component is specific to ACPV modules and is not available as an individual unit. | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2024-08-01 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2+/AC 430 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 430 W, 108 half-cut cell monocrystalline ACPV Module. Black Backsheet. DC Module: Q.TRON BLK M-G2+ 430W. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-08-01 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 | 2024-08-01 | This component is specific to ACPV modules and is not available as an individual unit. | Y | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2024-08-01 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2+/AC 435 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Inverter for ACPV module applications. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-09-23 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 | 2024-09-23 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2024-09-23 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2+/AC 440 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 349 W, 240 Vac Grid Support Utility Interactive Inverter for ACPV module applications. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2024-09-23 | [2/29/2024] | 2024-08-01 | UL | 2024-06-27 | 2024-09-23 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2024-09-23 | 2025-12-22
Qcells North America | Q.TRON BLK M-G2+/AC 445 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 445 W, 108 half-cut cell monocrystalline ACPV Module. Black Backsheet. DC Module: Q.TRON BLK M-G2+ 445W. Microinverter: Q.MI.349B-G1. | 0.349 | 240 | 97 | UL | [2/29/2024] | UL | [2/29/2024] | [MI10US0701] | 2025-12-22 | [2/29/2024] | 2025-12-22 | UL | 2024-06-27 |  | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.27 |  |  | 31 | 33.5 | 40 | 0.034854 | 0.069708 | 0.10456 | 0.17427 | 0.26141 | 0.34854 | 93.5042 | 96.2106 | 96.7658 | 97.3192 | 97.15 | 96.4898 | 96.9136 | 93.4616 | 96.1882 | 96.7146 | 97.2734 | 97.1624 | 96.6388 | 96.9091 | 92.981 | 96.0486 | 96.6488 | 97.1138 | 97.0792 | 96.7344 | 96.8021 | 2025-12-22
Qcells North America | Q.MI.380C-G2 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 380 W, 240 Vac Grid Support Utility Interactive Standalone Microinverter | 0.3789 | 240 | 97 | UL | [4/15/2026] | UL | [4/15/2026] | [MI20US0202] | 2026-06-22 | [4/15/2026] | 2026-06-22 | UL | 2026-05-06 |  |  | Y | Y | 0.029 |  |  | 30 | 32.5 | 40 | 0.03789 | 0.07578 | 0.11367 | 0.18945 | 0.28417 | 0.3789 | 94.5694 | 96.756 | 97.1813 | 97.6086 | 97.439 | 96.9906 | 97.2723 | 94.671 | 96.7276 | 97.1464 | 97.5516 | 97.4651 | 96.9694 | 97.2716 | 94.592 | 96.5817 | 96.9996 | 97.3329 | 97.3664 | 97.108 | 97.1522 | 2026-06-22 |  | N | N | Y | N | N | N | N | N | N
Qcells North America | Q.MICRO.380C-G2 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 380 W, 240 Vac Grid Support Utility Interactive Standalone Microinverter | 0.3789 | 240 | 97 | UL | [4/15/2026] | UL | [4/15/2026] | [MI20US0202] | 2026-06-22 | [4/15/2026] | 2026-06-22 | UL | 2026-05-06 |  |  | Y | Y | 0.029 |  |  | 30 | 32.5 | 40 | 0.03789 | 0.07578 | 0.11367 | 0.18945 | 0.28417 | 0.3789 | 94.5694 | 96.756 | 97.1813 | 97.6086 | 97.439 | 96.9906 | 97.2723 | 94.671 | 96.7276 | 97.1464 | 97.5516 | 97.4651 | 96.9694 | 97.2716 | 94.592 | 96.5817 | 96.9996 | 97.3329 | 97.3664 | 97.108 | 97.1522 | 2026-06-22 |  | N | N | Y | N | N | N | N | N | N
Qcells North America | Q.MI.384B-P2 {240V} | N | Y | Y | Y | Y | Y | N |  | 384 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.383 | 240 | 97 | UL | [4/15/2026] | UL | [4/15/2026] | [MI20US0202] | 2026-08-03 | [4/15/2026] | 2026-08-03 | No Information Submitted | No Information Submitted |  |  | N | Y | 0.019 |  |  | 30 | 32.5 | 40 | 0.038 | 0.077 | 0.115 | 0.191 | 0.287 | 0.383 | 94.68 | 96.81 | 97.22 | 97.62 | 97.41 | 96.61 | 97.25 | 94.77 | 96.77 | 97.19 | 97.56 | 97.45 | 96.89 | 97.27 | 94.62 | 96.61 | 97.02 | 97.34 | 97.36 | 97.08 | 97.15 | 2026-08-03 |  | N | N | Y | N | N | N | N | N | N
Qcells North America | Q.MICRO.384B-P2 {240V} | N | Y | Y | Y | Y | Y | Y* |  | 384 W, 240 Vac Grid Support Utility Interactive Standalone Microinverter | 0.383 | 240 | 97 | UL | [4/15/2026] | UL | [4/15/2026] | [MI20US0202] | 2026-07-01 | [4/15/2026] | 2026-07-01 | UL | 2026-05-06 |  |  | Y | Y | 0.019 |  |  | 30 | 32.5 | 40 | 0.038 | 0.077 | 0.115 | 0.191 | 0.287 | 0.383 | 94.68 | 96.81 | 97.22 | 97.62 | 97.41 | 96.61 | 97.25 | 94.77 | 96.77 | 97.19 | 97.56 | 97.45 | 96.89 | 97.27 | 94.62 | 96.61 | 97.02 | 97.34 | 97.36 | 97.08 | 97.15 | 2026-07-01 |  | N | N | Y | N | N | N | N | N | N
Qcells North America | Q.VOLT H3.8SX {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid support, utility-interactive hybrid inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 3.805 | 240 | 97 | CSA Group | [4/12/2024] | CSA Group | [9/8/2022];[3/14/2023] | [V1.05, V1.03, V1.10] | 2023-03-13 | [9/8/2022];[3/14/2023] | 2023-03-13 | Intertek | 2023-01-11 | 2023-03-13 |  | N | N | 1.2 |  |  | 175.4 | 337.9 | 499.5 | 0.38047 | 0.76094 | 1.1414 | 1.9023 | 2.8535 | 3.8047 | 92.7832 | 95.3783 | 96.1221 | 96.5347 | 96.5885 | 96.4765 | 96.3029 | 94.0899 | 96.2193 | 96.885 | 97.3248 | 97.4661 | 97.4427 | 97.1681 | 91.4685 | 96.3171 | 97.1281 | 97.4492 | 97.6556 | 97.6619 | 97.2348 | 2023-03-13 | 2024-06-03
Qcells North America | Q.VOLT H5.0SX {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid support, utility-interactive hybrid inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 5.003 | 240 | 97.5 | CSA Group | [4/12/2024] | CSA Group | [9/8/2022];[3/14/2023] | [V1.05, V1.03, V1.10] | 2023-03-13 | [9/8/2022];[3/14/2023] | 2023-03-13 | Intertek | 2023-01-11 | 2023-03-13 |  | N | N | 1.2 |  |  | 229.9 | 363.7 | 499.9 | 0.50027 | 1.0005 | 1.5008 | 2.5013 | 3.752 | 5.0027 | 94.4996 | 96.2452 | 96.7656 | 97.0082 | 96.9837 | 96.852 | 96.8198 | 95.7546 | 97.2612 | 97.4657 | 97.7249 | 97.7239 | 97.6405 | 97.5871 | 94.8122 | 97.071 | 97.3678 | 97.6591 | 97.7118 | 97.6279 | 97.5072 | 2023-03-13 | 2024-06-03
Qcells North America | Q.HOME+ HYB-G1-6.0 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac, single-phase, hybrid PV and battery, grid support utility interactive inverter | 5.57 | 240 | 94 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2021-01-11 | [10/23/2020] | 2021-01-11 | Intertek | 2020-09-11 | 2021-01-11 |  | N | N | 25 |  |  | 240 | 335 | 425 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 93.8526 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 94.3396 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888 | 94.1609 | 2021-01-11 | 2024-10-11
Qcells North America | Q.VOLT H6.0SX {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Grid support, utility-interactive hybrid inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 6.017 | 240 | 97.5 | CSA Group | [4/12/2024] | CSA Group | [9/8/2022];[3/14/2023] | [V1.05, V1.03, V1.10] | 2023-03-13 | [9/8/2022];[3/14/2023] | 2023-03-13 | Intertek | 2023-01-11 | 2023-03-13 |  | N | N | 1.2 |  |  | 277 | 388.3 | 498.7 | 0.60166 | 1.2033 | 1.805 | 3.0083 | 4.5125 | 6.0166 | 95.0593 | 96.7801 | 97.1224 | 97.2712 | 97.1927 | 97.0029 | 97.0853 | 96.3129 | 97.458 | 97.7478 | 97.8566 | 97.7758 | 97.645 | 97.7085 | 94.8068 | 96.9441 | 97.5246 | 97.7657 | 97.6571 | 97.5829 | 97.5106 | 2023-03-13 | 2024-06-03
Qcells North America | Q.HOME+ HYB-G1-7.0 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.0 kW, 240 Vac, single-phase, hybrid PV and battery, grid support utility interactive inverter | 6.666 | 240 | 94.5 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2021-01-11 | [10/23/2020] | 2021-01-11 | Intertek | 2020-09-11 | 2021-01-11 |  | N | N | 25 |  |  | 290 | 360 | 425 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 94.3168 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 94.5405 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836 | 94.4389 | 2021-01-11 | 2024-10-11
Qcells North America | Q.VOLT H7.6SX {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid support, utility-interactive hybrid inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 7.593 | 240 | 97.5 | CSA Group | [4/12/2024] | CSA Group | [9/8/2022];[3/14/2023] | [V1.05, V1.03, V1.10] | 2023-03-13 | [9/8/2022];[3/14/2023] | 2023-03-13 | Intertek | 2023-01-11 | 2023-03-13 |  | N | N | 1.2 |  |  | 234.1 | 365.5 | 498.4 | 0.75932 | 1.5186 | 2.278 | 3.7966 | 5.6949 | 7.5932 | 95.5301 | 96.9355 | 97.2078 | 97.319 | 96.9534 | 96.7056 | 96.9905 | 96.6677 | 97.8357 | 97.9705 | 97.937 | 97.774 | 97.5335 | 97.7786 | 96.0575 | 97.25 | 97.8206 | 97.8742 | 97.7481 | 97.6184 | 97.6843 | 2023-03-13 | 2024-06-03
Qcells North America | Q.HOME+ HYB-G1-7.6 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, single-phase, hybrid PV and battery, grid support utility interactive inverter | 7.642 | 240 | 95.5 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2020-04-13 | [10/23/2020] | 2020-12-11 | Intertek | 2020-09-25 | 2020-10-12 |  | N | N | 44 |  |  | 304 | 402 | 500 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 95.4058 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 95.4118 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449 | 96.1997 | 2020-04-13 | 2024-10-11
Qcells North America | Q.HOME+ HYB-G1-8.6 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, single-phase, hybrid PV and battery, grid support utility interactive inverter | 8.604 | 240 | 96 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2020-04-13 | [10/23/2020] | 2020-12-11 | Intertek | 2020-09-25 | 2020-10-12 |  | N | N | 40 |  |  | 258 | 379 | 500 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 95.2714 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 95.7814 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922 | 96.1906 | 2020-04-13 | 2024-10-11
RCT Power Energy Technology Corporation | Power Storage DC US-8.0 {208V} | Y | Y | Y | Y | Y | Y | N | Y | 7 kW, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.015 | 208 | 97 | CSA Group | [5/15/2024] | CSA Group | [5/15/2024] | [V127(2.27.0104-1.44)] | 2024-08-01 | [5/15/2024] | 2024-08-01 | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | N | 0.3 |  |  | 220 | 360 | 420 | 0.701 | 1.403 | 2.104 | 3.507 | 5.261 | 7.015 | 93.43 | 95.62 | 96.35 | 96.74 | 96.65 | 96.23 | 96.43 | 93.5 | 96.2 | 96.79 | 97.21 | 97.18 | 96.89 | 96.93 | 93.92 | 96.44 | 97.09 | 97.42 | 97.35 | 97.01 | 97.13 | 2024-08-01
RCT Power Energy Technology Corporation | Power Storage DC US-8.0 PRO {208V} | Y | Y | Y | Y | Y | Y | N | Y | 7 kW, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.015 | 208 | 97 | CSA Group | [5/15/2024] | CSA Group | [5/15/2024] | [V127(2.27.0104-1.44)] | 2024-08-01 | [5/15/2024] | 2024-08-01 | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | N | 0.3 |  |  | 220 | 360 | 420 | 0.701 | 1.403 | 2.104 | 3.507 | 5.261 | 7.015 | 93.4321 | 95.6214 | 96.3503 | 96.7391 | 96.6452 | 96.2338 | 96.4293 | 93.4986 | 96.2026 | 96.7947 | 97.209 | 97.1825 | 96.889 | 96.9305 | 93.9173 | 96.445 | 97.0889 | 97.4174 | 97.3475 | 97.0142 | 97.1321 | 2024-08-01
RCT Power Energy Technology Corporation | Power Storage DC US-8.0 {240V} | Y | Y | Y | Y | Y | Y | N | Y | 8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.0322 | 240 | 97 | CSA Group | [5/15/2024] | CSA Group | [5/15/2024] | [V127(2.27.0104-1.44)] | 2024-08-01 | [5/15/2024] | 2024-08-01 | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | N | 0.4025 |  |  | 220 | 360 | 420 | 0.80322 | 1.6064 | 2.4097 | 4.0161 | 6.0241 | 8.0322 | 94.4835 | 96.2889 | 96.8676 | 97.1353 | 96.9831 | 96.5638 | 96.8456 | 94.8035 | 96.8257 | 97.2969 | 97.5898 | 97.5257 | 97.2299 | 97.353 | 94.7472 | 96.886 | 97.455 | 97.7157 | 97.636 | 97.3371 | 97.463 | 2024-08-01
RCT Power Energy Technology Corporation | Power Storage DC US-8.0 PRO {240V} | Y | Y | Y | Y | Y | Y | N | Y | 8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.0322 | 240 | 97 | CSA Group | [5/15/2024] | CSA Group | [5/15/2024] | [V127(2.27.0104-1.44)] | 2024-08-01 | [5/15/2024] | 2024-08-01 | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | N | 0.4025 |  |  | 220 | 360 | 420 | 0.80322 | 1.6064 | 2.4097 | 4.0161 | 6.0241 | 8.0322 | 94.4835 | 96.2889 | 96.8676 | 97.1353 | 96.9831 | 96.5638 | 96.8456 | 94.8035 | 96.8257 | 97.2969 | 97.5898 | 97.5257 | 97.2299 | 97.353 | 94.7472 | 96.886 | 97.455 | 97.7157 | 97.636 | 97.3371 | 97.463 | 2024-08-01
RCT Power Energy Technology Corporation | Power Storage DC US-15.0 {208V} | Y | Y | N | N | N | N | Y* | Y | 15 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 14.947 | 208 | 95.5 | CSA Group | [4/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-04-19 | 2025-07-01 |  | N | N | 16.1 |  |  | 220 | 380 | 440 | 1.495 | 2.989 | 4.484 | 7.473 | 11.21 | 14.947 | 91.8 | 93.83 | 94.74 | 95.19 | 95.05 | 94.69 | 94.83 | 92.49 | 94.62 | 95.44 | 95.86 | 95.79 | 95.51 | 95.56 | 93.2 | 95.35 | 95.98 | 96.24 | 96.09 | 95.75 | 95.94 | 2025-07-01
RCT Power Energy Technology Corporation | Power Storage DC US-15.0 {240V} | Y | Y | N | N | N | N | Y* | Y | 15 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 14.947 | 240 | 95.5 | CSA Group | [4/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-04-19 | 2025-07-01 |  | N | N | 16.1 |  |  | 220 | 380 | 440 | 1.495 | 2.989 | 4.484 | 7.473 | 11.21 | 14.947 | 90.56 | 93.08 | 94.22 | 94.88 | 94.87 | 94.58 | 94.52 | 92.58 | 94.69 | 95.49 | 95.96 | 95.92 | 95.66 | 95.67 | 93.17 | 95.39 | 96.01 | 96.32 | 96.22 | 95.93 | 96.04 | 2025-07-01
RelyEZ Energy Storage Technology Co., Ltd. | Sync Micro 550S {240V} | N | Y | N | N | N | N | N | N | 0.55 kW, 240Vac Grid Support Utility Interactive PV Microinverter | 0.55 | 240 | 94 | Intertek | [2/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.03 |  |  | 36 | 56 | 76 | 0.055 | 0.11 | 0.165 | 0.275 | 0.412 | 0.55 | 81.49 | 89.22 | 91.99 | 94.12 | 95.15 | 95.43 | 93.73 | 83.04 | 88.86 | 92.04 | 94.42 | 95.46 | 95.86 | 94.03 | 80.32 | 89.67 | 92.29 | 94.62 | 95.91 | 96.44 | 94.3 | 2025-05-01
RelyEZ Energy Storage Technology Co., Ltd. | Sync Micro 660S {240V} | N | Y | N | N | N | N | N | N | 0.66 kW, 240Vac Grid Support Utility Interactive PV Microinverter | 0.66 | 240 | 94.5 | Intertek | [2/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.03 |  |  | 43 | 60 | 76 | 0.066 | 0.132 | 0.198 | 0.33 | 0.495 | 0.66 | 83.65 | 90.63 | 92.97 | 94.7 | 95.46 | 95.54 | 94.29 | 85.26 | 90.35 | 93.03 | 95.02 | 95.85 | 96.05 | 94.65 | 83.43 | 90.41 | 93.29 | 95.3 | 96.26 | 96.61 | 94.91 | 2025-05-01
RelyEZ Energy Storage Technology Co., Ltd. | Sync Micro 760S {240V} | N | Y | N | N | N | N | N | N | 0.76 kW, 240Vac Grid Support Utility Interactive PV Microinverter | 0.76 | 240 | 95 | Intertek | [2/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.04 |  |  | 50 | 63 | 76 | 0.076 | 0.152 | 0.228 | 0.38 | 0.57 | 0.76 | 85.3 | 91.55 | 93.68 | 95.19 | 95.62 | 95.77 | 94.69 | 86.86 | 91.35 | 93.71 | 95.3 | 96.04 | 96.2 | 95.01 | 84.96 | 91.47 | 93.97 | 95.7 | 96.46 | 96.66 | 95.3 | 2025-05-01
Rhombus Energy Solutions | RES-BESS60DP-480 {480V} | Y | N | Y | Y | Y | Y | Y* | N | 60 kW, 480 Vac Grid Support Utility Interactive PV and Battery Inverter | 59.789 | 480 | 91.5 | No Information Submitted | No Information Submitted | UL | [09/03/2020] | [00020520] | 2020-12-11 | [09/03/2020] | 2022-02-11 | UL | 2021-12-20 | No Information Submitted |  | Y | N | 92 |  |  | 270 | 441 | 870 | 5.9789 | 11.9578 | 17.9367 | 29.8945 | 44.8418 | 59.789 | 82.328 | 88.79 | 91.344 | 93.2 | 93.729 | 93.632 | 92.6239 | 81.46 | 87.412 | 90.408 | 92.422 | 93.1 | 93 | 91.8796 | 79.44 | 86.038 | 88.894 | 91.278 | 92.026 | 92.06 | 90.6919 | 2020-12-11 | 2022-02-11
RNG International Inc. | RIV4850HI-SPS {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 5 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 5.0897 | 240 | 97 | SGS | [10/9/2023] | SGS | [11/7/2023] | [V1.04.06(DSP),V1.03.06(ARM)] | 2023-12-21 | [11/7/2023] | 2023-12-21 | SGS | 2023-10-20 | 2023-10-30 |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2023-06-01 | 2024-09-03
RNG International Inc. | RIV4860HI-SPS {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 6 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 6.117 | 240 | 97 | SGS | [10/9/2023] | SGS | [11/7/2023] | [V1.04.06(DSP),V1.03.06(ARM)] | 2023-12-21 | [11/7/2023] | 2023-12-21 | SGS | 2023-10-20 | 2023-10-30 |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2023-08-11 | 2024-09-03
RNG International Inc. | RIV4876HI-SPS {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 7 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 7.765 | 240 | 97 | SGS | [10/9/2023] | SGS | [11/7/2023] | [V1.04.06(DSP),V1.03.06(ARM)] | 2023-12-21 | [11/7/2023] | 2023-12-21 | SGS | 2023-10-20 | 2023-10-30 |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2023-08-11 | 2024-09-03
RNG International Inc. | RIV4880HI-SPS {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 8.084 | 240 | 97.5 | SGS | [10/9/2023] | SGS | [11/7/2023] | [V1.04.06(DSP),V1.03.06(ARM)] | 2023-12-21 | [11/7/2023] | 2023-12-21 | SGS | 2023-10-20 | 2023-10-30 |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2023-06-01 | 2024-09-03
RNG International Inc. | RIV4810HI-SPS {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 10.177 | 240 | 97 | SGS | [10/9/2023] | SGS | [11/7/2023] | [V1.04.06(DSP),V1.03.06(ARM)] | 2023-12-21 | [11/7/2023] | 2023-12-21 | SGS | 2023-10-20 | 2023-10-30 |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2023-08-11 | 2024-09-03
Savant Systems Inc. | PS-INV-10KW-100A-XX {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 10 kW, 240 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter, where XX are two characters, and with PCS functionality. | 9.9227 | 240 | 94 | Intertek | [12/11/2024] | Intertek | [5/9/2024] | [ARM/10010, pv/10050, pcs/10025] | 2024-02-12 | [12/1/2023] | 2024-02-12 | SunSpec Alliance | 2024-05-09 | No Information Submitted |  | N | N | 21.92 |  |  | 250 | 360 | 530 | 0.99227 | 1.9845 | 2.9768 | 4.9613 | 7.442 | 9.9227 | 91.2728 | 93.8665 | 92.8466 | 93.9818 | 94.1882 | 93.8918 | 93.8364 | 94.433 | 94.2287 | 93.579 | 93.0905 | 94.0391 | 94.2974 | 93.8229 | 93.3697 | 95.1764 | 93.7928 | 94.5765 | 94.8844 | 95.1581 | 94.6565 | 2024-02-12 | 2024-12-23
Savant Systems Inc. | PS-INV-10KW-60A-XX {240V} | Y | Y | Y | Y | Y | Y | N | N | 10 kW, 240 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter, where XX can be any letters, numbers, or symbols | 9.9227 | 240 | 94 | Intertek | [12/1/2023] | Intertek | [12/1/2023] | [ARM/10010, pv/10050, pcs/10025] | 2024-02-12 | [12/1/2023] | 2024-02-12 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 21.92 |  |  | 250 | 360 | 530 | 0.99227 | 1.9845 | 2.9768 | 4.9613 | 7.442 | 9.9227 | 91.2728 | 93.8665 | 92.8466 | 93.9818 | 94.1882 | 93.8918 | 93.8364 | 94.433 | 94.2287 | 93.579 | 93.0905 | 94.0391 | 94.2974 | 93.8229 | 93.3697 | 95.1764 | 93.7928 | 94.5765 | 94.8844 | 95.1581 | 94.6565 | 2024-02-12
Savant Systems Inc. | PS-INV-12.5KW-100A-XX {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 12.5 kW, 240 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter, where XX are two characters, and with PCS functionality. | 12.4109 | 240 | 95 | Intertek | [12/11/2024] | Intertek | [5/9/2024] | [ARM/10010, pv/10050, pcs/10025] | 2024-02-12 | [12/1/2023] | 2024-02-12 | SunSpec Alliance | 2024-05-09 | No Information Submitted |  | N | N | 19.49 |  |  | 250 | 360 | 530 | 1.2411 | 2.4822 | 3.7233 | 6.2054 | 9.3082 | 12.4109 | 90.7047 | 93.4995 | 95.4688 | 95.3105 | 95.6568 | 96.2106 | 95.2832 | 90.4857 | 93.9644 | 94.7088 | 94.9923 | 95.5978 | 95.9127 | 95.0936 | 90.5641 | 94.3267 | 94.7516 | 94.8157 | 95.6216 | 96.0765 | 95.1036 | 2024-02-12 | 2024-12-23
Savant Systems Inc. | PS-INV-12.5KW-60A-XX {240V} | Y | Y | Y | Y | Y | Y | N | N | 12.5 kW, 240 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter, where XX can be any letters, numbers, or symbols | 12.4109 | 240 | 95 | Intertek | [12/1/2023] | Intertek | [12/1/2023] | [ARM/10010, pv/10050, pcs/10025] | 2024-02-12 | [12/1/2023] | 2024-02-12 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 19.49 |  |  | 250 | 360 | 530 | 1.2411 | 2.4822 | 3.7233 | 6.2054 | 9.3082 | 12.4109 | 90.7047 | 93.4995 | 95.4688 | 95.3105 | 95.6568 | 96.2106 | 95.2832 | 90.4857 | 93.9644 | 94.7088 | 94.9923 | 95.5978 | 95.9127 | 95.0936 | 90.5641 | 94.3267 | 94.7516 | 94.8157 | 95.6216 | 96.0765 | 95.1036 | 2024-02-12
Schneider Electric USA, Inc. | HY8K1NA1 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.68 kW, 240Vac, Transformerless, Bi-directional, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 7.626 | 240 | 97 | CSA Group | [5/14/2025] | CSA Group | [5/14/2025] | [M57] | 2023-10-11 | [10/20/2023] | 2024-03-21 | CSA Group | 2023-11-20 | 2024-01-11 |  | N | N | 13.71 |  |  | 200 | 360 | 480 | 0.763 | 1.525 | 2.288 | 3.813 | 5.72 | 7.626 | 93.03 | 95.42 | 96.11 | 96.65 | 96.61 | 96.38 | 96.34 | 93.66 | 96.41 | 97.06 | 97.43 | 97.4 | 97.14 | 97.15 | 93.55 | 96.53 | 97.2 | 97.61 | 97.55 | 97.81 | 97.32 | 2023-10-11 | 2025-09-22
Schneider Electric USA, Inc. | Conext CL125 {600V} | N | N | Y | Y | N | N | N | N | 125 kW, 600Vac, 3-phase Gird Support Utility Interactive Inverter with the advanced power conversion technology IGBT to convert the DC power normally from the photovoltaic array to stable three-phase AC power and then feed the power to the utility grid. | 125 | 600 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [05/31/2018] | [MDSP_CL125_V11_V01_A_05] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.59 |  |  | 860 | 945 | 1200 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 98.5868 | 98.8265 | 98.8839 | 98.6821 | 98.446 | 98.2553 | 98.5633 | 98.2894 | 98.5842 | 98.5889 | 98.4931 | 98.3594 | 98.1067 | 98.4108 | 98.0841 | 98.4259 | 98.4773 | 98.3848 | 98.097 | 97.626 | 98.1955 | 2018-08-01 | 2024-04-02
Schneider Electric USA, Inc. | CS1666-1-NA {575V} | N | N | Y | Y | N | N | N | N | 1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter with 1666 kVA Maximum Output Continuous Apparent Power | 1666 | 575 | 98 | No Information Submitted | No Information Submitted | SGS North America | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 2. MVA Square D 3PH distribution transformer, liquid-filled type. | N | N | 295 |  |  | 856 | 1024 | 1200 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 97.9 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 97.8 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44 | 97.7 | 2018-08-15 | 2024-04-02
Schneider Electric USA, Inc. | CS1666-2-NA {575V} | N | N | Y | Y | N | N | N | N | 1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter with 1831 kVA Maximum Output Continuous Apparent Power | 1666 | 575 | 98 | No Information Submitted | No Information Submitted | SGS North America | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 2. MVA Square D 3PH distribution transformer, liquid-filled type. | N | N | 295 |  |  | 856 | 1024 | 1200 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 97.9 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 97.8 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44 | 97.7 | 2018-08-15 | 2024-04-02
Schneider Electric USA, Inc. | CS1666-3-NA {575V} | N | N | Y | Y | N | N | N | N | 1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter with 1851 kVA Maximum Output Continuous Apparent Power | 1666 | 575 | 98 | No Information Submitted | No Information Submitted | SGS North America | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 2. MVA Square D 3PH distribution transformer, liquid-filled type. | N | N | 295 |  |  | 856 | 1024 | 1200 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 97.9 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 97.8 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44 | 97.7 | 2018-08-15 | 2024-04-02
Schneider Electric USA, Inc. | CS1800-NA {575V} | N | N | Y | Y | N | N | N | N | 1.8 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter | 1800 | 575 | 98 | No Information Submitted | No Information Submitted | SGS North America | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 2. MVA Square D 3PH distribution transformer, liquid-filled type. | N | N | 295 |  |  | 856 | 1024 | 1200 | 180 | 360 | 540 | 900 | 1350 | 1800 | 96.89 | 97.93 | 98.08 | 98.11 | 97.92 | 97.47 | 97.9 | 96.67 | 97.74 | 98 | 97.99 | 97.8 | 97.45 | 97.8 | 95.89 | 97.43 | 97.67 | 97.87 | 97.7 | 97.34 | 97.6 | 2018-08-15 | 2024-04-02
Schneider Electric USA, Inc. | CS2000-NA {575V} | N | N | Y | Y | N | N | N | N | 2 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter | 2000 | 575 | 97.5 | No Information Submitted | No Information Submitted | SGS North America | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Formerly Schneider Electric Solar Inverters USA, Inc. Conext SmartGen CS2-NA. Weighted Efficiency includes efficiency of 2 KVA Square D 3PH distribution transformer, liquid-filled type (4425642-6-S9-1). | N | N | 295 |  |  | 865 | 1042 | 1195 | 200 | 400 | 600 | 1000 | 1500 | 2000 | 96.76 | 97.71 | 97.98 | 97.96 | 97.66 | 97.21 | 97.71 | 96.32 | 97.58 | 97.87 | 97.83 | 97.56 | 97.15 | 97.58 | 95.92 | 97.38 | 97.69 | 97.72 | 97.5 | 97.06 | 97.48 | 2018-08-15 | 2024-04-02
Schneider Electric USA, Inc. | CS2200-NA {600V} | N | N | Y | Y | N | N | N | N | 2.2 MW, 1500 Vdc, 600 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter | 2200 | 600 | 98 | No Information Submitted | No Information Submitted | SGS North America | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 2.5 MVA Square D 3PH distribution transformer, liquid-filled type. | N | N | 295 |  |  | 905 | 1054 | 1200 | 220 | 440 | 660 | 1100 | 1650 | 2200 | 97.9 | 98.28 | 98.33 | 98.2 | 97.82 | 97.24 | 98 | 97.6 | 98.1 | 98.19 | 98.09 | 97.72 | 97.17 | 97.8 | 97.21 | 97.9 | 98.05 | 97.99 | 97.65 | 97.1 | 97.7 | 2018-08-15 | 2024-04-02
Shanghai Chelion RenewableTechnology Co., Ltd. | iHome-INV7.6K-H1H02 {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac Grid Support Power Conversion System | 7.581 | 240 | 97 | Intertek | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.7581 | 1.5162 | 2.2743 | 3.7905 | 5.6858 | 7.581 | 94.2651 | 95.2225 | 96.163 | 96.9234 | 97.1125 | 97.0636 | 96.748 | 95.2164 | 96.1836 | 96.7935 | 97.3649 | 97.6024 | 97.5348 | 97.2857 | 94.8243 | 95.8334 | 96.5515 | 97.2034 | 97.4231 | 97.3541 | 97.0855 | 2023-03-13
Shanghai Chelion RenewableTechnology Co., Ltd. | iHome-INV9.6K-H1H02 {240V} | Y | Y | N | N | N | N | N | N | 9 kW, 240 Vac Grid Support Power Conversion System | 9.5733 | 240 | 97 | Intertek | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.95733 | 1.9147 | 2.872 | 4.7866 | 7.1799 | 9.5733 | 94.324 | 95.4338 | 96.4736 | 97.0126 | 97.0914 | 97.0133 | 96.8032 | 95.7635 | 96.4127 | 97.0422 | 97.4839 | 97.5735 | 97.4048 | 97.352 | 94.8907 | 95.9847 | 96.8438 | 97.3145 | 97.3946 | 97.234 | 97.133 | 2023-03-13
Shanghai Chelion RenewableTechnology Co., Ltd. | iHome-INV10K-H1H02 {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Power Conversion System | 9.9563 | 240 | 97 | Intertek | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.99563 | 1.9913 | 2.9869 | 4.9782 | 7.4672 | 9.9563 | 94.3337 | 95.6136 | 96.5122 | 97.0308 | 97.0728 | 96.9826 | 96.8097 | 95.7935 | 96.475 | 97.0733 | 97.5049 | 97.543 | 97.3726 | 97.3468 | 95.184 | 96.0843 | 96.883 | 97.3434 | 97.3652 | 97.2134 | 97.1439 | 2023-03-13
Shanghai Chelion RenewableTechnology Co., Ltd. | iHome-INV11.4K-H1H02 {240V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 240 Vac Grid Support Power Conversion System | 11.3705 | 240 | 97 | Intertek | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.1371 | 2.2741 | 3.4112 | 5.6853 | 8.5279 | 11.3705 | 94.3642 | 96.055 | 96.9052 | 97.1019 | 97.0437 | 96.9028 | 96.8756 | 95.8125 | 96.7944 | 97.3353 | 97.6036 | 97.4725 | 97.2634 | 97.3728 | 95.284 | 96.5532 | 97.1622 | 97.414 | 97.3038 | 97.0831 | 97.1806 | 2023-03-13
Shanghai Chelion RenewableTechnology Co., Ltd. | iHome-INV12K-H1H02 {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Power Conversion System | 11.9682 | 240 | 97 | Intertek | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.1968 | 2.3936 | 3.5905 | 5.9841 | 8.9761 | 11.9682 | 94.3841 | 96.0625 | 96.9237 | 97.1216 | 97.0131 | 96.8713 | 96.8654 | 95.8343 | 96.815 | 97.3428 | 97.6232 | 97.4548 | 97.223 | 97.3683 | 95.3154 | 96.5735 | 97.1839 | 97.4422 | 97.282 | 97.04 | 97.1777 | 2023-03-13
SHEN ZHEN MY SMART ENERGY ELECTRIC CO., LTD | MY-HL8K-P2WB {240V} | Y | Y | N | N | N | N | N |  | 8 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.9814 | 240 | 96 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.39 |  |  | 108 | 380 | 480 | 0.79814 | 1.5963 | 2.3944 | 3.9907 | 5.986 | 7.9814 | 90.9385 | 94.1039 | 94.9752 | 95.083 | 95.0387 | 94.6196 | 94.8087 | 92.1593 | 95.6656 | 96.6163 | 96.6433 | 97.0374 | 96.9779 | 96.6374 | 92.4438 | 95.9014 | 96.6012 | 97.0486 | 97.2916 | 97.2167 | 96.8905 | 2026-04-13 |  | Y | Y | Y | Y | Y | Y | Y | Y | N
SHEN ZHEN MY SMART ENERGY ELECTRIC CO., LTD | MY-HL10K-P2WB {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.0109 | 240 | 96 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.12 |  |  | 135 | 380 | 480 | 1.0011 | 2.0022 | 3.0033 | 5.0055 | 7.5082 | 10.0109 | 92.0512 | 94.9782 | 94.9328 | 95.3714 | 95.3991 | 94.9543 | 95.1601 | 93.0994 | 96.2304 | 96.2761 | 96.8719 | 97.0247 | 96.9062 | 96.7001 | 93.6663 | 96.3246 | 96.5808 | 97.0256 | 97.1253 | 97.0288 | 96.8558 | 2026-04-13 |  | Y | Y | Y | Y | Y | Y | Y | Y | N
SHEN ZHEN MY SMART ENERGY ELECTRIC CO., LTD | MY-HL12K-P2WB {240V} | Y | Y | N | N | N | N | N |  | 12 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.0145 | 240 | 96.5 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.39 |  |  | 161 | 380 | 480 | 1.2014 | 2.4029 | 3.6043 | 6.0072 | 9.0109 | 12.0145 | 93.1006 | 95.228 | 95.5523 | 95.8393 | 95.6025 | 95.1408 | 95.5043 | 94.3433 | 96.5994 | 96.675 | 97.0511 | 96.9701 | 96.7737 | 96.8183 | 95.2452 | 96.8669 | 96.9412 | 97.2998 | 97.1893 | 96.9458 | 97.0767 | 2026-04-13 |  | Y | Y | Y | Y | Y | Y | Y | Y | N
SHEN ZHEN MY SMART ENERGY ELECTRIC CO., LTD | MY-HL15K-P2WB {240V} | Y | Y | N | N | N | N | N |  | 15 kW, 240 Vac Grid Support Utility Interactive Inverter | 15.0148 | 240 | 96.5 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.08 |  |  | 202 | 380 | 480 | 1.5015 | 3.003 | 4.5045 | 7.5074 | 11.2611 | 15.0148 | 94.5483 | 95.5289 | 96.0138 | 96.1843 | 95.8054 | 95.25 | 95.8181 | 95.5893 | 96.5176 | 96.9793 | 97.101 | 96.8732 | 96.5137 | 96.8467 | 96.0793 | 96.8399 | 97.2558 | 97.3226 | 96.9795 | 96.6351 | 97.0245 | 2026-04-13 |  | Y | Y | Y | Y | Y | Y | Y | Y | N
Shenzhen Eternalplanet Energy Pingshan Ltd. | HNA7G {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.58 | 240 | 95 | TUV Rheinland | [7/21/2022] | TUV Rheinland | [7/21/2022] | [V2.0] | 2023-09-21 | [7/21/2022] | 2023-09-21 | TUV Rheinland | 2022-09-05 | 2022-08-15 |  | N | N | 23 |  |  | 240 | 350 | 480 | 0.758 | 1.516 | 2.274 | 3.79 | 5.685 | 7.581 | 90 | 91.46 | 93.64 | 94.94 | 94.15 | 93.8 | 93.94 | 89.04 | 91.71 | 94.45 | 95.18 | 94.58 | 94.13 | 94.3 | 92.5 | 95.06 | 95.48 | 95.89 | 95.66 | 95.37 | 95.52 | 2023-09-21
Shenzhen Eternalplanet Energy Pingshan Ltd. | HNA7G_AT {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.58 | 240 | 95 | TUV Rheinland | [7/21/2022] | TUV Rheinland | [7/21/2022] | [V2.0] | 2023-09-21 | [7/21/2022] | 2023-09-21 | TUV Rheinland | 2022-09-05 | 2022-08-15 |  | N | N | 23 |  |  | 240 | 350 | 480 | 0.758 | 1.516 | 2.274 | 3.79 | 5.685 | 7.581 | 90 | 91.46 | 93.64 | 94.94 | 94.15 | 93.8 | 93.94 | 89.04 | 91.71 | 94.45 | 95.18 | 94.58 | 94.13 | 94.3 | 92.5 | 95.06 | 95.48 | 95.89 | 95.66 | 95.37 | 95.52 | 2023-09-21
Shenzhen Eternalplanet Energy Pingshan Ltd. | HNA7G_TT {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.58 | 240 | 95 | TUV Rheinland | [7/21/2022] | TUV Rheinland | [7/21/2022] | [V2.0] | 2023-09-21 | [7/21/2022] | 2023-09-21 | TUV Rheinland | 2022-09-05 | 2022-08-15 |  | N | N | 23 |  |  | 240 | 350 | 480 | 0.758 | 1.516 | 2.274 | 3.79 | 5.685 | 7.581 | 90 | 91.46 | 93.64 | 94.94 | 94.15 | 93.8 | 93.94 | 89.04 | 91.71 | 94.45 | 95.18 | 94.58 | 94.13 | 94.3 | 92.5 | 95.06 | 95.48 | 95.89 | 95.66 | 95.37 | 95.52 | 2023-09-21
Shenzhen Eternalplanet Energy Pingshan Ltd. | HNA7W {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.58 | 240 | 95 | TUV Rheinland | [7/21/2022] | TUV Rheinland | [7/21/2022] | [V2.0] | 2023-09-21 | [7/21/2022] | 2023-09-21 | TUV Rheinland | 2022-09-05 | 2022-08-15 |  | N | N | 23 |  |  | 240 | 350 | 480 | 0.758 | 1.516 | 2.274 | 3.79 | 5.685 | 7.581 | 90 | 91.46 | 93.64 | 94.94 | 94.15 | 93.8 | 93.94 | 89.04 | 91.71 | 94.45 | 95.18 | 94.58 | 94.13 | 94.3 | 92.5 | 95.06 | 95.48 | 95.89 | 95.66 | 95.37 | 95.52 | 2023-09-21
Shenzhen Eternalplanet Energy Pingshan Ltd. | HNA7W_TT {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.58 | 240 | 95 | TUV Rheinland | [7/21/2022] | TUV Rheinland | [7/21/2022] | [V2.0] | 2023-09-21 | [7/21/2022] | 2023-09-21 | TUV Rheinland | 2022-09-05 | 2022-08-15 |  | N | N | 23 |  |  | 240 | 350 | 480 | 0.758 | 1.516 | 2.274 | 3.79 | 5.685 | 7.581 | 90 | 91.46 | 93.64 | 94.94 | 94.15 | 93.8 | 93.94 | 89.04 | 91.71 | 94.45 | 95.18 | 94.58 | 94.13 | 94.3 | 92.5 | 95.06 | 95.48 | 95.89 | 95.66 | 95.37 | 95.52 | 2023-09-21
Shenzhen Growatt New Energy Co., Ltd. | MIN 3000TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 2.626 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 2.626 | 208 | 96.5 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.576 |  |  | 125 | 380 | 480 | 0.26259 | 0.52518 | 0.78777 | 1.3129 | 1.9694 | 2.6259 | 91.2934 | 93.7087 | 95.2183 | 95.8997 | 95.8355 | 95.6645 | 95.4784 | 93.5823 | 95.3477 | 96.9042 | 97.2283 | 97.3991 | 97.0876 | 97.033 | 92.5038 | 95.6858 | 96.4301 | 96.8779 | 96.8499 | 96.9624 | 96.579 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 3000TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 2.93 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 2.934 | 240 | 93.5 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 150 | 380 | 480 | 0.29344 | 0.58687 | 0.88031 | 1.4672 | 2.2008 | 2.9344 | 83.5494 | 88.742 | 91.5187 | 93.466 | 94.3778 | 94.5735 | 93.1381 | 82.9531 | 88.9774 | 91.284 | 94.7821 | 95.7609 | 95.9493 | 94.1761 | 81.2489 | 86.9992 | 91.7283 | 93.6156 | 94.9487 | 95.5889 | 93.3689 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 3000TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 3.0 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 2.999 | 208 | 93.5 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 150 | 380 | 480 | 0.29986 | 0.59972 | 0.89958 | 1.4993 | 2.249 | 2.9986 | 83.2934 | 88.7087 | 91.2183 | 93.3997 | 94.3355 | 94.6645 | 93.0584 | 83.5823 | 88.3477 | 91.9042 | 94.2283 | 95.3991 | 95.8876 | 93.933 | 82.5038 | 87.6858 | 91.4301 | 93.8779 | 94.8499 | 95.7624 | 93.429 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 3000TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.095 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 3.095 | 240 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.593 |  |  | 125 | 380 | 480 | 0.30951 | 0.61902 | 0.92853 | 1.5475 | 2.3213 | 3.0951 | 92.5494 | 94.742 | 95.5187 | 96.466 | 96.3778 | 96.1735 | 96.0481 | 94.9531 | 96.9774 | 97.284 | 97.7821 | 97.7609 | 97.4493 | 97.5411 | 93.2489 | 95.9992 | 96.7283 | 97.2156 | 97.3487 | 97.3889 | 97.0169 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 3800TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.324 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 3.324 | 208 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.576 |  |  | 160 | 380 | 480 | 0.33238 | 0.66477 | 0.99715 | 1.6619 | 2.4929 | 3.3238 | 91.7552 | 94.4271 | 95.625 | 96.3968 | 96.3716 | 96.2365 | 95.9987 | 92.8401 | 95.7332 | 97.3293 | 97.2908 | 97.7747 | 97.4727 | 97.3051 | 92.8717 | 95.7668 | 96.7784 | 97.4953 | 97.5884 | 97.4672 | 97.1859 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 3600TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 3.58 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 3.581 | 208 | 94 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 150 | 380 | 480 | 0.3581 | 0.7162 | 1.0743 | 1.7905 | 2.6858 | 3.581 | 84.9552 | 90.4271 | 92.825 | 93.7968 | 94.5716 | 94.4365 | 93.6007 | 85.0401 | 90.7332 | 93.4293 | 94.4908 | 95.7747 | 96.2727 | 94.5671 | 82.3717 | 88.9668 | 92.9784 | 94.2953 | 95.7884 | 95.6672 | 94.2539 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 3600TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 3.61 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.608 | 240 | 94 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 150 | 380 | 480 | 0.36084 | 0.72167 | 1.0825 | 1.8042 | 2.7063 | 3.6084 | 84.9226 | 90.0495 | 92.9079 | 93.7875 | 94.4318 | 94.456 | 93.5153 | 84.8681 | 90.93 | 93.8567 | 94.562 | 95.5583 | 95.9727 | 94.5066 | 82.4977 | 88.9887 | 92.2935 | 94.4687 | 94.7381 | 95.6144 | 93.6549 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 4000MTLP-US {208V} | N | N | Y | Y | Y | N | N | N | 4 kW, 208 Vac Grid Support Utility Interactive Inverter | 3.62 | 208 | 95.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.05 |  |  | 100 | 482 | 550 | 0.36 | 0.72 | 1.08 | 1.81 | 2.71 | 3.62 | 88.8 | 91.7 | 93.1 | 94.6 | 95.2 | 95.2 | 94.4 | 92.2 | 95.7 | 95.7 | 96.5 | 96.7 | 96.7 | 96.3 | 91.4 | 94.3 | 95.3 | 96.2 | 96.5 | 96.6 | 96 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 3800TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.888 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 3.888 | 240 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.593 |  |  | 160 | 380 | 480 | 0.38882 | 0.77764 | 1.1665 | 1.9441 | 2.9162 | 3.8882 | 92.9226 | 95.0495 | 95.9079 | 96.5875 | 96.7318 | 96.456 | 96.3523 | 95.8681 | 97.43 | 97.8567 | 98.062 | 98.0583 | 97.9727 | 97.9116 | 93.4977 | 96.4887 | 97.1935 | 97.6687 | 97.7381 | 97.6144 | 97.4199 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 4000TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 3.99 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.988 | 240 | 95 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 180 | 380 | 480 | 0.39884 | 0.79767 | 1.1965 | 1.9942 | 2.9913 | 3.9884 | 86.9226 | 91.0495 | 92.9079 | 94.5875 | 95.1318 | 95.156 | 94.2193 | 86.5681 | 92.23 | 94.3567 | 95.662 | 96.2583 | 96.1727 | 95.3116 | 84.4977 | 91.0887 | 93.3935 | 95.1687 | 96.1381 | 96.0144 | 94.8809 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 4000TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 4.0 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 4.004 | 208 | 95 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 150 | 380 | 480 | 0.4004 | 0.8008 | 1.2012 | 2.002 | 3.003 | 4.004 | 86.7552 | 91.4271 | 93.125 | 94.3968 | 94.9716 | 95.2365 | 94.1367 | 86.8401 | 92.1332 | 94.3293 | 95.6908 | 96.1747 | 96.1727 | 95.2761 | 84.8717 | 91.2668 | 93.5784 | 95.1953 | 96.0884 | 96.0672 | 94.9089 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 4000MTLP-US {240V} | N | N | Y | Y | Y | N | N | N | 4 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.05 | 240 | 96 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.05 |  |  | 100 | 482 | 550 | 0.4 | 0.81 | 1.21 | 2.02 | 3.04 | 4.05 | 89.5 | 92.1 | 93.7 | 95 | 95.5 | 95.6 | 94.8 | 93.1 | 95.4 | 96.2 | 96.9 | 97.1 | 97.1 | 96.7 | 92.3 | 94.8 | 95.9 | 96.6 | 96.9 | 97 | 96.4 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 4000MTLP-US {277V} | N | N | Y | Y | Y | N | N | N | 4 kW, 277 Vac Grid Support Utility Interactive Inverter | 4.06 | 277 | 96 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.05 |  |  | 100 | 482 | 550 | 0.41 | 0.81 | 1.22 | 2.03 | 3.04 | 4.06 | 88.3 | 91.5 | 93.1 | 94.6 | 95.3 | 95.5 | 94.4 | 93.6 | 95.7 | 96.6 | 95.3 | 97.4 | 97.4 | 96.6 | 92.7 | 95.1 | 96.3 | 96.9 | 97.2 | 97.3 | 96.8 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 5000TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4.28 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 4.28 | 208 | 97.5 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.576 |  |  | 210 | 380 | 480 | 0.42805 | 0.85609 | 1.2841 | 2.1402 | 3.2104 | 4.2805 | 93.9969 | 95.6291 | 96.5292 | 97.277 | 96.8685 | 96.4968 | 96.7182 | 95.6415 | 97.3556 | 97.7545 | 97.9536 | 97.7989 | 97.5872 | 97.707 | 95.0137 | 96.8034 | 97.3434 | 97.6629 | 97.6924 | 97.3985 | 97.478 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 5000MTLP-US {208V} | N | N | Y | Y | Y | N | N | N | 5 kW, 208 Vac Grid Support Utility Interactive Inverter | 4.59 | 208 | 95.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.05 |  |  | 100 | 482 | 550 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 89.9 | 92.5 | 93.8 | 94.9 | 95.1 | 95.1 | 94.6 | 93.2 | 95.3 | 96 | 96.6 | 96.7 | 96.6 | 96.4 | 92.5 | 94.8 | 95.7 | 96.4 | 96.6 | 96.5 | 96.2 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | SPH 4600TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 4.598 | 240 | 95 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 180 | 380 | 480 | 0.45977 | 0.91955 | 1.3793 | 2.2989 | 3.4483 | 4.5977 | 86.9226 | 92.0495 | 93.3079 | 94.9095 | 95.2538 | 95.188 | 94.4512 | 86.8681 | 92.43 | 94.5567 | 95.897 | 96.2323 | 96.2077 | 95.3949 | 85.4977 | 91.4887 | 93.6035 | 95.4327 | 96.2821 | 96.1164 | 95.103 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 4600TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 4.604 | 208 | 95 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 180 | 380 | 480 | 0.4604 | 0.9208 | 1.3812 | 2.302 | 3.453 | 4.604 | 86.7552 | 91.6271 | 93.425 | 94.7968 | 95.1716 | 95.2365 | 94.3727 | 87.8401 | 92.8332 | 94.7293 | 95.7908 | 96.2747 | 96.2727 | 95.4781 | 85.8717 | 92.5668 | 94.0784 | 95.2953 | 96.3884 | 96.2672 | 95.2639 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 5000TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4.943 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 4.943 | 240 | 97.5 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.593 |  |  | 210 | 380 | 480 | 0.49432 | 0.98864 | 1.483 | 2.4716 | 3.7074 | 4.9432 | 94.2674 | 96.0279 | 96.6177 | 96.9688 | 96.7976 | 96.4626 | 96.6555 | 95.8274 | 97.6476 | 97.9929 | 98.1977 | 98.0262 | 97.7757 | 97.9388 | 95.1548 | 97.2155 | 97.7005 | 97.9802 | 97.817 | 97.6089 | 97.6903 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 5000TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 4.95 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 4.954 | 240 | 95 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 230 | 380 | 480 | 0.49537 | 0.99073 | 1.4861 | 2.4768 | 3.7153 | 4.9537 | 88.2674 | 92.0279 | 93.9177 | 95.1688 | 95.5976 | 95.4626 | 94.8275 | 88.8274 | 93.6476 | 94.5929 | 96.1977 | 96.5262 | 95.9757 | 95.7458 | 86.6548 | 92.4155 | 93.7005 | 95.5802 | 96.117 | 96.1089 | 95.1503 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 5000TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 4.97 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 4.969 | 208 | 95.5 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 230 | 380 | 480 | 0.49688 | 0.99376 | 1.4906 | 2.4844 | 3.7266 | 4.9688 | 87.9969 | 91.8291 | 94.0292 | 95.277 | 95.6685 | 95.4968 | 94.8822 | 88.6415 | 93.5556 | 94.7545 | 95.9536 | 96.5989 | 96.0872 | 95.746 | 87.0137 | 92.8034 | 93.5434 | 96.1629 | 96.0924 | 96.1985 | 95.279 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 5000MTLP-US {277V} | N | N | Y | Y | Y | N | N | N | 5 kW, 277 Vac Grid Support Utility Interactive Inverter | 5.06 | 277 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.05 |  |  | 100 | 482 | 550 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 89.5 | 92.3 | 93.8 | 95 | 95.5 | 95.5 | 94.8 | 94.3 | 96.1 | 96.8 | 97.3 | 97.4 | 97.3 | 97.1 | 93.5 | 95.6 | 96.4 | 97 | 97.2 | 97.2 | 96.9 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 5000MTLP-US {240V} | N | N | Y | Y | Y | N | N | N | 5 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.07 | 240 | 96 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.05 |  |  | 100 | 482 | 550 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.07 | 90.5 | 93 | 94.3 | 95.2 | 95.4 | 95.3 | 94.9 | 93.9 | 95.8 | 96.5 | 97 | 97.1 | 96.9 | 96.8 | 93.1 | 95.3 | 96.1 | 96.8 | 96.9 | 96.9 | 96.6 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 6000TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.143 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 5.143 | 208 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.576 |  |  | 170 | 380 | 480 | 0.51426 | 1.0285 | 1.5428 | 2.5713 | 3.8569 | 5.1426 | 93.4812 | 95.1436 | 95.9216 | 96.4143 | 96.4086 | 96.2016 | 96.1607 | 95.7404 | 97.2023 | 97.6753 | 97.7276 | 97.7059 | 97.2003 | 97.5777 | 94.531 | 96.5287 | 97.1839 | 97.4841 | 97.5 | 97.1255 | 97.2727 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 6000TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 5.23 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 5.232 | 208 | 96 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 230 | 380 | 480 | 0.52322 | 1.0464 | 1.5697 | 2.6161 | 3.9242 | 5.2322 | 91.6216 | 94.3804 | 95.004 | 95.6415 | 95.648 | 95.6498 | 95.345 | 94.0058 | 96.3321 | 96.66 | 96.8442 | 96.8058 | 96.5216 | 96.6465 | 93.9666 | 96.0001 | 96.4128 | 96.8643 | 96.7314 | 96.4957 | 96.5622 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 6000MTLP-US {208V} | N | N | Y | Y | Y | N | N | N | 6 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.34 | 208 | 96 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.05 |  |  | 100 | 482 | 550 | 0.53 | 1.07 | 1.6 | 2.67 | 4.01 | 5.34 | 90.7 | 93.2 | 94.3 | 95 | 95 | 94.9 | 94.7 | 93.9 | 95.7 | 96.3 | 96.7 | 96.6 | 96.4 | 96.4 | 93.3 | 95.3 | 95.9 | 96.5 | 96.5 | 96.3 | 96.2 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | SPH 6000TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 5.86 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 5.864 | 240 | 96 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 230 | 380 | 480 | 0.58643 | 1.1729 | 1.7593 | 2.9322 | 4.3982 | 5.8643 | 91.5816 | 94.3604 | 94.954 | 95.5915 | 95.628 | 95.6398 | 95.3148 | 93.9658 | 96.3021 | 96.58 | 96.8142 | 96.7558 | 96.5216 | 96.601 | 93.9266 | 95.9701 | 96.3828 | 96.8343 | 96.7114 | 96.4757 | 96.5376 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 6000TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.918 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 5.918 | 240 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.593 |  |  | 170 | 380 | 480 | 0.59178 | 1.1836 | 1.7753 | 2.9589 | 4.4383 | 5.9177 | 93.4931 | 95.0713 | 96.0091 | 96.5068 | 96.5375 | 96.277 | 96.2595 | 96.2836 | 97.6235 | 97.995 | 98.0323 | 97.7405 | 97.6407 | 97.7632 | 95.2829 | 97.0935 | 97.4899 | 97.8279 | 97.6998 | 97.4333 | 97.5612 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 6000MTLP-US {240V} | N | N | Y | Y | Y | N | N | N | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 6.08 | 240 | 96 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.05 |  |  | 100 | 482 | 550 | 0.61 | 1.22 | 1.82 | 3.04 | 4.56 | 6.08 | 91.3 | 93.6 | 94.7 | 95.4 | 95.5 | 95.6 | 95.1 | 94.6 | 96.1 | 96.7 | 97 | 97 | 96.8 | 96.8 | 93.9 | 95.6 | 96.3 | 96.8 | 96.8 | 96.7 | 96.6 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 6000MTLP-US {277V} | N | N | Y | Y | Y | N | N | N | 6 kW, 277 Vac Grid Support Utility Interactive Inverter | 6.08 | 277 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.05 |  |  | 100 | 482 | 550 | 0.61 | 1.22 | 1.82 | 3.04 | 4.56 | 6.08 | 90.4 | 93 | 94.4 | 95.3 | 95.4 | 95.3 | 94.9 | 94.9 | 96.4 | 96.9 | 97.3 | 97.4 | 97.2 | 97.2 | 94.1 | 95.9 | 96.6 | 97.1 | 97.2 | 97.1 | 96.9 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 7000MTLP-US {208V} | N | N | Y | Y | Y | N | N | N | 7 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.093 | 208 | 96 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.05 |  |  | 280 | 385 | 485 | 609.3 | 1218.6 | 1827.9 | 3046.5 | 4569.75 | 6093 | 93.9 | 95.4 | 95.8 | 95.9 | 95.5 | 95.3 | 95.6 | 95.4 | 96.6 | 96.8 | 96.6 | 96.1 | 95.9 | 96.3 | 94.3 | 95.9 | 96.4 | 96.5 | 96.2 | 96 | 96.2 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 7600TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.58 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 6.58 | 208 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.576 |  |  | 212 | 380 | 480 | 0.65804 | 1.3161 | 1.9741 | 3.2902 | 4.9353 | 6.5804 | 93.7826 | 95.5421 | 96.606 | 96.8324 | 96.8224 | 96.4415 | 96.5939 | 95.6144 | 97.208 | 97.6283 | 97.7129 | 97.8083 | 97.3895 | 97.628 | 94.0659 | 96.3435 | 97.3147 | 97.3793 | 97.4451 | 97.2215 | 97.2142 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 7600TL-XH2 US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.61 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 6.611 | 208 | 95.6 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.12 |  |  | 150 | 345 | 500 | 0.661 | 1.322 | 1.983 | 3.306 | 4.959 | 6.611 | 88.96 | 92.49 | 94 | 94.76 | 94.85 | 94.47 | 94.36 | 93.96 | 96.07 | 96.65 | 96.88 | 96.88 | 96.67 | 96.69 | 90.55 | 94.4 | 95.25 | 95.84 | 96.07 | 96.16 | 95.62 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 7600MTLP-US {208V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.741 | 208 | 96 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.05 |  |  | 270 | 380 | 480 | 674.1 | 1348.2 | 2022.3 | 3370.51 | 5055.76 | 6741.01 | 94.1 | 95.5 | 95.7 | 95.7 | 95.2 | 95 | 95.3 | 95.7 | 96.7 | 96.8 | 96.6 | 96.1 | 95.9 | 96.3 | 94.7 | 96.2 | 96.5 | 96.5 | 96.1 | 95.8 | 96.2 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 7000MTLP-US {240V} | N | N | Y | Y | Y | N | N | N | 7 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.011 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.051 |  |  | 270 | 385 | 485 | 701.11 | 1402.22 | 2103.33 | 3505.55 | 5258.33 | 7011.1 | 94 | 95.7 | 95.9 | 96 | 95.8 | 95.5 | 95.8 | 95.7 | 96.8 | 97 | 96.9 | 96.7 | 96.4 | 96.7 | 94.6 | 96.4 | 96.8 | 96.9 | 96.7 | 96.3 | 96.6 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 7000MTLP-US {277V} | N | N | Y | Y | Y | N | N | N | 7 kW, 277 Vac Grid Support Utility Interactive Inverter | 7.0161 | 277 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KA 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.051 |  |  | 275 | 385 | 480 | 701.61 | 1403.21 | 2104.82 | 3508.04 | 5262.05 | 7016.07 | 92.8 | 95.2 | 95.4 | 95.9 | 96.1 | 95.9 | 95.8 | 93.6 | 96.3 | 96.7 | 96.9 | 96.8 | 96.5 | 96.6 | 95 | 96.6 | 97.1 | 97.3 | 97.2 | 97 | 97.1 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 8000MTLP-US {208V} | N | N | Y | Y | Y | N | N | N | 8 kW, 208 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 7.107 | 208 | 97 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KC 1.0] | 2018-10-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.3 |  |  | 330 | 480 | 550 | 0.7107 | 1.4214 | 2.1321 | 3.5535 | 5.3303 | 7.107 | 95.2319 | 96.8981 | 97.1668 | 97.2152 | 96.9406 | 96.7327 | 96.9445 | 95.3248 | 96.8981 | 97.3535 | 97.5256 | 97.3657 | 97.2044 | 97.2847 | 94.5675 | 96.5387 | 97.0783 | 97.371 | 97.2917 | 97.1309 | 97.1281 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 8200TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.2 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 7.166 | 208 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.71659 | 1.4332 | 2.1498 | 3.5829 | 5.3744 | 7.1659 | 93.818 | 95.9467 | 96.5916 | 96.9394 | 96.8921 | 96.7981 | 96.691 | 95.2258 | 97.2231 | 97.7432 | 97.9238 | 97.8229 | 97.7412 | 97.6966 | 93.7147 | 96.5216 | 97.2952 | 97.7041 | 97.7221 | 97.6373 | 97.4425 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | MIN 7600TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.524 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 7.524 | 240 | 97.5 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.593 |  |  | 212 | 380 | 480 | 0.75242 | 1.5048 | 2.2573 | 3.7621 | 5.6431 | 7.5242 | 94.8321 | 96.2443 | 96.9372 | 97.1359 | 97.0549 | 96.4681 | 96.899 | 96.1031 | 97.82 | 98.0103 | 98.1875 | 98.0302 | 97.4081 | 97.9421 | 95.2191 | 97.2034 | 97.6838 | 97.8749 | 97.7927 | 97.3782 | 97.6437 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 7600MTLP-US {240V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.604 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KC 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.051 |  |  | 270 | 380 | 480 | 760.4 | 1520.8 | 2281.19 | 3801.99 | 5702.99 | 7603.98 | 94.3 | 95.8 | 96.2 | 96.1 | 95.8 | 95.3 | 95.8 | 96.1 | 97 | 97.2 | 97.1 | 96.8 | 96.3 | 96.9 | 94.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.3 | 96.7 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 7600TL-XH2 US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 7.65 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 7.651 | 240 | 96 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.53 |  |  | 150 | 345 | 500 | 0.765 | 1.53 | 2.295 | 3.825 | 5.738 | 7.651 | 91.51 | 94.02 | 95.54 | 95.78 | 95.47 | 95.06 | 95.29 | 95.15 | 96.32 | 96.83 | 97.44 | 97.45 | 97.27 | 97.21 | 91.54 | 94.77 | 96.08 | 96.68 | 96.53 | 96.38 | 96.21 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 7600MTLP-US {277V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 277 Vac Grid Support Utility Interactive Inverter | 7.652 | 277 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KC 1.0] | 2019-01-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0.051 |  |  | 270 | 380 | 480 | 765.15 | 1530.3 | 2295.45 | 3825.75 | 5738.63 | 7651.5 | 94.3 | 95.8 | 96.2 | 96.1 | 95.8 | 95.3 | 95.8 | 96.1 | 97 | 97.2 | 97.1 | 96.8 | 96.3 | 96.9 | 94.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.3 | 96.7 | 2017-10-16 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 9000MTLP-US {208V} | N | N | Y | Y | Y | N | N | N | 9 kW, 208 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 7.864 | 208 | 97 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KC 1.0] | 2018-10-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.3 |  |  | 330 | 480 | 550 | 0.7864 | 1.5728 | 2.3592 | 3.932 | 5.898 | 7.864 | 95.4343 | 96.8634 | 97.1228 | 97.0837 | 96.7601 | 96.5393 | 96.8127 | 95.5184 | 96.9899 | 97.3531 | 97.4463 | 97.1787 | 97.0001 | 97.1711 | 94.827 | 96.6169 | 97.0564 | 97.2473 | 97.0819 | 96.8936 | 96.9907 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 9000TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 7.874 | 208 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.78742 | 1.5748 | 2.3623 | 3.9371 | 5.9056 | 7.8742 | 93.9829 | 96.0797 | 96.6986 | 97.0304 | 96.9127 | 96.7846 | 96.7465 | 95.5872 | 97.3526 | 97.782 | 97.9238 | 97.7705 | 97.6713 | 97.6909 | 94.5847 | 96.692 | 97.396 | 97.712 | 97.6675 | 97.5806 | 97.4678 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | SPH 8000TL-HU-US(B) {208V} | Y | Y | Y | Y | Y | Y | Y* | N | 8kW, 208 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 7.9075 | 208 | 96 | Intertek | [12/16/2024] | Intertek | [12/16/2024] | [Skaa-00] | 2025-02-21 | [12/16/2024] | 2025-02-21 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 54.38 |  |  | 160 | 370 | 450 | 0.79075 | 1.5815 | 2.3723 | 3.9538 | 5.9306 | 7.9075 | 92.7147 | 94.7026 | 95.7205 | 95.3803 | 94.8072 | 94.5138 | 94.9335 | 93.3925 | 96.7303 | 98.328 | 97.8196 | 97.55 | 96.4208 | 97.4362 | 96.0032 | 97.2174 | 97.722 | 96.9998 | 96.0451 | 96.139 | 96.5084 | 2025-02-21 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 8000TL-HU-US(B) {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 8kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 7.9251 | 240 | 96 | Intertek | [12/16/2024] | Intertek | [12/16/2024] | [Skaa-00] | 2025-02-21 | [12/16/2024] | 2025-02-21 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 53.28 |  |  | 160 | 370 | 450 | 0.79251 | 1.585 | 2.3775 | 3.9625 | 5.9438 | 7.9251 | 93.7414 | 94.3116 | 95.3773 | 96.1404 | 95.1985 | 94.2518 | 95.2678 | 93.9854 | 96.9456 | 97.0733 | 96.317 | 96.6317 | 96.3931 | 96.5165 | 95.2983 | 96.6715 | 96.9225 | 96.7206 | 96.1224 | 95.9018 | 96.3275 | 2025-02-21 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 8000MTLP-US {240V} | N | N | Y | Y | Y | N | N | N | 8 kW, 240 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 8.061 | 240 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KC 1.0] | 2018-10-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.5 |  |  | 330 | 480 | 550 | 0.8061 | 1.6122 | 2.4183 | 4.0305 | 6.0457 | 8.061 | 95.4816 | 96.806 | 97.2982 | 97.458 | 97.318 | 97.0166 | 97.2309 | 95.7939 | 97.0913 | 97.5954 | 97.859 | 97.7928 | 97.5766 | 97.6572 | 95.2637 | 96.7576 | 97.3124 | 97.6341 | 97.6942 | 97.5279 | 97.4834 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 8000MTLP-US {277V} | N | N | Y | Y | Y | N | N | N | 8 kW, 277 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 8.137 | 277 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KC 1.0] | 2018-10-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.7 |  |  | 330 | 480 | 550 | 0.8137 | 1.6274 | 2.4411 | 4.0685 | 6.1028 | 8.137 | 95.4421 | 96.6109 | 97.1824 | 97.5198 | 97.4925 | 97.2428 | 97.3225 | 96.2697 | 97.2044 | 97.777 | 98.0996 | 98.0984 | 97.9494 | 97.9348 | 95.8631 | 96.8898 | 97.4879 | 97.8391 | 97.9642 | 97.8946 | 97.7395 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 8200TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.2 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 8.251 | 240 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.82514 | 1.6503 | 2.4754 | 4.1257 | 6.1886 | 8.2514 | 93.9258 | 96.1247 | 96.8143 | 97.2666 | 97.2617 | 97.0721 | 97.0092 | 95.5722 | 97.4863 | 97.9916 | 98.2391 | 98.1842 | 98.0166 | 98.0249 | 93.7743 | 96.6734 | 97.4868 | 97.9609 | 97.966 | 97.9229 | 97.673 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | MIN 10000TL-XH2 US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 8.61 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 8.606 | 208 | 96 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.12 |  |  | 150 | 345 | 500 | 0.861 | 1.721 | 2.582 | 4.303 | 6.455 | 8.606 | 91.98 | 94.53 | 95.17 | 95.38 | 94.87 | 94.34 | 94.85 | 94.99 | 96.51 | 96.87 | 96.97 | 96.71 | 96.34 | 96.68 | 92.54 | 95.17 | 95.88 | 96.22 | 96.1 | 95.81 | 95.9 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 10000MTLP-US {208V} | N | N | Y | Y | Y | N | N | N | 10 kW, 208 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 8.63 | 208 | 97 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KC 1.0] | 2018-10-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.3 |  |  | 330 | 480 | 550 | 0.863 | 1.726 | 2.589 | 4.315 | 6.4725 | 8.63 | 95.5609 | 96.3702 | 96.5193 | 97.0537 | 96.6088 | 96.4293 | 96.6286 | 95.6227 | 96.7681 | 96.7901 | 97.4531 | 97.1269 | 96.9585 | 97.0684 | 95.0326 | 96.7812 | 97.1518 | 97.3399 | 96.9975 | 96.8805 | 96.9926 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 10000TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 8.76 | 208 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.87595 | 1.7519 | 2.6278 | 4.3797 | 6.5696 | 8.7595 | 94.7147 | 96.1872 | 96.7641 | 96.9456 | 96.7226 | 96.627 | 96.6625 | 96.1898 | 97.4947 | 97.8331 | 97.8547 | 97.653 | 97.5442 | 97.6451 | 94.884 | 96.9958 | 97.5353 | 97.726 | 97.6134 | 97.5151 | 97.4827 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 9000MTLP-US {240V} | N | N | Y | Y | Y | N | N | N | 9 kW, 240 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 9.061 | 240 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KC 1.0] | 2018-10-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.5 |  |  | 330 | 480 | 550 | 0.9061 | 1.8122 | 2.7183 | 4.5305 | 6.7957 | 9.061 | 95.9306 | 97.0351 | 97.3624 | 97.4055 | 97.1587 | 96.7832 | 97.1609 | 96.1264 | 97.3308 | 97.7098 | 97.8566 | 97.7061 | 97.4356 | 97.6427 | 95.536 | 96.9828 | 97.3349 | 97.5876 | 97.5568 | 97.3138 | 97.415 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 9000TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 9.063 | 240 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.90625 | 1.8125 | 2.7188 | 4.5312 | 6.7969 | 9.0625 | 94.2384 | 96.2702 | 96.908 | 97.3235 | 97.2 | 97.0403 | 97.018 | 95.9482 | 97.6026 | 98.0707 | 98.2515 | 98.1428 | 97.9914 | 98.0346 | 94.3716 | 96.8985 | 97.6347 | 98.0229 | 98.0409 | 97.9412 | 97.7795 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 9000MTLP-US {277V} | N | N | Y | Y | Y | N | N | N | 9 kW, 277 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 9.169 | 277 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KC 1.0] | 2018-10-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.7 |  |  | 330 | 480 | 550 | 0.9169 | 1.8338 | 2.7507 | 4.5845 | 6.8768 | 9.169 | 95.6877 | 96.866 | 97.3366 | 97.5417 | 97.445 | 97.1574 | 97.3387 | 96.3449 | 97.2806 | 97.7734 | 98.114 | 98.0647 | 97.8914 | 97.9234 | 95.9346 | 97.0873 | 97.6193 | 97.9244 | 98.0003 | 97.8943 | 97.8051 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Co., Ltd. | SPH 10000TL-HU-US {208V} | Y | Y | Y | Y | Y | Y | Y* | N | 10 kW, 208Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.767 | 208 | 97 | Intertek | [3/8/2024] | Intertek | [3/8/2024] | [Skaa-00] | 2024-05-21 | [3/8/2024] | 2024-05-21 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 71.72 |  |  | 165 | 370 | 450 | 0.9767 | 1.9534 | 2.9301 | 4.8835 | 7.3252 | 9.767 | 94.6343 | 95.553 | 95.9068 | 96.6465 | 96.199 | 95.45 | 96.1256 | 96.8912 | 97.4223 | 97.7861 | 97.6411 | 97.3935 | 97.2927 | 97.4689 | 95.6167 | 96.5583 | 97.6099 | 97.2567 | 96.061 | 95.8447 | 96.4942 | 2024-05-21 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 10000TL-HU-US(B) {208V} | Y | Y | Y | Y | Y | Y | Y* | N | 10 kW, 208 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 9.767 | 208 | 96.5 | Intertek | [8/26/2024] | Intertek | [8/26/2024] | [Skaa-00] | 2024-12-23 | [8/26/2024] | 2024-12-23 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 71.72 |  |  | 165 | 370 | 450 | 0.9767 | 1.9534 | 2.9301 | 4.8835 | 7.3252 | 9.767 | 94.6343 | 95.553 | 95.9068 | 96.6465 | 96.199 | 95.45 | 96.1256 | 96.8912 | 97.4223 | 97.7861 | 97.6411 | 97.3935 | 97.2927 | 97.4689 | 95.6167 | 96.5583 | 97.6099 | 97.2567 | 96.061 | 95.8447 | 96.4942 | 2024-12-23 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 11400TL-XH2 US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 9.83 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 9.827 | 208 | 96 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.12 |  |  | 150 | 345 | 500 | 0.983 | 1.965 | 2.948 | 4.914 | 7.371 | 9.827 | 92.75 | 94.53 | 95.11 | 95.21 | 94.79 | 94.19 | 94.79 | 95.4 | 96.64 | 96.95 | 96.91 | 96.57 | 96.12 | 96.62 | 93.16 | 95.44 | 96.01 | 96.2 | 96.01 | 95.63 | 95.89 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | SPH 10000TL-HU-US {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 10 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.925 | 240 | 96 | Intertek | [3/8/2024] | Intertek | [3/8/2024] | [Skaa-00] | 2024-05-21 | [3/8/2024] | 2024-05-21 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 77.25 |  |  | 165 | 370 | 450 | 0.9925 | 1.985 | 2.9775 | 4.9625 | 7.4438 | 9.925 | 92.1758 | 95.1599 | 95.5659 | 95.379 | 94.481 | 94.14 | 94.7244 | 96.9763 | 97.4188 | 97.8105 | 97.5927 | 97.2795 | 97.203 | 97.4 | 95.6685 | 96.3912 | 97.5705 | 97.0698 | 96.0899 | 95.9206 | 96.4631 | 2024-05-21 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 10000TL-HU-US(B) {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 10 kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 9.925 | 240 | 96 | Intertek | [8/26/2024] | Intertek | [8/26/2024] | [Skaa-00] | 2024-12-23 | [8/26/2024] | 2024-12-23 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 77.25 |  |  | 165 | 370 | 450 | 0.9925 | 1.985 | 2.9775 | 4.9625 | 7.4438 | 9.925 | 92.1758 | 95.1599 | 95.5659 | 95.379 | 94.481 | 94.14 | 94.7244 | 96.9763 | 97.4188 | 97.8105 | 97.5927 | 97.2795 | 97.203 | 97.4 | 95.6685 | 96.3912 | 97.5705 | 97.0698 | 96.0899 | 95.9206 | 96.4631 | 2024-12-23 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 11400TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 10.04 | 208 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.004 | 2.008 | 3.0119 | 5.0199 | 7.5298 | 10.0398 | 95.0284 | 96.5616 | 97.0154 | 97.1814 | 96.9023 | 96.8567 | 96.8802 | 95.703 | 97.5294 | 97.8587 | 97.8733 | 97.7607 | 97.7179 | 97.7001 | 95.102 | 97.007 | 97.5024 | 97.6871 | 97.6273 | 97.6013 | 97.4916 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | MIN 10000TL-XH2 US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10.0 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 10.057 | 240 | 96 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.53 |  |  | 150 | 345 | 500 | 1.006 | 2.011 | 3.017 | 5.028 | 7.543 | 10.057 | 92.34 | 94.23 | 94.98 | 95.27 | 95.01 | 94.61 | 94.9 | 95.92 | 97.15 | 97.46 | 97.53 | 97.29 | 97.04 | 97.29 | 93.38 | 95.77 | 96.41 | 96.71 | 96.64 | 96.4 | 96.44 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 10000MTLP-US {240V} | N | N | Y | Y | Y | N | N | N | 10 kW, 240 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 10.058 | 240 | 97 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KC 1.0] | 2018-10-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.5 |  |  | 330 | 480 | 550 | 1.0058 | 2.0116 | 3.0174 | 5.029 | 7.5435 | 10.058 | 95.7496 | 96.5751 | 96.6916 | 96.5323 | 96.917 | 96.6087 | 96.7299 | 95.8602 | 96.9019 | 97.0339 | 97.0528 | 97.6148 | 97.3005 | 97.3055 | 95.3753 | 96.9373 | 97.3973 | 97.6401 | 97.5368 | 97.2343 | 97.4102 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 10000TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 10.082 | 240 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.0082 | 2.0164 | 3.0246 | 5.041 | 7.5615 | 10.082 | 95.1276 | 96.4976 | 97.0675 | 97.3296 | 97.1985 | 96.9229 | 97.0787 | 96.3253 | 97.7618 | 98.1384 | 98.2919 | 98.1462 | 97.9316 | 98.0731 | 95.0134 | 97.1984 | 97.7803 | 98.0517 | 98.0092 | 97.8719 | 97.8234 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 10000MTLP-US {277V} | N | N | Y | Y | Y | N | N | N | 10 kW, 277 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 10.165 | 277 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [10/13/2017] | [KC 1.0] | 2018-10-15 | [10/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.7 |  |  | 330 | 480 | 550 | 1.0165 | 2.033 | 3.0495 | 5.0825 | 7.6238 | 10.165 | 95.5795 | 96.4291 | 96.9301 | 97.5168 | 97.3177 | 97.0515 | 97.1857 | 96.0695 | 97.219 | 97.3929 | 98.1228 | 97.9602 | 97.7314 | 97.8021 | 95.8737 | 97.1605 | 97.9253 | 97.9533 | 97.9509 | 97.7632 | 97.8163 | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Co., Ltd. | MIN 11400TL-XH2 US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 9.83 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 11.354 | 240 | 96.5 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.53 |  |  | 150 | 345 | 500 | 1.135 | 2.271 | 3.406 | 5.677 | 8.516 | 11.354 | 93.14 | 94.89 | 95.47 | 95.55 | 95.13 | 94.56 | 95.14 | 96.25 | 97.26 | 97.52 | 97.43 | 97.18 | 96.86 | 97.22 | 93.94 | 96.02 | 96.6 | 96.76 | 96.57 | 96.22 | 96.46 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | MIN 11400TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 11.52 | 240 | 98 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.152 | 2.304 | 3.456 | 5.76 | 8.64 | 11.52 | 95.3626 | 96.9572 | 97.4775 | 97.685 | 97.5433 | 97.3539 | 97.4392 | 96.5819 | 98.0275 | 98.3999 | 98.5274 | 98.4351 | 98.2539 | 98.3467 | 95.457 | 97.1914 | 97.7448 | 97.9708 | 97.8318 | 97.6582 | 97.7149 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | WIT 28K-H-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 28 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 27.8239 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.6 |  |  | 340 | 445 | 550 | 2.7824 | 5.5648 | 8.3472 | 13.912 | 20.8679 | 27.8239 | 89.3535 | 92.9799 | 93.5425 | 93.7804 | 94.1758 | 94.1687 | 93.7638 | 86.3526 | 91.6348 | 93.2996 | 94.6671 | 95.226 | 95.6842 | 94.3659 | 89.5969 | 93.4201 | 94.3331 | 94.4212 | 94.5744 | 94.4525 | 94.2504 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 28K-HU-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 28 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 27.8239 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.6 |  |  | 340 | 445 | 550 | 2.7824 | 5.5648 | 8.3472 | 13.912 | 20.8679 | 27.8239 | 89.3535 | 92.9799 | 93.5425 | 93.7804 | 94.1758 | 94.1687 | 93.7638 | 86.3526 | 91.6348 | 93.2996 | 94.6671 | 95.226 | 95.6842 | 94.3659 | 89.5969 | 93.4201 | 94.3331 | 94.4212 | 94.5744 | 94.4525 | 94.2504 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 33000TL3-US {480V} | N | N | Y | Y | Y | N | N | N | 33 kW, 480 Vac, three phases, 3/N/PE, Transformerless Grid Support Utility Interactive Inverter | 32.27 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [09/05/2018] | [teba0101] | 2019-01-15 | [09/05/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.092 |  |  | 480 | 700 | 800 | 3.23 | 6.45 | 9.68 | 16.14 | 24.2 | 32.27 | 97.3 | 97.8 | 98.1 | 98.1 | 97.8 | 97.5 | 97.9 | 97.8 | 98.6 | 98.8 | 98.9 | 98.7 | 98.5 | 98.7 | 97.5 | 98 | 98.3 | 98.5 | 98.3 | 98.1 | 98.3 | 2018-11-15 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | WIT 35K-H-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 35 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 34.8249 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.8 |  |  | 340 | 445 | 550 | 3.4825 | 6.965 | 10.4475 | 17.4124 | 26.1187 | 34.8249 | 90.1793 | 92.1362 | 92.9634 | 93.9766 | 94.1926 | 94.0402 | 93.7288 | 89.55 | 92.7943 | 93.9785 | 94.8535 | 95.0543 | 95.0025 | 94.5473 | 89.8865 | 92.2004 | 92.8939 | 93.9755 | 94.2824 | 94.2525 | 93.7699 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 35K-HU-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 35 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 34.8249 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.8 |  |  | 340 | 445 | 550 | 3.4825 | 6.965 | 10.4475 | 17.4124 | 26.1187 | 34.8249 | 90.1793 | 92.1362 | 92.9634 | 93.9766 | 94.1926 | 94.0402 | 93.7288 | 89.55 | 92.7943 | 93.9785 | 94.8535 | 95.0543 | 95.0025 | 94.5473 | 89.8865 | 92.2004 | 92.8939 | 93.9755 | 94.2824 | 94.2525 | 93.7699 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 36000TL3-US {480V} | N | N | Y | Y | Y | N | N | N | 36 kW, 480 Vac, three phases, 3/N/PE, Transformerless Grid Support Utility Interactive Inverter | 35.71 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [09/05/2018] | [teba0101] | 2019-01-15 | [09/05/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.051 |  |  | 520 | 700 | 800 | 3.57 | 7.14 | 10.71 | 17.86 | 26.78 | 35.71 | 97.5 | 98.1 | 98.2 | 98.3 | 97.9 | 97.6 | 98 | 98 | 98.6 | 98.6 | 98.6 | 98.6 | 98.4 | 98.6 | 97.4 | 98.1 | 98.2 | 98.2 | 98.3 | 98.1 | 98.2 | 2018-11-15 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | GROWATT 40000TL3-US {480V} | N | N | Y | Y | Y | N | N | N | 40 kW, 480Vac, three phases, 3/N/PE, Transformerless Grid Support Utility Interactive Inverter | 39.85 | 480 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [09/05/2018] | [teba0101] | 2019-01-15 | [09/05/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.051 |  |  | 570 | 700 | 800 | 3.98 | 7.97 | 11.95 | 19.92 | 29.89 | 39.85 | 97.5 | 98 | 98 | 98.2 | 98 | 97.6 | 98 | 98.2 | 98.6 | 98.6 | 98.4 | 98.7 | 98.5 | 98.6 | 97.5 | 98.1 | 98.1 | 98 | 98.3 | 98.1 | 98.2 | 2018-11-15 | 2019-01-15
Shenzhen Growatt New Energy Co., Ltd. | WIT 40K-H-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 40 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 39.9153 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.86 |  |  | 340 | 445 | 550 | 3.9915 | 7.9831 | 11.9746 | 19.9577 | 29.9365 | 39.9153 | 88.6409 | 91.9185 | 93.0057 | 93.731 | 93.8832 | 93.745 | 93.4311 | 90.4709 | 93.2534 | 94.2632 | 94.9549 | 95.0333 | 94.9341 | 94.648 | 87.8965 | 91.953 | 93.0647 | 93.8311 | 93.9925 | 93.8533 | 93.4945 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 40K-HU-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 40 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 39.9153 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.86 |  |  | 340 | 445 | 550 | 3.9915 | 7.9831 | 11.9746 | 19.9577 | 29.9365 | 39.9153 | 88.6409 | 91.9185 | 93.0057 | 93.731 | 93.8832 | 93.745 | 93.4311 | 90.4709 | 93.2534 | 94.2632 | 94.9549 | 95.0333 | 94.9341 | 94.648 | 87.8965 | 91.953 | 93.0647 | 93.8311 | 93.9925 | 93.8533 | 93.4945 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 50K-H-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 277 Vac Grid Support Utility Interactive Inverter | 49.2183 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.78 |  |  | 520 | 660 | 800 | 4.9218 | 9.8437 | 14.7655 | 24.6092 | 36.9137 | 49.2183 | 91.024 | 93.4794 | 94.4915 | 95.4508 | 95.8863 | 96.0973 | 95.3232 | 89.7386 | 92.6539 | 93.6591 | 95.4146 | 95.663 | 96.5287 | 95.0262 | 92.5268 | 94.5347 | 95.9508 | 96.8739 | 97.0983 | 97.1578 | 96.6054 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 50K-H-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 49.2183 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.78 |  |  | 520 | 660 | 800 | 4.9218 | 9.8437 | 14.7655 | 24.6092 | 36.9137 | 49.2183 | 91.024 | 93.4794 | 94.4915 | 95.4508 | 95.8863 | 96.0973 | 95.3232 | 89.7386 | 92.6539 | 93.6591 | 95.4146 | 95.663 | 96.5287 | 95.0262 | 92.5268 | 94.5347 | 95.9508 | 96.8739 | 97.0983 | 97.1578 | 96.6054 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 50K-HU-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 277 Vac Grid Support Utility Interactive Inverter | 49.2183 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.78 |  |  | 520 | 660 | 800 | 4.9218 | 9.8437 | 14.7655 | 24.6092 | 36.9137 | 49.2183 | 91.024 | 93.4794 | 94.4915 | 95.4508 | 95.8863 | 96.0973 | 95.3232 | 89.7386 | 92.6539 | 93.6591 | 95.4146 | 95.663 | 96.5287 | 95.0262 | 92.5268 | 94.5347 | 95.9508 | 96.8739 | 97.0983 | 97.1578 | 96.6054 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 50K-HU-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 49.2183 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.78 |  |  | 520 | 660 | 800 | 4.9218 | 9.8437 | 14.7655 | 24.6092 | 36.9137 | 49.2183 | 91.024 | 93.4794 | 94.4915 | 95.4508 | 95.8863 | 96.0973 | 95.3232 | 89.7386 | 92.6539 | 93.6591 | 95.4146 | 95.663 | 96.5287 | 95.0262 | 92.5268 | 94.5347 | 95.9508 | 96.8739 | 97.0983 | 97.1578 | 96.6054 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 55K-H-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 55 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 54.972 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.87 |  |  | 340 | 445 | 550 | 5.4972 | 10.9944 | 16.4916 | 27.486 | 41.229 | 54.972 | 90.4576 | 92.7793 | 93.5202 | 93.8925 | 93.7285 | 93.3291 | 93.5397 | 92.1892 | 94.1012 | 94.8002 | 95.0847 | 94.9182 | 94.5949 | 94.7728 | 90.3443 | 92.8849 | 93.5981 | 93.9775 | 93.8679 | 93.5563 | 93.6528 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 55K-HU-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 55 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 54.972 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.87 |  |  | 340 | 445 | 550 | 5.4972 | 10.9944 | 16.4916 | 27.486 | 41.229 | 54.972 | 90.4576 | 92.7793 | 93.5202 | 93.8925 | 93.7285 | 93.3291 | 93.5397 | 92.1892 | 94.1012 | 94.8002 | 95.0847 | 94.9182 | 94.5949 | 94.7728 | 90.3443 | 92.8849 | 93.5981 | 93.9775 | 93.8679 | 93.5563 | 93.6528 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 63K-H-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 63 kW, 277 Vac Grid Support Utility Interactive Inverter | 62.5698 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.66 |  |  | 520 | 660 | 800 | 6.257 | 12.514 | 18.7709 | 31.2849 | 46.9274 | 62.5698 | 92.7451 | 94.0137 | 94.892 | 95.6379 | 96.0413 | 96.1506 | 95.5909 | 90.7529 | 93.1172 | 94.3637 | 96.0455 | 96.3439 | 96.7951 | 95.6812 | 96.0987 | 96.9077 | 97.1195 | 97.2451 | 97.1695 | 96.8696 | 97.1085 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 63K-H-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 63 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 62.5698 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.66 |  |  | 520 | 660 | 800 | 6.257 | 12.514 | 18.7709 | 31.2849 | 46.9274 | 62.5698 | 92.7451 | 94.0137 | 94.892 | 95.6379 | 96.0413 | 96.1506 | 95.5909 | 90.7529 | 93.1172 | 94.3637 | 96.0455 | 96.3439 | 96.7951 | 95.6812 | 96.0987 | 96.9077 | 97.1195 | 97.2451 | 97.1695 | 96.8696 | 97.1085 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 63K-HU-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 63 kW, 277 Vac Grid Support Utility Interactive Inverter | 62.5698 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.66 |  |  | 520 | 660 | 800 | 6.257 | 12.514 | 18.7709 | 31.2849 | 46.9274 | 62.5698 | 92.7451 | 94.0137 | 94.892 | 95.6379 | 96.0413 | 96.1506 | 95.5909 | 90.7529 | 93.1172 | 94.3637 | 96.0455 | 96.3439 | 96.7951 | 95.6812 | 96.0987 | 96.9077 | 97.1195 | 97.2451 | 97.1695 | 96.8696 | 97.1085 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 63K-HU-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 63 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 62.5698 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.66 |  |  | 520 | 660 | 800 | 6.257 | 12.514 | 18.7709 | 31.2849 | 46.9274 | 62.5698 | 92.7451 | 94.0137 | 94.892 | 95.6379 | 96.0413 | 96.1506 | 95.5909 | 90.7529 | 93.1172 | 94.3637 | 96.0455 | 96.3439 | 96.7951 | 95.6812 | 96.0987 | 96.9077 | 97.1195 | 97.2451 | 97.1695 | 96.8696 | 97.1085 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 75K-H-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 277 Vac Grid Support Utility Interactive Inverter | 74.5887 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.39 |  |  | 520 | 660 | 800 | 7.4589 | 14.9177 | 22.3766 | 37.2944 | 55.9415 | 74.5887 | 92.7584 | 94.4451 | 95.2606 | 95.9213 | 96.2493 | 96.4023 | 95.8396 | 91.7788 | 93.5602 | 94.9048 | 96.3781 | 96.6739 | 96.7728 | 96.053 | 93.9304 | 95.5069 | 96.3065 | 96.9396 | 97.0081 | 97.0747 | 96.7147 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 75K-H-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 74.5887 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.39 |  |  | 520 | 660 | 800 | 7.4589 | 14.9177 | 22.3766 | 37.2944 | 55.9415 | 74.5887 | 92.7584 | 94.4451 | 95.2606 | 95.9213 | 96.2493 | 96.4023 | 95.8396 | 91.7788 | 93.5602 | 94.9048 | 96.3781 | 96.6739 | 96.7728 | 96.053 | 93.9304 | 95.5069 | 96.3065 | 96.9396 | 97.0081 | 97.0747 | 96.7147 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 75K-HU-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 277 Vac Grid Support Utility Interactive Inverter | 74.5887 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.39 |  |  | 520 | 660 | 800 | 7.4589 | 14.9177 | 22.3766 | 37.2944 | 55.9415 | 74.5887 | 92.7584 | 94.4451 | 95.2606 | 95.9213 | 96.2493 | 96.4023 | 95.8396 | 91.7788 | 93.5602 | 94.9048 | 96.3781 | 96.6739 | 96.7728 | 96.053 | 93.9304 | 95.5069 | 96.3065 | 96.9396 | 97.0081 | 97.0747 | 96.7147 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 75K-HU-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 74.5887 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.39 |  |  | 520 | 660 | 800 | 7.4589 | 14.9177 | 22.3766 | 37.2944 | 55.9415 | 74.5887 | 92.7584 | 94.4451 | 95.2606 | 95.9213 | 96.2493 | 96.4023 | 95.8396 | 91.7788 | 93.5602 | 94.9048 | 96.3781 | 96.6739 | 96.7728 | 96.053 | 93.9304 | 95.5069 | 96.3065 | 96.9396 | 97.0081 | 97.0747 | 96.7147 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 100K-H-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 277 Vac Grid Support Utility Interactive Inverter | 99.3703 | 277 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.36 |  |  | 520 | 660 | 800 | 9.937 | 19.8741 | 29.8111 | 49.6852 | 74.5277 | 99.3703 | 93.283 | 94.9912 | 95.423 | 95.9323 | 96.2295 | 96.1392 | 95.886 | 93.0324 | 94.3918 | 95.4827 | 96.4392 | 96.6953 | 96.5074 | 96.2249 | 94.6296 | 96.1332 | 96.7387 | 97.0403 | 97.0238 | 96.9629 | 96.8497 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 100K-H-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 99.3703 | 480 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.36 |  |  | 520 | 660 | 800 | 9.937 | 19.8741 | 29.8111 | 49.6852 | 74.5277 | 99.3703 | 93.283 | 94.9912 | 95.423 | 95.9323 | 96.2295 | 96.1392 | 95.886 | 93.0324 | 94.3918 | 95.4827 | 96.4392 | 96.6953 | 96.5074 | 96.2249 | 94.6296 | 96.1332 | 96.7387 | 97.0403 | 97.0238 | 96.9629 | 96.8497 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 100K-HU-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 277 Vac Grid Support Utility Interactive Inverter | 99.3703 | 277 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.36 |  |  | 520 | 660 | 800 | 9.937 | 19.8741 | 29.8111 | 49.6852 | 74.5277 | 99.3703 | 93.283 | 94.9912 | 95.423 | 95.9323 | 96.2295 | 96.1392 | 95.886 | 93.0324 | 94.3918 | 95.4827 | 96.4392 | 96.6953 | 96.5074 | 96.2249 | 94.6296 | 96.1332 | 96.7387 | 97.0403 | 97.0238 | 96.9629 | 96.8497 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 100K-HU-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 99.3703 | 480 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.36 |  |  | 520 | 660 | 800 | 9.937 | 19.8741 | 29.8111 | 49.6852 | 74.5277 | 99.3703 | 93.283 | 94.9912 | 95.423 | 95.9323 | 96.2295 | 96.1392 | 95.886 | 93.0324 | 94.3918 | 95.4827 | 96.4392 | 96.6953 | 96.5074 | 96.2249 | 94.6296 | 96.1332 | 96.7387 | 97.0403 | 97.0238 | 96.9629 | 96.8497 | 2024-06-21
Shenzhen GSL Energy Co., Ltd. | HS-LV8KNA {208V} | Y | Y | N | N | N | N | N |  | 8.8 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 8.8085 | 208 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.88085 | 1.7617 | 2.6426 | 4.4043 | 6.6064 | 8.8085 | 94.444 | 95.624 | 96.816 | 96.49 | 97.126 | 95.666 | 96.6999 | 94.382 | 95.75 | 96.022 | 96.526 | 97.2 | 95.958 | 96.6698 | 93.96 | 94.784 | 96.388 | 96.654 | 96.84 | 95.102 | 96.4418 | 2025-11-21
Shenzhen GSL Energy Co., Ltd. | HS-LV8KNA {240V} | Y | Y | N | N | N | N | N |  | 8.8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 8.81 | 240 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.88096 | 1.7619 | 2.6429 | 4.4048 | 6.6072 | 8.8096 | 94.272 | 95.424 | 96.778 | 96.326 | 97.096 | 95.646 | 96.6271 | 93.65 | 95.692 | 96.638 | 96.466 | 97.23 | 96.198 | 96.7268 | 94.002 | 95.676 | 96.698 | 96.354 | 96.548 | 95.556 | 96.3302 | 2025-11-21
Shenzhen GSL Energy Co., Ltd. | HS-LV10KNA {208V} | Y | Y | N | N | N | N | N |  | 10 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.0057 | 208 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 72.5 |  |  | 275 | 362.5 | 450 | 1.0006 | 2.0011 | 3.0017 | 5.0028 | 7.5043 | 10.0057 | 93.636 | 96.268 | 96.57 | 96.558 | 97.164 | 94.944 | 96.6685 | 94.79 | 96.362 | 96.58 | 96.79 | 97.524 | 95.16 | 96.9709 | 93.936 | 96.22 | 96.374 | 96.486 | 96.948 | 95.296 | 96.5426 | 2025-11-21
Shenzhen GSL Energy Co., Ltd. | HS-LV10KNA {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 10.0082 | 240 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 73.6 |  |  | 275 | 362.5 | 450 | 1.0008 | 2.0016 | 3.0025 | 5.0041 | 7.5061 | 10.0082 | 92.884 | 96.19 | 96.28 | 96.506 | 97.094 | 94.834 | 96.5462 | 93.182 | 96.368 | 96.912 | 96.706 | 97.522 | 95.052 | 96.9226 | 93.246 | 96.288 | 96.896 | 97.016 | 96.938 | 95.276 | 96.6861 | 2025-11-21
Shenzhen GSL Energy Co., Ltd. | HS-LV12KNA {208V} | Y | Y | N | N | N | N | N |  | 12 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.3972 | 208 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.0397 | 2.0794 | 3.1192 | 5.1986 | 7.7979 | 10.3972 | 95.11 | 95.714 | 96.534 | 96.55 | 96.714 | 95.27 | 96.4716 | 95.33 | 96.102 | 96.616 | 96.924 | 97.478 | 95.264 | 96.9928 | 95.036 | 95.774 | 96.604 | 96.55 | 96.668 | 95.186 | 96.4515 | 2025-11-21
Shenzhen GSL Energy Co., Ltd. | GSL-H-12KLV-US {208V} | Y | Y | N | N | N | N | N | Y | 10.4 kW, 208 Vac Grid support Utility Interactive Hybrid Inverter | 10.499 | 208 | 96.5 | Intertek | [9/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2022-12-12 |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.0499 | 2.0999 | 3.1498 | 5.2497 | 7.8745 | 10.4994 | 93.4773 | 95.2677 | 95.9298 | 95.8461 | 95.6083 | 95.2856 | 95.5784 | 95.0713 | 96.6555 | 97.0252 | 97.3102 | 97.0957 | 96.4058 | 96.9948 | 94.2867 | 96.7139 | 97.1633 | 96.953 | 96.7744 | 96.4653 | 96.7406 | 2022-12-12
Shenzhen GSL Energy Co., Ltd. | GSL-H-12KLV-US {240V} | Y | Y | N | N | N | N | N | Y | 12 kW, 240 Vac Grid support Utility Interactive Hybrid Inverter | 11.933 | 240 | 97 | Intertek | [9/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2022-12-12 |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.1933 | 2.3865 | 3.5798 | 5.9663 | 8.9494 | 11.9326 | 95.0246 | 96.0981 | 96.5396 | 96.4958 | 96.126 | 95.9005 | 96.1965 | 96.5925 | 97.1942 | 97.5102 | 97.3417 | 97.2365 | 97.1037 | 97.2569 | 95.8173 | 97.0077 | 97.4221 | 97.2641 | 97.1385 | 97.0353 | 97.1344 | 2022-12-12
Shenzhen GSL Energy Co., Ltd. | HS-LV12KNA {240V} | Y | Y | N | N | N | N | N |  | 12 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 11.9957 | 240 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.1996 | 2.3991 | 3.5987 | 5.9979 | 8.9968 | 11.9957 | 95.452 | 95.688 | 96.376 | 96.392 | 96.504 | 95.226 | 96.3183 | 95.568 | 96.168 | 96.69 | 96.874 | 97.428 | 95.228 | 96.9757 | 95.526 | 95.868 | 96.596 | 96.456 | 96.536 | 95.324 | 96.392 | 2025-11-21
Shenzhen Kstar New Energy Company Limited | E8KD {240V} | Y | Y | N | N | N | N | N | Y | 8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.024 | 240 | 97.5 | CSA Group | [5/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-12-11 |  | N | N | 20.79 |  |  | 200 | 300 | 400 | 0.802 | 1.605 | 2.407 | 4.012 | 6.018 | 8.024 | 95.56 | 96.7 | 96.92 | 96.95 | 96.64 | 96.29 | 96.68 | 96.57 | 97.45 | 97.7 | 97.59 | 97.37 | 97.04 | 97.41 | 96.78 | 98.15 | 98.24 | 98.08 | 97.84 | 97.49 | 97.89 | 2024-12-11
Shenzhen Kstar New Energy Company Limited | E10KD {240V} | Y | Y | N | N | N | N | N | Y | 10 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 10.036 | 240 | 97.5 | CSA Group | [5/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-12-11 |  | N | N | 20.79 |  |  | 240 | 300 | 400 | 1.004 | 2.007 | 3.011 | 5.018 | 7.527 | 10.036 | 96.22 | 97.14 | 97.18 | 97.14 | 96.76 | 96.29 | 96.86 | 97.06 | 97.65 | 97.59 | 97.49 | 97.14 | 96.7 | 97.26 | 97.38 | 98 | 98.08 | 97.89 | 97.59 | 97.18 | 97.7 | 2024-12-11
Shenzhen Kstar New Energy Company Limited | E12KD {240V} | Y | Y | N | N | N | N | N | Y | 12 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 12.02 | 240 | 97 | CSA Group | [5/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-12-11 |  | N | N | 20.79 |  |  | 200 | 300 | 400 | 1.202 | 2.404 | 3.606 | 6.01 | 9.015 | 12.02 | 95.15 | 96.36 | 96.71 | 96.63 | 96.2 | 95.67 | 96.29 | 95.34 | 96.88 | 97.22 | 97.18 | 96.85 | 96.36 | 96.88 | 96.15 | 97.26 | 97.5 | 97.64 | 97.21 | 96.84 | 97.28 | 2024-12-11
Shenzhen Kstar New Energy Company Limited | E15KD {240V} | Y | Y | N | N | N | N | N | Y | 15 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 14.993 | 240 | 97 | CSA Group | [5/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-12-11 |  | N | N | 20.79 |  |  | 240 | 300 | 400 | 1.499 | 2.999 | 4.498 | 7.497 | 11.245 | 14.993 | 96.25 | 97.24 | 97.34 | 96.97 | 96.34 | 95.56 | 96.6 | 96.53 | 97.55 | 97.62 | 97.28 | 96.68 | 95.93 | 96.92 | 97.54 | 98.07 | 98.1 | 97.72 | 97.11 | 96.45 | 97.39 | 2024-12-11
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 8K {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.8599 | 208 | 96.5 | Intertek | [3/12/2024] | Intertek | [3/12/2024] | [EA1.0] | 2024-04-22 | [3/12/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-08-11 |  | N | N | 18.53 |  |  | 210 | 360 | 480 | 0.78599 | 1.572 | 2.358 | 3.93 | 5.895 | 7.8599 | 92.7458 | 94.8821 | 95.7877 | 96.2814 | 95.7548 | 95.5452 | 95.6949 | 95.3183 | 96.7852 | 96.9298 | 97.2401 | 96.7733 | 96.6331 | 96.8255 | 94.866 | 96.387 | 96.7215 | 97.1053 | 96.6941 | 96.6144 | 96.6913 | 2022-08-11 | 2024-08-12
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 8K {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.8627 | 240 | 96.5 | Intertek | [3/12/2024] | Intertek | [3/12/2024] | [EA1.0] | 2024-04-22 | [3/12/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-08-11 |  | N | N | 18.84 |  |  | 210 | 360 | 480 | 0.78627 | 1.5725 | 2.3588 | 3.9313 | 5.897 | 7.8627 | 92.9578 | 94.8899 | 95.7481 | 96.2838 | 95.9702 | 95.8604 | 95.8294 | 95.5741 | 96.5787 | 96.6854 | 97.0389 | 96.7425 | 96.7486 | 96.7433 | 94.682 | 96.1785 | 96.6318 | 96.9367 | 96.7571 | 96.7998 | 96.67 | 2022-08-11 | 2024-08-12
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 10K {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.7577 | 208 | 96.5 | Intertek | [3/12/2024] | Intertek | [3/12/2024] | [EA1.0] | 2024-04-22 | [3/12/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-08-11 |  | N | N | 14.8 |  |  | 210 | 360 | 480 | 0.97577 | 1.9515 | 2.9273 | 4.8789 | 7.3183 | 9.7577 | 92.7092 | 94.8879 | 95.3456 | 95.9721 | 95.5079 | 95.3565 | 95.4354 | 96.1203 | 96.8726 | 97.0518 | 97.3038 | 96.7285 | 96.5437 | 96.8618 | 95.0454 | 96.5267 | 96.8926 | 97.167 | 96.5064 | 96.4285 | 96.6301 | 2022-08-11 | 2024-08-12
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 10K {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.7586 | 240 | 96.5 | Intertek | [3/12/2024] | Intertek | [3/12/2024] | [EA1.0] | 2024-04-22 | [3/12/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-08-11 |  | N | N | 14.3 |  |  | 210 | 360 | 480 | 0.97586 | 1.9517 | 2.9276 | 4.8793 | 7.3189 | 9.7586 | 93.035 | 95.0464 | 95.7433 | 96.0352 | 95.4309 | 95.34 | 95.4757 | 95.1061 | 96.6509 | 97.0749 | 97.2195 | 96.6243 | 96.5263 | 96.7391 | 94.2113 | 96.1002 | 96.6822 | 96.9911 | 96.5706 | 96.5369 | 96.5527 | 2022-08-11 | 2024-08-12
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 12K {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 10.499 | 208 | 96.5 | Intertek | [3/13/2024] | Intertek | [3/13/2024] | [fA1.0] | 2024-04-22 | [3/13/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-10-03 |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.0499 | 2.0999 | 3.1498 | 5.2497 | 7.8745 | 10.4994 | 93.4773 | 95.2677 | 95.9298 | 95.8461 | 95.6083 | 95.2856 | 95.5784 | 95.0713 | 96.6555 | 97.0252 | 97.3102 | 97.0957 | 96.4058 | 96.9948 | 94.2867 | 96.7139 | 97.1633 | 96.953 | 96.7744 | 96.4653 | 96.7406 | 2022-10-03 | 2024-04-22
Shenzhen Lux Power Technology Co., Ltd. | GEN-LB-US 13K {208V} | Y | Y | Y | Y | Y | Y | Y* | N | 13 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.325 | 208 | 97 | Intertek | [6/23/2025] | Intertek | [6/23/2025] | [fA1.0] | 2025-08-01 | [6/16/2025] | 2025-08-01 | Intertek | 2025-04-14 | No Information Submitted |  | N | N | 31.95 |  |  | 250 | 360 | 440 | 1.133 | 2.265 | 3.398 | 5.663 | 8.494 | 11.325 | 96.29 | 96.28 | 96.21 | 96.25 | 96.23 | 96.33 | 96.24 | 96.07 | 96.94 | 97.19 | 97.71 | 97.5 | 96.64 | 97.38 | 95.73 | 97.68 | 97.82 | 98 | 97.11 | 97.31 | 97.36 | 2025-08-01
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 13K {208V} | Y | Y | Y | Y | Y | Y | N | N | 16 kW, 208 Vac Grid support Hybrid Inverter with PCS functionality. | 11.325 | 208 | 97 | Intertek | [1/22/2025] | Intertek | [1/22/2025] | [fA1.0] | 2025-05-01 | [1/22/2025] | 2025-05-01 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 31.95 |  |  | 250 | 360 | 440 | 1.1325 | 2.265 | 3.3975 | 5.6625 | 8.4937 | 11.325 | 96.2893 | 96.2849 | 96.2071 | 96.2512 | 96.2259 | 96.3252 | 96.2394 | 96.0747 | 96.9361 | 97.1869 | 97.7129 | 97.4996 | 96.6438 | 97.3789 | 95.7303 | 97.6771 | 97.8156 | 97.9986 | 97.1094 | 97.3148 | 97.3644 | 2025-05-01
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 12K {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 11.933 | 240 | 97 | Intertek | [3/13/2024] | Intertek | [3/13/2024] | [fA1.0] | 2024-04-22 | [3/13/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-10-03 |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.1933 | 2.3865 | 3.5798 | 5.9663 | 8.9494 | 11.9326 | 95.0246 | 96.0981 | 96.5396 | 96.4958 | 96.126 | 95.9005 | 96.1965 | 96.5925 | 97.1942 | 97.5102 | 97.3417 | 97.2365 | 97.1037 | 97.2569 | 95.8173 | 97.0077 | 97.4221 | 97.2641 | 97.1385 | 97.0353 | 97.1344 | 2022-10-03 | 2024-04-22
Shenzhen Lux Power Technology Co., Ltd. | GEN-LB-US 13K {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 13 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.997 | 240 | 96.5 | Intertek | [6/23/2025] | Intertek | [6/23/2025] | [fA1.0] | 2025-08-01 | [6/16/2025] | 2025-08-01 | Intertek | 2025-04-14 | No Information Submitted |  | N | N | 29.57 |  |  | 250 | 360 | 440 | 1.3 | 2.599 | 3.899 | 6.499 | 9.748 | 12.997 | 95.84 | 96.15 | 95.67 | 96.57 | 96.39 | 96.14 | 96.3 | 96.62 | 97.05 | 97.3 | 98.11 | 96.99 | 96.68 | 97.24 | 96.24 | 96.52 | 96.56 | 96.51 | 96.26 | 96.12 | 96.35 | 2025-08-01
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 13K {240V} | Y | Y | Y | Y | Y | Y | N | N | 16 kW, 240 Vac Grid support Hybrid Inverter with PCS functionality. | 12.9973 | 240 | 96.5 | Intertek | [1/22/2025] | Intertek | [1/22/2025] | [fA1.0] | 2025-05-01 | [1/22/2025] | 2025-05-01 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 29.57 |  |  | 250 | 360 | 440 | 1.2997 | 2.5995 | 3.8992 | 6.4986 | 9.748 | 12.9973 | 95.8394 | 96.1488 | 95.6701 | 96.568 | 96.3915 | 96.1373 | 96.2951 | 96.6194 | 97.0472 | 97.3014 | 98.1054 | 96.9933 | 96.6758 | 97.2357 | 96.2395 | 96.5234 | 96.5619 | 96.5053 | 96.2597 | 96.1215 | 96.353 | 2025-05-01
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 16K {208V} | Y | Y | Y | Y | Y | Y | N | N | 13.8 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 13.8987 | 208 | 96.5 | Intertek | [10/11/24] | Intertek | [1/22/2025] | [fA1.0] | 2025-02-03 | [1/22/2025] | 2025-02-03 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.3899 | 2.7797 | 4.1696 | 6.9494 | 10.424 | 13.8987 | 95.2216 | 96.3623 | 96.3314 | 96.3567 | 96.0039 | 95.9864 | 96.103 | 95.5416 | 96.5717 | 96.9718 | 97.1706 | 97.0713 | 96.2488 | 96.9529 | 95.5994 | 96.8339 | 97.3771 | 97.1744 | 97.0907 | 96.9737 | 97.0643 | 2025-02-03
Shenzhen Lux Power Technology Co., Ltd. | GEN-LB-US 16K {208V} | Y | Y | Y | Y | Y | Y | Y* | N | 16 kW, 208 Vac Grid Support Utility Interactive Inverter | 13.899 | 208 | 96.5 | Intertek | [5/23/2025] | Intertek | [5/23/2025] | [fA1.0] | 2025-08-01 | [5/19/2025] | 2025-08-01 | Intertek | 2025-04-14 | No Information Submitted |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.39 | 2.78 | 4.17 | 6.949 | 10.424 | 13.899 | 95.22 | 96.36 | 96.33 | 96.36 | 96 | 95.99 | 96.1 | 95.54 | 96.57 | 96.97 | 97.17 | 97.07 | 96.25 | 96.95 | 95.6 | 96.83 | 97.38 | 97.17 | 97.09 | 96.97 | 97.06 | 2025-08-01
Shenzhen Lux Power Technology Co., Ltd. | GEN-LB-US 16K {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 16 kW, 240 Vac Grid Support Utility Interactive Inverter | 16.153 | 240 | 97 | Intertek | [5/23/2025] | Intertek | [5/23/2025] | [fA1.0] | 2025-08-01 | [5/19/2025] | 2025-08-01 | Intertek | 2025-04-14 | No Information Submitted |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.615 | 3.231 | 4.846 | 8.077 | 12.115 | 16.153 | 95.1 | 96 | 96.39 | 96.4 | 96.73 | 95.86 | 96.48 | 96.47 | 97.1 | 97.48 | 97.12 | 97.08 | 96.94 | 97.1 | 95.46 | 96.91 | 97.25 | 97.17 | 96.99 | 96.82 | 96.99 | 2025-08-01
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 16K {240V} | Y | Y | Y | Y | Y | Y | N | N | 16 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 16.1532 | 240 | 97 | Intertek | [10/11/24] | Intertek | [1/22/2025] | [fA1.0] | 2025-02-03 | [1/22/2025] | 2025-02-03 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.6153 | 3.2306 | 4.846 | 8.0766 | 12.1149 | 16.1532 | 95.0963 | 95.9965 | 96.3882 | 96.4022 | 96.7311 | 95.8608 | 96.4752 | 96.4687 | 97.0976 | 97.478 | 97.1222 | 97.077 | 96.941 | 97.1045 | 95.4554 | 96.9149 | 97.2473 | 97.1696 | 96.9929 | 96.8158 | 96.9863 | 2025-02-03
Shenzhen Lux Power Technology Co., Ltd. | GEN-HB-US 25K {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 21.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 21.6632 | 208 | 96.5 | Intertek | [10/27/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2025-11-17 |  |  | Y | N | 34.81 |  |  | 190 | 360 | 480 | 2.1663 | 4.3326 | 6.499 | 10.8316 | 16.2474 | 21.6632 | 95.7337 | 96.059 | 96.1625 | 96.1561 | 96.0996 | 95.9915 | 96.0969 | 95.9398 | 96.2286 | 96.3225 | 96.526 | 96.2301 | 96.2494 | 96.2926 | 96.3084 | 96.5349 | 96.6268 | 96.9377 | 96.5422 | 96.4234 | 96.6198 | 2026-06-22 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
Shenzhen Lux Power Technology Co., Ltd. | GEN-HB-US 25K {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 25 kW, 240 Vac Grid Support Utility Interactive Inverter | 25.1291 | 240 | 96.5 | Intertek | [10/27/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2025-11-17 |  |  | Y | N | 28.42 |  |  | 190 | 360 | 480 | 2.5129 | 5.0258 | 7.5387 | 12.5646 | 18.8468 | 25.1291 | 96.0006 | 96.1397 | 96.3289 | 96.5333 | 96.3477 | 96.2381 | 96.3546 | 96.1449 | 96.3247 | 96.5119 | 96.6265 | 96.4352 | 96.3402 | 96.4627 | 96.3032 | 96.6022 | 96.8131 | 97.1518 | 96.5163 | 96.4328 | 96.677 | 2026-06-22 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
Shenzhen Megarevo Technology Co., Ltd. | R5KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 5.081 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.4332 |  |  | 180 | 360 | 430 | 0.508 | 1.016 | 1.524 | 2.541 | 3.811 | 5.081 | 94.78 | 95.87 | 96.54 | 97.73 | 97.23 | 96.77 | 97.06 | 95.47 | 96.39 | 97.44 | 98.31 | 97.79 | 97.53 | 97.68 | 95.11 | 96.89 | 96.83 | 97.99 | 97.73 | 97.13 | 97.5 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R5KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 5.0897 | 240 | 97 | SGS | [9/15/2023] | SGS | [9/15/2023] | [Ver0306] | No Information Submitted | [9/15/2023] | No Information Submitted | SGS | 2023-07-19 | No Information Submitted |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2023-05-11 | 2024-03-21
Shenzhen Megarevo Technology Co., Ltd. | R6KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 6.082 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.02 |  |  | 180 | 360 | 430 | 0.608 | 1.216 | 1.825 | 3.041 | 4.562 | 6.082 | 94.57 | 95.91 | 96.64 | 97.49 | 96.98 | 96.44 | 96.87 | 95.36 | 96.6 | 97.72 | 98.25 | 97.84 | 97.32 | 97.72 | 94.95 | 96.15 | 97.25 | 97.96 | 97.52 | 97.06 | 97.38 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R6KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 6.117 | 240 | 97 | SGS | [9/15/2023] | SGS | [9/15/2023] | [Ver0306] | No Information Submitted | [9/15/2023] | No Information Submitted | SGS | 2023-07-19 | No Information Submitted |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2023-05-11 | 2024-03-21
Shenzhen Megarevo Technology Co., Ltd. | R7K6H1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 7.765 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.3655 |  |  | 180 | 360 | 430 | 0.776 | 1.553 | 2.329 | 3.882 | 5.823 | 7.765 | 94.67 | 95.75 | 96.57 | 97.46 | 96.99 | 96.45 | 96.85 | 95.25 | 96.32 | 97.47 | 98.31 | 97.88 | 97.29 | 97.71 | 94.9 | 95.96 | 97.14 | 97.88 | 97.37 | 96.89 | 97.26 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R7K6LNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 7.765 | 240 | 97 | SGS | [9/15/2023] | SGS | [9/15/2023] | [Ver0306] | No Information Submitted | [9/15/2023] | No Information Submitted | SGS | 2023-07-19 | No Information Submitted |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2023-05-11 | 2024-03-21
Shenzhen Megarevo Technology Co., Ltd. | R8KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 8.084 | 240 | 97.5 | SGS | [9/15/2023] | SGS | [9/15/2023] | [Ver0306] | No Information Submitted | [9/15/2023] | No Information Submitted | SGS | 2023-07-19 | No Information Submitted |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2023-05-11 | 2024-03-21
Shenzhen Megarevo Technology Co., Ltd. | R8KLNA-P4 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.0 kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 8.111 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 20.205 |  |  | 150 | 360 | 430 | 0.8111 | 1.6222 | 2.4333 | 4.0555 | 6.0832 | 8.111 | 93.7032 | 94.658 | 95.6518 | 96.6831 | 96.5045 | 96.1164 | 96.2159 | 94.1867 | 95.5035 | 96.5637 | 97.5413 | 97.1721 | 96.9438 | 96.9623 | 94.0252 | 95.3961 | 96.1441 | 97.253 | 96.9761 | 96.6831 | 96.7227 | 2024-11-21
Shenzhen Megarevo Technology Co., Ltd. | R8KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 8.116 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.021 |  |  | 200 | 360 | 430 | 0.812 | 1.623 | 2.435 | 4.058 | 6.087 | 8.116 | 94.42 | 95.83 | 96.39 | 97.57 | 97.36 | 96.6 | 97.06 | 95.36 | 96.47 | 97.54 | 98.25 | 97.81 | 97.37 | 97.69 | 94.87 | 96.17 | 97.07 | 97.94 | 97.8 | 97.13 | 97.51 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R8KLNA-P6 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.0 kW, 240Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 8.1809 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 19.254 |  |  | 150 | 360 | 430 | 0.81809 | 1.6362 | 2.4543 | 4.0905 | 6.1357 | 8.1809 | 93.4783 | 94.6843 | 95.5771 | 96.7312 | 96.4419 | 96.1554 | 96.1782 | 94.1318 | 95.3434 | 96.55 | 97.5594 | 97.2213 | 96.7995 | 96.9732 | 93.9303 | 95.1558 | 96.1549 | 97.2766 | 97.0383 | 96.4559 | 96.7348 | 2024-11-21
Shenzhen Megarevo Technology Co., Ltd. | R9KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 9 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 9.103 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.1397 |  |  | 200 | 360 | 430 | 0.91 | 1.821 | 2.731 | 4.551 | 6.827 | 9.103 | 94.43 | 95.76 | 96.56 | 97.5 | 97.03 | 96.53 | 96.88 | 95.28 | 96.44 | 97.43 | 98.28 | 97.77 | 97.3 | 97.65 | 95.14 | 95.94 | 97.15 | 97.85 | 97.48 | 96.99 | 97.32 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R10KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 10 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 10.154 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.0848 |  |  | 250 | 360 | 430 | 1.015 | 2.031 | 3.046 | 5.077 | 7.616 | 10.154 | 94.46 | 95.68 | 96.64 | 97.53 | 96.98 | 96.37 | 96.86 | 95.29 | 96.36 | 97.31 | 98.21 | 97.97 | 97.45 | 97.73 | 94.84 | 95.95 | 96.94 | 97.77 | 97.47 | 96.97 | 97.26 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R10KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 10.177 | 240 | 97 | SGS | [9/15/2023] | SGS | [9/15/2023] | [Ver0306] | No Information Submitted | [9/15/2023] | No Information Submitted | SGS | 2023-07-19 | No Information Submitted |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2023-05-11 | 2024-03-21
Shenzhen Megarevo Technology Co., Ltd. | R11K4H1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 11.598 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.0512 |  |  | 250 | 360 | 430 | 1.16 | 2.32 | 3.479 | 5.799 | 8.699 | 11.598 | 94.52 | 95.67 | 96.86 | 97.58 | 96.98 | 96.68 | 96.91 | 95.34 | 96.27 | 97.31 | 98.23 | 97.96 | 97.37 | 97.72 | 94.94 | 95.86 | 97.01 | 97.89 | 97.36 | 97.09 | 97.25 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R12KLNA-P4 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12.0 kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 12.1371 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 19.85 |  |  | 200 | 360 | 430 | 1.2137 | 2.4274 | 3.6411 | 6.0686 | 9.1028 | 12.1371 | 93.6636 | 94.7366 | 95.8921 | 96.8165 | 96.5363 | 96.1752 | 96.2949 | 94.2679 | 95.609 | 96.6993 | 97.5191 | 97.2309 | 96.7878 | 97.0058 | 94.2082 | 95.4735 | 96.3042 | 97.2515 | 96.9592 | 96.5623 | 96.7378 | 2024-11-21
Shenzhen Megarevo Technology Co., Ltd. | R12KLNA-P6 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12.0 kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 12.2135 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 13.202 |  |  | 200 | 360 | 430 | 1.2214 | 2.4427 | 3.6641 | 6.1068 | 9.1601 | 12.2135 | 93.6096 | 94.6754 | 95.8363 | 96.8413 | 96.422 | 95.9874 | 96.2182 | 94.3362 | 95.3888 | 96.4568 | 97.5342 | 97.106 | 96.8384 | 96.908 | 93.9397 | 95.049 | 96.1157 | 97.2352 | 96.8097 | 96.3485 | 96.5899 | 2024-11-21
Shenzhen Megarevo Technology Co., Ltd. | R12KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 12 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 12.362 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.0487 |  |  | 250 | 360 | 430 | 1.236 | 2.472 | 3.709 | 6.181 | 9.272 | 12.362 | 94.43 | 95.74 | 96.84 | 97.57 | 97.16 | 96.62 | 97 | 95.1 | 96.35 | 97.29 | 98.24 | 97.9 | 97.33 | 97.68 | 94.93 | 96 | 96.97 | 97.89 | 97.43 | 97.09 | 97.28 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R16LNA-P4 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 16.0 kW, 240Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 16.1309 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 19.23 |  |  | 220 | 360 | 430 | 1.6131 | 3.2262 | 4.8393 | 8.0655 | 12.0982 | 16.1309 | 93.7909 | 94.8057 | 95.743 | 96.6913 | 96.4404 | 95.9995 | 96.1996 | 94.4435 | 95.6318 | 96.6583 | 97.5607 | 97.1891 | 96.599 | 96.9863 | 94.2996 | 95.0169 | 96.238 | 97.1403 | 96.7969 | 96.3892 | 96.5927 | 2024-11-21
Shenzhen Megarevo Technology Co., Ltd. | R16KLNA-P6 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 16.0 kW, 240Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 16.1988 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 20.465 |  |  | 220 | 360 | 430 | 1.6199 | 3.2398 | 4.8596 | 8.0994 | 12.1491 | 16.1988 | 93.6398 | 94.6882 | 95.7477 | 96.6139 | 96.4152 | 96.0602 | 96.1617 | 94.3008 | 95.4624 | 96.4359 | 97.5442 | 97.2542 | 96.8193 | 96.9875 | 93.8386 | 95.1008 | 96.1652 | 97.1016 | 96.8655 | 96.2759 | 96.5923 | 2024-11-21
Shenzhen Poweroak Newener Co Ltd | EP900 {240V} | Y | Y | N | N | N | N | Y* | N | 9 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.23 | 240 | 95 | Intertek | [12/20/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-01-09 | No Information Submitted |  | N | N | 11.7 |  |  | 86 | 100 | 113 | 0.92297 | 1.8459 | 2.7689 | 4.6149 | 6.9223 | 9.2297 | 91.2622 | 94.8345 | 95.4546 | 95.2169 | 94.5125 | 93.662 | 94.6171 | 91.4645 | 94.5626 | 95.4472 | 95.3814 | 94.9862 | 94.2891 | 94.9276 | 90.698 | 94.6443 | 94.8447 | 95.3783 | 95.212 | 94.6643 | 94.9665 | 2025-06-02 | 2025-12-01
Shenzhen Poweroak Newener Co Ltd | EnergyPro 13K {240V} | Y | Y | N | N | N | N | Y* |  | 13.2 kVA, 240V split phase, Grid Support Inverter with PCS functionality | 13.1961 | 240 | 97 | Intertek | [7/8/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2025-07-11 |  |  | N | N | 16.4 |  |  | 370 | 420 | 500 | 1.3196 | 2.6392 | 3.9588 | 6.598 | 9.8971 | 13.1961 | 95.5412 | 97.4059 | 97.655 | 97.6563 | 97.4482 | 97.1279 | 97.4223 | 95.0427 | 97.0198 | 97.3378 | 97.4362 | 97.2394 | 96.9072 | 97.1771 | 94.0961 | 96.5435 | 96.954 | 97.1164 | 96.952 | 96.6122 | 96.8351 | 2025-09-02 | 2025-10-13
Shenzhen Senergy Technology Co., Ltd. | SE 5KHB-130-D2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 5.02 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 92.68 | 95.27 | 95.93 | 96.35 | 96.16 | 95.99 | 95.98 | 93.57 | 95.86 | 96.53 | 97.03 | 97.08 | 96.97 | 96.8 | 93.73 | 95.93 | 96.5 | 96.81 | 96.9 | 96.81 | 96.65 | 2024-02-01 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 5KHB-130-D2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 5.04 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.504 | 1.008 | 1.512 | 2.52 | 3.78 | 5.04 | 92.99 | 95.51 | 96.13 | 96.56 | 96.34 | 96.22 | 96.18 | 93.67 | 95.99 | 96.75 | 97.31 | 97.43 | 97.38 | 97.1 | 93.79 | 96.14 | 96.61 | 96.98 | 97.24 | 97.24 | 96.92 | 2024-02-01 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 6KHB-130-D2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 6.124 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.61237 | 1.2247 | 1.8371 | 3.0618 | 4.5927 | 6.1237 | 91.5057 | 94.3751 | 95.4429 | 96.1451 | 96.2033 | 96.0221 | 95.8115 | 93.6071 | 95.9507 | 96.6981 | 97.1632 | 97.1394 | 97.0155 | 96.8845 | 93.0132 | 95.454 | 96.3177 | 96.9016 | 96.9299 | 96.7629 | 96.6117 | 2024-02-01 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 6KHB-130-D2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 6.149 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.61493 | 1.2299 | 1.8448 | 3.0747 | 4.612 | 6.1493 | 91.5991 | 94.4496 | 95.4631 | 96.2597 | 96.4111 | 96.355 | 95.9722 | 93.875 | 96.1389 | 96.881 | 97.3815 | 97.4928 | 97.4245 | 97.1802 | 92.6866 | 95.4464 | 96.4097 | 97.0954 | 97.2951 | 97.2686 | 96.8688 | 2024-02-01 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 7K6HB-180-T2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6472 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.76472 | 1.5294 | 2.2942 | 3.8236 | 5.7354 | 7.6472 | 92.9526 | 95.5516 | 96.215 | 96.6536 | 96.4528 | 96.189 | 96.2682 | 89.7494 | 96.0782 | 96.7932 | 97.1622 | 96.9742 | 96.771 | 96.648 | 94.069 | 96.2392 | 96.7722 | 97.1198 | 96.913 | 96.6498 | 96.7789 | 2023-11-13 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 7K6HB-180-T2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 7.648 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.736 | 7.648 | 92.946 | 95.544 | 96.21 | 96.648 | 96.448 | 96.186 | 96.2631 | 93.74 | 96.074 | 96.788 | 97.158 | 96.97 | 96.766 | 96.8034 | 94.064 | 96.234 | 96.766 | 97.116 | 96.906 | 96.704 | 96.7759 | 2024-02-01 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 8KHB-180-T2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac Grid Support Utility Interactive Inverter | 8.0472 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.80472 | 1.6094 | 2.4142 | 4.0236 | 6.0354 | 8.0472 | 92.9526 | 95.5528 | 96.2152 | 96.6546 | 96.452 | 96.1892 | 96.2681 | 93.7514 | 96.077 | 96.7964 | 97.1666 | 96.974 | 96.7728 | 96.8093 | 94.0688 | 96.2392 | 96.77 | 97.1224 | 96.9124 | 96.6488 | 96.7788 | 2023-11-13 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 8KHB-180-T2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 208 Vac Grid Support Utility Interactive Inverter | 8.06 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 17.78 |  |  | 200 | 360 | 480 | 0.806 | 1.612 | 2.418 | 4.03 | 6.045 | 8.06 | 92.852 | 95.4494 | 96.1102 | 96.5538 | 96.3506 | 96.0918 | 96.1665 | 93.649 | 95.9818 | 96.693 | 97.0644 | 96.8732 | 96.6702 | 96.708 | 93.969 | 96.1426 | 96.6718 | 97.023 | 96.8134 | 96.5544 | 96.6802 | 2023-11-13 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 11K4HB-210-T2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 10.14 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.91 | 95.48 | 96.12 | 96.56 | 96.36 | 96.1 | 96.18 | 93.66 | 96.02 | 96.72 | 97.07 | 96.88 | 96.68 | 96.72 | 94.07 | 96.17 | 96.67 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-07-22 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 10KHB-210-T2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.1472 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 18 | 200 | 360 | 200 | 360 | 480 | 1.0147 | 2.0294 | 3.0442 | 5.0736 | 7.6104 | 10.1472 | 92.9963 | 95.5759 | 96.2237 | 96.6613 | 96.4562 | 96.1983 | 96.2761 | 93.7907 | 96.1027 | 96.8102 | 97.1618 | 96.9743 | 96.7739 | 96.8131 | 94.1119 | 96.2672 | 96.7835 | 97.1258 | 96.9159 | 96.6586 | 96.7866 | 2024-09-03 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 10KHB-210-T2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.1858 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.0186 | 2.0372 | 3.0557 | 5.0929 | 7.6393 | 10.1858 | 92.8933 | 95.4787 | 96.1281 | 96.5592 | 96.3579 | 96.0975 | 96.177 | 93.6955 | 96.0051 | 96.7063 | 97.0717 | 96.8789 | 96.675 | 96.7174 | 94.0173 | 96.1625 | 96.6817 | 96.9927 | 96.8158 | 96.5601 | 96.6795 | 2023-11-13 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 11K4HB-210-T2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 10.186 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.028 | 3.042 | 5.07 | 7.605 | 10.14 | 93.05 | 95.58 | 96.24 | 96.66 | 96.45 | 96.2 | 96.28 | 93.72 | 96.07 | 96.82 | 97.15 | 96.96 | 96.78 | 96.8 | 94.05 | 96.25 | 96.79 | 97.12 | 96.92 | 96.66 | 96.79 | 2024-07-22 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 11K4HB-T2/LV-ULP {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 11.5669 | 240 | 96.5 | SGS | [3/28/2025] | SGS | [3/28/2025] | [051001] | 2025-07-01 | [3/28/2025] | 2025-07-01 | SGS | 2025-06-06 | 2025-07-01 |  | N | N | 19 |  |  | 200 | 360 | 480 | 1.1567 | 2.3134 | 3.4701 | 5.7834 | 8.6752 | 11.5669 | 93.0675 | 95.5749 | 96.2997 | 96.6409 | 96.4392 | 96.2088 | 96.2752 | 93.6781 | 96.0439 | 96.7972 | 97.1353 | 96.9536 | 96.7793 | 96.7878 | 94.0465 | 96.3229 | 96.8228 | 97.1182 | 96.9286 | 96.6545 | 96.7965 | 2025-07-01
Shenzhen Senergy Technology Co., Ltd. | SE 11K4HB-T2/LV-ULP {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 11.6088 | 208 | 96.5 | SGS | [3/28/2025] | SGS | [3/28/2025] | [051001] | 2025-07-01 | [3/28/2025] | 2025-07-01 | SGS | 2025-06-06 | 2025-07-01 |  | N | N | 19 |  |  | 200 | 360 | 480 | 1.1609 | 2.3218 | 3.4827 | 5.8044 | 8.7066 | 11.6088 | 92.8881 | 95.4935 | 96.1138 | 96.5693 | 96.353 | 96.1025 | 96.1756 | 93.6426 | 96.0296 | 96.7159 | 97.0645 | 96.8809 | 96.677 | 96.7174 | 94.0961 | 96.1711 | 96.6734 | 96.9968 | 96.8241 | 96.5565 | 96.6871 | 2025-07-01
Shenzhen Sinexcel Isuna Energy Technology Co., Ltd. | Isuna U10K-PH {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 10.074 | 240 | 97 | Intertek | [12/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 21.406 |  |  | 140 | 320 | 500 | 1.007 | 2.015 | 3.022 | 5.037 | 7.555 | 10.074 | 92.03 | 93.91 | 95.29 | 96.22 | 96.62 | 96.53 | 96.05 | 93.89 | 95.38 | 96.16 | 96.87 | 97.32 | 97.34 | 96.85 | 95.68 | 96.99 | 97.54 | 97.87 | 98.03 | 97.89 | 97.78 | 2026-02-23 |  | Y | N | N | N | N | N | N | N | N
Shenzhen Sinexcel Isuna Energy Technology Co., Ltd. | Isuna U15K-PH {240V} | Y | Y | N | N | N | N | N |  | 15 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 15.042 | 240 | 97 | Intertek | [12/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 21.42 |  |  | 140 | 320 | 500 | 1.504 | 3.008 | 4.513 | 7.521 | 11.281 | 15.042 | 95.39 | 95.29 | 96.25 | 96.62 | 96.44 | 96.07 | 96.34 | 95.33 | 96.16 | 96.99 | 97.32 | 97.32 | 97.16 | 97.14 | 97.49 | 97.54 | 98 | 98.03 | 97.84 | 97.58 | 97.85 | 2026-02-23 |  | Y | N | N | N | N | N | N | N | N
Shenzhen Sinexcel Isuna Energy Technology Co., Ltd. | Isuna U20K-PH {240V} | Y | Y | N | N | N | N | N |  | 20 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 20.181 | 240 | 97 | Intertek | [12/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 21.408 |  |  | 140 | 320 | 500 | 2.018 | 4.036 | 6.054 | 10.09 | 15.136 | 20.181 | 93.91 | 95.93 | 96.47 | 96.53 | 96.07 | 95.54 | 96.09 | 95.38 | 97.14 | 97.14 | 97.34 | 97.16 | 96.73 | 97.1 | 96.99 | 97.82 | 98 | 97.89 | 97.58 | 96.64 | 97.64 | 2026-02-23 |  | Y | N | N | N | N | N | N | N | N
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL8K-P2US {240V} | Y | Y | N | N | N | N | Y* |  | 7.98 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.9814 | 240 | 96 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.39 |  |  | 108 | 380 | 480 | 0.79814 | 1.5963 | 2.3944 | 3.9907 | 5.986 | 7.9814 | 90.9385 | 94.1039 | 94.9752 | 95.083 | 95.0387 | 94.6196 | 94.8087 | 92.1593 | 95.6656 | 96.6163 | 96.6433 | 97.0374 | 96.9779 | 96.6374 | 92.4438 | 95.9014 | 96.6012 | 97.0486 | 97.2916 | 97.2167 | 96.8905 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL8K-P2US-S {240V} | Y | Y | N | N | N | N | Y* |  | 7.98 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.9814 | 240 | 96 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.39 |  |  | 108 | 380 | 480 | 0.79814 | 1.5963 | 2.3944 | 3.9907 | 5.986 | 7.9814 | 90.9385 | 94.1039 | 94.9752 | 95.083 | 95.0387 | 94.6196 | 94.8087 | 92.1593 | 95.6656 | 96.6163 | 96.6433 | 97.0374 | 96.9779 | 96.6374 | 92.4438 | 95.9014 | 96.6012 | 97.0486 | 97.2916 | 97.2167 | 96.8905 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL10K-P2US {240V} | Y | Y | N | N | N | N | Y* |  | 10.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.0109 | 240 | 96 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.12 |  |  | 135 | 380 | 480 | 1.0011 | 2.0022 | 3.0033 | 5.0055 | 7.5082 | 10.0109 | 92.0512 | 94.9782 | 94.9328 | 95.3714 | 95.3991 | 94.9543 | 95.1601 | 93.0994 | 96.2304 | 96.2761 | 96.8719 | 97.0247 | 96.9062 | 96.7001 | 93.6663 | 96.3246 | 96.5808 | 97.0256 | 97.1253 | 97.0288 | 96.8558 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL10K-P2US-S {240V} | Y | Y | N | N | N | N | Y* |  | 10.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.0109 | 240 | 96 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.12 |  |  | 135 | 380 | 480 | 1.0011 | 2.0022 | 3.0033 | 5.0055 | 7.5082 | 10.0109 | 92.0512 | 94.9782 | 94.9328 | 95.3714 | 95.3991 | 94.9543 | 95.1601 | 93.0994 | 96.2304 | 96.2761 | 96.8719 | 97.0247 | 96.9062 | 96.7001 | 93.6663 | 96.3246 | 96.5808 | 97.0256 | 97.1253 | 97.0288 | 96.8558 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL12K-P2US {240V} | Y | Y | N | N | N | N | Y* |  | 12.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.0145 | 240 | 96.5 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.39 |  |  | 161 | 380 | 480 | 1.2014 | 2.4029 | 3.6043 | 6.0072 | 9.0109 | 12.0145 | 93.1006 | 95.228 | 95.5523 | 95.8393 | 95.6025 | 95.1408 | 95.5043 | 94.3433 | 96.5994 | 96.675 | 97.0511 | 96.9701 | 96.7737 | 96.8183 | 95.2452 | 96.8669 | 96.9412 | 97.2998 | 97.1893 | 96.9458 | 97.0767 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL12K-P2US-S {240V} | Y | Y | N | N | N | N | Y* |  | 12.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.0145 | 240 | 96.5 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.39 |  |  | 161 | 380 | 480 | 1.2014 | 2.4029 | 3.6043 | 6.0072 | 9.0109 | 12.0145 | 93.1006 | 95.228 | 95.5523 | 95.8393 | 95.6025 | 95.1408 | 95.5043 | 94.3433 | 96.5994 | 96.675 | 97.0511 | 96.9701 | 96.7737 | 96.8183 | 95.2452 | 96.8669 | 96.9412 | 97.2998 | 97.1893 | 96.9458 | 97.0767 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL15K-P2US {240V} | Y | Y | N | N | N | N | Y* |  | 15.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 15.0148 | 240 | 96.5 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.08 |  |  | 202 | 380 | 480 | 1.5015 | 3.003 | 4.5045 | 7.5074 | 11.2611 | 15.0148 | 94.5483 | 95.5289 | 96.0138 | 96.1843 | 95.8054 | 95.25 | 95.8181 | 95.5893 | 96.5176 | 96.9793 | 97.101 | 96.8732 | 96.5137 | 96.8467 | 96.0793 | 96.8399 | 97.2558 | 97.3226 | 96.9795 | 96.6351 | 97.0245 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL15K-P2US-S {240V} | Y | Y | N | N | N | N | Y* |  | 15.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 15.0148 | 240 | 96.5 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.08 |  |  | 202 | 380 | 480 | 1.5015 | 3.003 | 4.5045 | 7.5074 | 11.2611 | 15.0148 | 94.5483 | 95.5289 | 96.0138 | 96.1843 | 95.8054 | 95.25 | 95.8181 | 95.5893 | 96.5176 | 96.9793 | 97.101 | 96.8732 | 96.5137 | 96.8467 | 96.0793 | 96.8399 | 97.2558 | 97.3226 | 96.9795 | 96.6351 | 97.0245 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Siemens Industry, Inc. | blueplanet125 TL3 GEN2 M1 WM OD USP0 {600V} | N | Y | Y | Y | Y | Y | N | N | 137 kVA, 600 Vac Grid Support Utility Interactive Inverter | 136.47 | 600 | 99 | Bureau Veritas | [9/10/2024] | Bureau Veritas | [9/10/2024] | [V4.05 (D6B4)] | 2025-03-21 | [11/19/2024] | 2025-03-21 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.27 |  |  | 875 | 1000 | 1300 | 13.647 | 27.294 | 40.941 | 68.235 | 102.353 | 136.47 | 98.9 | 99.12 | 99.15 | 99.08 | 98.97 | 98.84 | 99.01 | 98.66 | 98.95 | 99 | 98.96 | 98.81 | 98.62 | 98.86 | 98 | 98.46 | 98.61 | 98.67 | 98.56 | 98.39 | 98.55 | 2025-03-21 | 2025-10-01
Siemens Industry, Inc. | blueplanet125 TL3 GEN2 M1 WM OD USPX {600V} | N | Y | Y | Y | Y | Y | N | N | 137 kVA, 600 Vac Grid Support Utility Interactive Inverter | 136.47 | 600 | 99 | Bureau Veritas | [9/10/2024] | Bureau Veritas | [9/10/2024] | [V4.05 (D6B4)] | 2025-03-21 | [11/19/2024] | 2025-03-21 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.27 |  |  | 875 | 1000 | 1300 | 13.647 | 27.294 | 40.941 | 68.235 | 102.353 | 136.47 | 98.9 | 99.12 | 99.15 | 99.08 | 98.97 | 98.84 | 99.01 | 98.66 | 98.95 | 99 | 98.96 | 98.81 | 98.62 | 98.86 | 98 | 98.46 | 98.61 | 98.67 | 98.56 | 98.39 | 98.55 | 2025-03-21 | 2025-10-01
Siemens Industry, Inc. | blueplanet155 TL3 GEN2 M1 WM OD USP0 {600V} | N | Y | Y | Y | Y | Y | N | N | 155 kVA, 600 Vac, Grid Support Utility Interactive Inverter | 155.9168 | 600 | 98.5 | Bureau Veritas Consumer Products Services | [9/10/2024] | Bureau Veritas Consumer Products Services | [9/10/2024] | [V4.05] | 2025-06-02 | [9/10/2024] | 2025-06-02 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.27 |  |  | 875 | 1000 | 1300 | 15.5917 | 31.1834 | 46.7751 | 77.9584 | 116.9376 | 155.9168 | 99.126 | 98.366 | 98.472 | 98.172 | 97.978 | 98.112 | 98.15 | 98.426 | 98.77 | 98.826 | 98.634 | 98.804 | 98.622 | 98.745 | 97.448 | 98.146 | 98.056 | 98.576 | 98.252 | 98.834 | 98.2882 | 2025-06-02
Siemens Industry, Inc. | blueplanet155 TL3 GEN2 M1 WM OD USPX {600V} | N | Y | Y | Y | Y | Y | N | N | 155 kVA, 600 Vac, Grid Support Utility Interactive Inverter | 155.9168 | 600 | 98.5 | Bureau Veritas Consumer Products Services | [9/10/2024] | Bureau Veritas Consumer Products Services | [9/10/2024] | [V4.05] | 2025-06-02 | [9/10/2024] | 2025-06-02 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.27 |  |  | 875 | 1000 | 1300 | 15.5917 | 31.1834 | 46.7751 | 77.9584 | 116.9376 | 155.9168 | 99.126 | 98.366 | 98.472 | 98.172 | 97.978 | 98.112 | 98.15 | 98.426 | 98.77 | 98.826 | 98.634 | 98.804 | 98.622 | 98.745 | 97.448 | 98.146 | 98.056 | 98.576 | 98.252 | 98.834 | 98.2882 | 2025-06-02
Sigenergy Technology Co., Ltd. | SigenMicro 384 US {240V} | N | Y | N | N | N | N | Y* |  | 0.38 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality. | 0.38806 | 240 | 97 | CSA Group | [7/15/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-08 |  |  | N | Y | 0.04 |  |  | 35 | 45 | 55 | 0.038806 | 0.077612 | 0.11642 | 0.19403 | 0.29104 | 0.38806 | 84.261 | 94.2434 | 96.115 | 97.6719 | 97.7826 | 97.581 | 96.8313 | 84.3941 | 94.0845 | 96.3188 | 97.5851 | 97.7258 | 97.452 | 96.7984 | 86.3738 | 94.7113 | 96.3736 | 97.4487 | 97.7316 | 97.2789 | 96.8813 | 2025-10-13 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
Sigenergy Technology Co., Ltd. | SigenMicro 480 US {240V} | N | Y | N | N | N | N | Y* |  | 0.48 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality. | 0.484 | 240 | 97 | CSA Group | [7/15/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-08 |  |  | N | Y | 0.04 |  |  | 35 | 45 | 55 | 0.0484 | 0.0968 | 0.1452 | 0.242 | 0.363 | 0.484 | 85.6306 | 95.0507 | 95.581 | 97.4309 | 97.5757 | 96.8325 | 96.6647 | 86.0291 | 95.5481 | 95.8314 | 97.7395 | 97.6126 | 97.3723 | 96.8469 | 86.8387 | 95.8774 | 96.1474 | 97.6553 | 97.3246 | 97.8547 | 96.7875 | 2025-10-13 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
Sigenergy Technology Co., Ltd. | SigenMicro 768 US {240V} | N | Y | N | N | N | N | Y* |  | 0.77 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality. | 0.776 | 240 | 97 | CSA Group | [7/15/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-08 |  |  | N | Y | 0.04 |  |  | 35 | 45 | 55 | 0.0776 | 0.1552 | 0.2328 | 0.388 | 0.582 | 0.776 | 88.8439 | 94.4397 | 96.5929 | 97.115 | 97.193 | 93.4844 | 96.4475 | 87.5585 | 93.8388 | 96.2123 | 97.8197 | 97.391 | 96.7566 | 96.7369 | 86.2933 | 94.4775 | 97.0153 | 97.5754 | 97.8829 | 97.6832 | 97.0704 | 2025-10-13 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
Sigenergy Technology Co., Ltd. | SigenMicro 960 US {240V} | N | Y | N | N | N | N | Y* |  | 0.96 kW, 240 Vac Grid Support Utility Interactive Microinverter with PCS functionality. | 0.969 | 240 | 97 | CSA Group | [7/15/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-08 |  |  | N | Y | 0.04 |  |  | 35 | 45 | 55 | 0.0969 | 0.1938 | 0.2907 | 0.4845 | 0.72675 | 0.969 | 91 | 95.3846 | 96.9072 | 97.7197 | 96.5186 | 92.7448 | 96.3513 | 90.099 | 94.9223 | 96.9072 | 97.7315 | 97.422 | 96.1524 | 96.9438 | 88.3495 | 93.9394 | 96.5753 | 97.6553 | 97.8112 | 97.6697 | 97.051 | 2025-10-13 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
Sigenergy Technology Co., Ltd. | SigenStor EC 4.8 SP US {240V} | Y | Y | N | N | N | N | Y* | Y | 4.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.808 | 240 | 97 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 | 2025-08-21 |  | N | N | 3.3 |  |  | 270 | 360 | 480 | 0.481 | 0.962 | 1.442 | 2.404 | 3.606 | 4.808 | 93.93 | 96.05 | 96.64 | 96.96 | 97.03 | 96.96 | 96.79 | 95.12 | 96.82 | 97.3 | 97.54 | 97.54 | 97.41 | 97.37 | 93.95 | 96.02 | 96.71 | 97.11 | 97.2 | 97.14 | 96.93 | 2025-08-21
Sigenergy Technology Co., Ltd. | SigenStor EC 5.7 SP US {240V} | Y | Y | N | N | N | N | Y* | Y | 5.7 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.776 | 240 | 97 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 | 2025-08-21 |  | N | N | 3.3 |  |  | 270 | 360 | 480 | 0.578 | 1.155 | 1.733 | 2.888 | 4.332 | 5.776 | 94.61 | 96.34 | 96.8 | 97 | 97 | 96.89 | 96.84 | 95.59 | 97.05 | 97.42 | 97.55 | 97.46 | 97.32 | 97.37 | 94.49 | 96.33 | 96.88 | 97.16 | 97.16 | 97.05 | 96.97 | 2025-08-21
Sigenergy Technology Co., Ltd. | SigenStor EC 7.6 SP US {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.649 | 240 | 97 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 | 2025-08-21 |  | N | N | 3.3 |  |  | 270 | 360 | 480 | 0.765 | 1.53 | 2.295 | 3.824 | 5.737 | 7.649 | 95.46 | 96.7 | 96.9 | 97.03 | 96.89 | 96.69 | 96.84 | 96.37 | 97.33 | 97.52 | 97.51 | 97.32 | 97.2 | 97.34 | 95.42 | 96.76 | 97.07 | 97.18 | 97.04 | 96.87 | 96.98 | 2025-08-21
Sigenergy Technology Co., Ltd. | SigenStor EC 9.6 SP US {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.6533 | 240 | 97 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 | 2025-08-21 |  | N | N | 3.3 |  |  | 270 | 360 | 480 | 0.96533 | 1.9307 | 2.896 | 4.8266 | 7.24 | 9.6533 | 95.9936 | 96.8717 | 96.9858 | 96.9572 | 96.7235 | 96.46 | 96.7691 | 96.7865 | 97.4783 | 97.5478 | 97.3936 | 97.2278 | 97.1 | 97.2895 | 95.9591 | 96.975 | 97.1574 | 97.1165 | 96.9118 | 96.779 | 96.9427 | 2025-08-21
Sigenergy Technology Co., Ltd. | SigenStor EC SP US {240V} | Y | Y | N | N | N | N | Y* | Y | 11.5 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.503 | 240 | 97 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 | 2025-08-21 |  | N | N | 9.6 |  |  | 270 | 360 | 480 | 1.15 | 2.301 | 3.451 | 5.751 | 8.627 | 11.503 | 96.17 | 96.91 | 97.12 | 97.07 | 96.82 | 96.49 | 96.87 | 96.87 | 97.5 | 97.61 | 97.53 | 97.18 | 97.13 | 97.31 | 96.14 | 97.06 | 97.2 | 97.18 | 97 | 96.69 | 97.02 | 2025-08-21 | 2025-10-01
Sigenergy Technology Co., Ltd. | SigenStor EC SP US {208V} | Y | Y | N | N | N | N | Y* |  | 11.5 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.504 | 208 | 96.5 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 |  |  | N | N | 10.2 |  |  | 270 | 360 | 480 | 1.15 | 2.301 | 3.451 | 5.752 | 8.628 | 11.504 | 95.63 | 96.31 | 96.52 | 96.48 | 96.21 | 94.78 | 96.21 | 96.26 | 96.92 | 97.03 | 96.93 | 96.62 | 94.8 | 96.64 | 95.58 | 96.5 | 96.7 | 96.63 | 96.36 | 94.54 | 96.34 | 2026-09-01 |  | Y | N | N | N | N | N | Y | N | N
SimpliPhi Power | SPHI-IN-6 {120V} | Y | N | Y | Y | Y | N | N | N | 6 kW, 120 Vac Split Phase, Transformerless Grid Support Utility Interactive Inverter | 6.0177 | 120 | 93.5 | No Information Submitted | No Information Submitted | Intertek | [8/24/2023] | [V01.14] | 2023-11-13 | [7/13/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 43 |  |  | 250 | 370 | 500 | 0.60177 | 1.2035 | 1.8053 | 3.0088 | 4.5133 | 6.0177 | 84.5 | 90.4 | 92.4 | 93.9 | 94.5 | 94.4 | 93.5 | 83.8 | 90.3 | 92.5 | 94.1 | 94.9 | 94.9 | 93.7 | 80.8 | 88.9 | 91 | 93.4 | 94.1 | 94.3 | 92.8 | 2023-11-13
SMA America | SB3.0-1SP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 3.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 3 | 208 | 96 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.36 |  |  | 155 | 365 | 480 | 0.3032 | 0.6064 | 0.9096 | 1.516 | 2.274 | 3.032 | 92.0828 | 94.9078 | 95.6295 | 95.9916 | 95.9966 | 95.7315 | 95.7273 | 92.071 | 95.6597 | 96.4583 | 97.0435 | 97.2021 | 97.084 | 96.7913 | 88.5154 | 94.503 | 95.7227 | 96.4246 | 96.7724 | 96.6443 | 96.1233 | 2018-08-01 | 2019-02-15
SMA America | SB3.0-1SP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 3.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.39 |  |  | 155 | 365 | 480 | 0.30403 | 0.60805 | 0.91208 | 1.5201 | 2.2802 | 3.0403 | 90.9512 | 94.442 | 95.3831 | 95.9418 | 96.0378 | 95.9409 | 95.651 | 92.0355 | 95.7848 | 96.6411 | 97.1637 | 97.5164 | 97.5821 | 97.0347 | 88.5098 | 94.4385 | 95.7364 | 96.6779 | 97.025 | 97.0008 | 96.3263 | 2018-08-01 | 2019-02-15
SMA America | SB3.0-1SP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 3 | 208 | 96 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.36 |  |  | 155 | 365 | 480 | 0.30276 | 0.60552 | 0.90828 | 1.5138 | 2.2707 | 3.0276 | 92.0828 | 94.9078 | 95.6295 | 95.9916 | 95.9966 | 95.7315 | 95.7273 | 92.071 | 95.6597 | 96.4583 | 97.0435 | 97.2021 | 97.084 | 96.7913 | 88.5154 | 94.503 | 95.7227 | 96.4246 | 96.7724 | 96.6443 | 96.1233 | 2019-05-01 | 2020-01-21
SMA America | SB3.0-1SP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.39 |  |  | 155 | 365 | 480 | 0.30362 | 0.60724 | 0.91086 | 1.5181 | 2.2771 | 3.0362 | 90.952 | 94.442 | 95.38 | 95.94 | 96.038 | 95.94 | 95.6503 | 92.036 | 95.788 | 96.642 | 97.166 | 97.516 | 97.58 | 97.0352 | 88.51 | 94.438 | 95.738 | 96.678 | 97.024 | 97 | 96.326 | 2019-05-01 | 2020-01-21
SMA America | SB3.0-1TP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 3.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 3 | 208 | 96 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.36 |  |  | 155 | 365 | 480 | 0.3032 | 0.6064 | 0.9096 | 1.516 | 2.274 | 3.032 | 92.0828 | 94.9078 | 95.6295 | 95.9916 | 95.9966 | 95.7315 | 95.7273 | 92.071 | 95.6597 | 96.4583 | 97.0435 | 97.2021 | 97.084 | 96.7913 | 88.5154 | 94.503 | 95.7227 | 96.4246 | 96.7724 | 96.6443 | 96.1233 | 2018-08-01 | 2019-02-15
SMA America | SB3.0-1TP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 3.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.39 |  |  | 155 | 365 | 480 | 0.30403 | 0.60805 | 0.91208 | 1.5201 | 2.2802 | 3.0403 | 90.9512 | 94.442 | 95.3831 | 95.9418 | 96.0378 | 95.9409 | 95.651 | 92.0355 | 95.7848 | 96.6411 | 97.1637 | 97.5164 | 97.5821 | 97.0347 | 88.5098 | 94.4385 | 95.7364 | 96.6779 | 97.025 | 97.0008 | 96.3263 | 2018-08-01 | 2019-02-15
SMA America | SB3.0-1TP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 3 | 208 | 96 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-11-15 | [03/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.36 |  |  | 155 | 365 | 480 | 0.303 | 0.606 | 0.908 | 1.514 | 2.271 | 3.028 | 92.08 | 94.91 | 95.63 | 95.99 | 96 | 95.73 | 95.73 | 92.07 | 95.66 | 96.46 | 97.04 | 97.2 | 97.08 | 96.79 | 88.52 | 94.5 | 95.72 | 96.42 | 96.77 | 96.64 | 96.12 | 2019-11-15 | 2020-01-13
SMA America | SB3.0-1TP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-11-15 | [03/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.39 |  |  | 155 | 365 | 480 | 0.304 | 0.607 | 0.911 | 1.518 | 2.277 | 3.036 | 90.95 | 94.44 | 95.38 | 95.94 | 96.04 | 95.94 | 95.65 | 92.04 | 95.79 | 96.64 | 97.17 | 97.52 | 97.58 | 97.04 | 88.51 | 94.44 | 95.74 | 96.68 | 97.02 | 97 | 96.33 | 2019-11-15 | 2020-01-13
SMA America | SBSE3.8-US-50 {208V} | Y | Y | N | N | N | N | Y* | Y | 3.8 kW, 208 Vac Grid Support Utility Interactive Inverters | 3.332 | 208 | 97 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.27 |  |  | 91 | 377 | 480 | 0.3332 | 0.6664 | 0.99961 | 1.666 | 2.499 | 3.332 | 91.9689 | 95.4371 | 95.015 | 95.362 | 95.1386 | 94.7227 | 95.038 | 90.7699 | 95.5679 | 96.3617 | 97.5224 | 97.7374 | 97.606 | 97.1334 | 93.4654 | 96.7253 | 97.4773 | 99.8451 | 98.089 | 97.991 | 98.1264 | 2024-04-02
SMA America | SB3.8-1SP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 3.8 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 3.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.36 |  |  | 195 | 365 | 480 | 0.36045 | 0.72091 | 1.0814 | 1.8023 | 2.7034 | 3.6045 | 92.9308 | 95.4761 | 96.03 | 96.4729 | 96.3788 | 96.1527 | 96.1623 | 92.5315 | 95.951 | 96.6213 | 97.0596 | 97.2247 | 96.9787 | 96.8539 | 89.8079 | 94.9193 | 95.9971 | 96.5769 | 96.77 | 96.8496 | 96.2697 | 2018-08-01 | 2019-02-15
SMA America | SB3.8-1TP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 3.8 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 3.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.36 |  |  | 195 | 365 | 480 | 0.36045 | 0.72091 | 1.0814 | 1.8023 | 2.7034 | 3.6045 | 92.9308 | 95.4761 | 96.03 | 96.4729 | 96.3788 | 96.1527 | 96.1623 | 92.5315 | 95.951 | 96.6213 | 97.0596 | 97.2247 | 96.9787 | 96.8539 | 89.8079 | 94.9193 | 95.9971 | 96.5769 | 96.77 | 96.8496 | 96.2697 | 2018-08-01 | 2019-02-15
SMA America | SB3.8-1SP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 208 Vac Grid Support Utility Interactive Inverter | 3.604 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.36 |  |  | 195 | 365 | 480 | 0.36039 | 0.72079 | 1.0812 | 1.802 | 2.7029 | 3.6039 | 92.9308 | 95.4761 | 96.03 | 96.4729 | 96.3788 | 96.1527 | 96.1623 | 92.5315 | 95.951 | 96.6213 | 97.0596 | 97.2247 | 96.9787 | 96.8539 | 89.8079 | 94.9193 | 95.9971 | 96.5769 | 96.77 | 96.8496 | 96.2697 | 2019-05-01 | 2020-01-21
SMA America | SB3.8-1TP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 208 Vac Grid Support Utility Interactive Inverter | 3.604 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-11-15 | [03/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.36 |  |  | 195 | 365 | 480 | 0.36 | 0.721 | 1.081 | 1.802 | 2.703 | 3.604 | 92.93 | 95.48 | 96.03 | 96.47 | 96.38 | 96.15 | 96.16 | 92.53 | 95.95 | 96.62 | 97.06 | 97.22 | 96.98 | 96.85 | 89.81 | 96.92 | 96 | 96.58 | 96.77 | 96.85 | 96.27 | 2019-11-15 | 2020-01-13
SMA America | SB3.8-1SP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 3.8 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 3.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.39 |  |  | 195 | 365 | 480 | 0.38543 | 0.77085 | 1.1563 | 1.9271 | 2.8907 | 3.8543 | 92.6814 | 95.3701 | 96.0702 | 96.4553 | 96.4439 | 96.2328 | 96.1867 | 93.6802 | 96.4354 | 96.8953 | 97.4346 | 97.5877 | 97.468 | 97.2525 | 90.8056 | 95.3096 | 96.4049 | 96.9099 | 97.1557 | 97.3074 | 96.6753 | 2018-08-01 | 2019-02-15
SMA America | SB3.8-1TP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 3.8 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 3.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.39 |  |  | 195 | 365 | 480 | 0.38543 | 0.77085 | 1.1563 | 1.9271 | 2.8907 | 3.8543 | 92.6814 | 95.3701 | 96.0702 | 96.4553 | 96.4439 | 96.2328 | 96.1867 | 93.6802 | 96.4354 | 96.8953 | 97.4346 | 97.5877 | 97.468 | 97.2525 | 90.8056 | 95.3096 | 96.4049 | 96.9099 | 97.1557 | 97.3074 | 96.6753 | 2018-08-01 | 2019-02-15
SMA America | SB3.8-1SP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 3.84 | 240 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.39 |  |  | 195 | 365 | 480 | 0.38532 | 0.77064 | 1.156 | 1.9266 | 2.8899 | 3.8532 | 92.6814 | 95.3701 | 96.0702 | 96.4553 | 96.4439 | 96.2328 | 96.1867 | 93.6802 | 96.4354 | 96.8953 | 97.4346 | 97.5877 | 97.468 | 97.2525 | 90.8056 | 95.3096 | 96.4049 | 96.9099 | 97.1557 | 97.3074 | 96.6753 | 2019-05-01 | 2020-01-21
SMA America | SB3.8-1TP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 3.84 | 240 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-11-15 | [03/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.39 |  |  | 195 | 365 | 480 | 0.385 | 0.771 | 1.156 | 1.927 | 2.89 | 3.853 | 92.68 | 95.37 | 96.07 | 96.46 | 96.44 | 96.23 | 96.19 | 93.68 | 96.44 | 96.9 | 97.43 | 97.59 | 97.47 | 97.25 | 90.81 | 95.31 | 96.4 | 96.91 | 97.16 | 97.31 | 96.68 | 2019-11-15 | 2020-01-13
SMA America | SBSE3.8-US-50 {240V} | Y | Y | N | N | N | N | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverters | 3.8699 | 240 | 96.5 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.22 |  |  | 91 | 377 | 480 | 0.38699 | 0.77399 | 1.161 | 1.935 | 2.9025 | 3.8699 | 93.0814 | 95.6956 | 95.2874 | 95.4254 | 95.1957 | 94.6509 | 95.1681 | 92.0493 | 95.9549 | 96.9939 | 97.7121 | 97.9883 | 97.752 | 97.4599 | 92.1616 | 96.1067 | 97.2841 | 97.9366 | 98.0623 | 98.0861 | 97.6099 | 2024-04-02
SMA America | SBSE4.8-US-50 {208V} | Y | Y | N | N | N | N | Y* | Y | 4.8 kW, 208 Vac Grid Support Utility Interactive Inverters | 4.166 | 208 | 97 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.27 |  |  | 112 | 383 | 480 | 0.4166 | 0.8332 | 1.2498 | 2.083 | 3.1245 | 4.166 | 92.7583 | 95.9984 | 96.4304 | 96.0094 | 95.7187 | 95.2343 | 95.7365 | 92.472 | 95.9293 | 97.0746 | 97.5559 | 97.5201 | 97.4297 | 97.1882 | 94.8507 | 97.0524 | 97.8281 | 98.3703 | 98.0199 | 97.8937 | 97.889 | 2024-04-02
SMA America | SBSE4.8-US-50 {240V} | Y | Y | N | N | N | N | Y* | Y | 4.8 kW, 240 Vac Grid Support Utility Interactive Inverters | 4.8229 | 240 | 97 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.22 |  |  | 112 | 383 | 480 | 0.48229 | 0.96458 | 1.4469 | 2.4114 | 3.6172 | 4.8229 | 93.5741 | 96.248 | 96.0843 | 96.094 | 95.8009 | 95.2777 | 95.8036 | 93.1963 | 96.5204 | 97.2174 | 97.9076 | 97.7361 | 97.671 | 97.4643 | 93.8017 | 96.6521 | 97.4959 | 97.9434 | 98.0153 | 97.982 | 97.6995 | 2024-04-02
SMA America | SBSE5.8-US-50 {208V} | Y | Y | N | N | N | N | Y* | Y | 5.8 kW, 208 Vac Grid Support Utility Interactive Inverters | 4.9999 | 208 | 97 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.27 |  |  | 136 | 389 | 480 | 0.49999 | 0.99998 | 1.5 | 2.5 | 3.7499 | 4.9999 | 93.5256 | 96.2479 | 97.0897 | 96.4304 | 96.1394 | 95.7037 | 96.1937 | 92.791 | 96.6303 | 97.3739 | 97.6607 | 97.4597 | 97.3226 | 97.2565 | 94.8507 | 97.4773 | 98.7461 | 98.1057 | 97.9486 | 97.7884 | 97.9218 | 2024-04-02
SMA America | SB5.0-1SP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 5.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 5 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.06 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 94.7 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.7 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.1 | 96.1 | 96.7 | 96.9 | 97 | 96.8 | 96.6 | 2018-08-01 | 2019-02-15
SMA America | SB5.0-1SP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 5.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 5 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.21 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.79 | 5.05 | 93.3 | 96 | 96.5 | 96.7 | 96.6 | 96.4 | 96.4 | 93.4 | 96.9 | 97.2 | 97.5 | 97.4 | 97.2 | 97.2 | 91.2 | 96.2 | 96.8 | 97.2 | 97.4 | 97.3 | 97 | 2018-08-01 | 2019-02-15
SMA America | SB5.0-1SP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 5 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.06 |  |  | 220 | 365 | 480 | 0.50499 | 1.01 | 1.515 | 2.5249 | 3.7874 | 5.0499 | 94.6943 | 96.3064 | 96.5562 | 96.6291 | 96.4459 | 96.0274 | 96.3997 | 94.7254 | 96.7172 | 97.0771 | 97.2289 | 97.0843 | 96.7747 | 96.9856 | 91.1032 | 96.149 | 96.6625 | 96.912 | 96.9618 | 96.7967 | 96.6322 | 2019-05-01 | 2020-01-21
SMA America | SB5.0-1SP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 5 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.21 |  |  | 220 | 365 | 480 | 0.50586 | 1.0117 | 1.5176 | 2.5293 | 3.794 | 5.0586 | 93.3494 | 96.0308 | 96.4559 | 96.6614 | 96.6099 | 96.3678 | 96.4308 | 93.4405 | 96.8585 | 97.2319 | 97.5098 | 97.4129 | 97.2237 | 97.2154 | 91.21 | 96.1804 | 96.8054 | 97.2068 | 97.3728 | 97.27 | 96.9586 | 2019-05-01 | 2020-01-21
SMA America | SB5.0-1TP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 5.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 5 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.06 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 94.7 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.7 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.1 | 96.1 | 96.7 | 96.9 | 97 | 96.8 | 96.6 | 2018-08-01 | 2019-02-15
SMA America | SB5.0-1TP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 5.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 5 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.21 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.79 | 5.05 | 93.3 | 96 | 96.5 | 96.7 | 96.6 | 96.4 | 96.4 | 93.4 | 96.9 | 97.2 | 97.5 | 97.4 | 97.2 | 97.2 | 91.2 | 96.2 | 96.8 | 97.2 | 97.4 | 97.3 | 97 | 2018-08-01 | 2019-02-15
SMA America | SB5.0-1TP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 5 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [3/13/2019] | [V2.04.15.R] | 2019-12-02 | [3/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.06 |  |  | 220 | 365 | 480 | 0.50499 | 1.01 | 1.515 | 2.5249 | 3.7874 | 5.0499 | 94.6943 | 96.3064 | 96.5562 | 96.6291 | 96.4459 | 96.0274 | 96.3997 | 94.7254 | 96.7172 | 97.0771 | 97.2289 | 97.0843 | 96.7747 | 96.9856 | 91.1032 | 96.149 | 96.6625 | 96.912 | 96.9618 | 96.7967 | 96.6322 | 2019-12-02 | 2020-01-13
SMA America | SB5.0-1TP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 5 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [3/13/2019] | [V2.04.15.R] | 2019-12-02 | [3/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.21 |  |  | 220 | 365 | 480 | 0.50586 | 1.0117 | 1.5176 | 2.5293 | 3.794 | 5.0586 | 93.3494 | 96.0308 | 96.4559 | 96.6614 | 96.6099 | 96.3678 | 96.4308 | 93.4405 | 96.8585 | 97.2319 | 97.5098 | 97.4129 | 97.2237 | 97.2154 | 91.21 | 96.1804 | 96.8054 | 97.2068 | 97.3728 | 97.27 | 96.9586 | 2019-12-02 | 2020-01-13
SMA America | SB6.0-1SP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.418 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.06 |  |  | 220 | 365 | 480 | 0.54177 | 1.0835 | 1.6253 | 2.7088 | 4.0633 | 5.4177 | 94.8098 | 96.3223 | 96.5669 | 96.627 | 96.4299 | 95.9837 | 96.3952 | 94.8499 | 96.7381 | 97.0781 | 97.2314 | 97.0698 | 96.7747 | 96.9846 | 91.7463 | 96.1806 | 96.6775 | 96.8453 | 96.9618 | 96.786 | 96.6468 | 2019-05-01 | 2020-01-21
SMA America | SB6.0-1TP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.418 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [3/13/2019] | [V2.04.15.R] | 2019-12-02 | [3/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.06 |  |  | 220 | 365 | 480 | 0.54177 | 1.0835 | 1.6253 | 2.7088 | 4.0633 | 5.4177 | 94.8098 | 96.3223 | 96.5669 | 96.627 | 96.4299 | 95.9837 | 96.3952 | 94.8499 | 96.7381 | 97.0781 | 97.2314 | 97.0698 | 96.7747 | 96.9846 | 91.7463 | 96.1806 | 96.6775 | 96.8453 | 96.9618 | 96.786 | 96.6468 | 2019-12-02 | 2020-01-13
SMA America | SB6.0-1SP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 6.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 5.49 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.06 |  |  | 220 | 365 | 480 | 0.55 | 1.1 | 1.65 | 2.75 | 4.12 | 5.49 | 94.8 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.8 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.7 | 96.2 | 96.7 | 96.8 | 97 | 96.8 | 96.6 | 2018-08-01 | 2019-02-15
SMA America | SB6.0-1TP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 6.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 5.49 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.06 |  |  | 220 | 365 | 480 | 0.55 | 1.1 | 1.65 | 2.75 | 4.12 | 5.49 | 94.8 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.8 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.7 | 96.2 | 96.7 | 96.8 | 97 | 96.8 | 96.6 | 2018-08-01 | 2019-02-15
SMA America | SBSE5.8-US-50 {240V} | Y | Y | N | N | N | N | Y* | Y | 5.8 kW, 240 Vac Grid Support Utility Interactive Inverters | 5.7759 | 240 | 97.5 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.22 |  |  | 136 | 389 | 480 | 0.57759 | 1.1552 | 1.7328 | 2.8879 | 4.3319 | 5.7759 | 94.5499 | 96.8326 | 97.173 | 96.576 | 96.2533 | 95.7726 | 96.3682 | 94.4396 | 96.989 | 97.5907 | 97.7376 | 97.6853 | 97.5726 | 97.5146 | 94.7989 | 97.2841 | 97.8769 | 98.0724 | 98.0767 | 97.9079 | 97.8726 | 2024-04-02
SMA America | SB6.0-1SP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 6.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 6 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.21 |  |  | 220 | 365 | 480 | 0.61 | 1.21 | 1.82 | 3.03 | 4.54 | 6.05 | 94.7 | 96.3 | 96.6 | 96.6 | 96.5 | 96.1 | 96.4 | 95.4 | 97.1 | 97.4 | 97.6 | 97.3 | 97 | 97.3 | 93.4 | 96.5 | 97 | 97.3 | 97.3 | 97 | 97.1 | 2018-08-01 | 2019-02-15
SMA America | SB6.0-1SP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 6 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.21 |  |  | 220 | 365 | 480 | 0.60518 | 1.2104 | 1.8155 | 3.0259 | 4.5389 | 6.0518 | 94.6792 | 96.3065 | 96.6157 | 96.6489 | 96.481 | 96.137 | 96.4344 | 95.4374 | 97.1021 | 97.3736 | 97.5643 | 97.3124 | 97.0135 | 97.2722 | 93.3743 | 96.5451 | 97.0147 | 97.3236 | 97.2821 | 97.0129 | 97.0521 | 2019-05-01 | 2020-01-21
SMA America | SB6.0-1TP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 6.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 6 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.21 |  |  | 220 | 365 | 480 | 0.61 | 1.21 | 1.82 | 3.03 | 4.54 | 6.05 | 94.7 | 96.3 | 96.6 | 96.6 | 96.5 | 96.1 | 96.4 | 95.4 | 97.1 | 97.4 | 97.6 | 97.3 | 97 | 97.3 | 93.4 | 96.5 | 97 | 97.3 | 97.3 | 97 | 97.1 | 2018-08-01 | 2019-02-15
SMA America | SB6.0-1TP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 6 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [3/13/2019] | [V2.04.15.R] | 2019-12-02 | [3/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.21 |  |  | 220 | 365 | 480 | 0.60518 | 1.2104 | 1.8155 | 3.0259 | 4.5389 | 6.0518 | 94.6792 | 96.3065 | 96.6157 | 96.6489 | 96.481 | 96.137 | 96.4344 | 95.4374 | 97.1021 | 97.3736 | 97.5643 | 97.3124 | 97.0135 | 97.2722 | 93.3743 | 96.5451 | 97.0147 | 97.3236 | 97.2821 | 97.0129 | 97.0521 | 2019-12-02 | 2020-01-13
SMA America | SBSE7.7-US-50 {208V} | Y | Y | N | N | N | N | Y* | Y | 7.7 kW, 208 Vac Grid Support Utility Interactive Inverters | 6.6445 | 208 | 97 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.27 |  |  | 180 | 400 | 480 | 0.66445 | 1.3289 | 1.9933 | 3.3222 | 4.9834 | 6.6445 | 94.2736 | 96.912 | 97.2224 | 96.8823 | 96.4626 | 96.0167 | 96.5545 | 94.4081 | 97.1816 | 97.5354 | 97.4703 | 97.3359 | 97.076 | 97.2502 | 96.3053 | 97.9159 | 98.3666 | 98.0074 | 97.8107 | 97.5284 | 97.8497 | 2024-04-02
SMA America | SB7.0-1SP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 7.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 6.92 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.37 |  |  | 245 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 96.2382 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2018-08-01 | 2019-02-15
SMA America | SB7.0-1TP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 7.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 6.92 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.37 |  |  | 245 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 96.2382 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2018-08-01 | 2019-02-15
SMA America | SB7.7-1SP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 7.7 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 6.92 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.37 |  |  | 270 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 96.2354 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2018-08-01 | 2019-02-15
SMA America | SB7.7-1TP-US-40 {208V} | N | N | Y | Y | Y | N | N | N | 7.7 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 6.92 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.37 |  |  | 270 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 96.2354 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2018-08-01 | 2019-02-15
SMA America | SB7.0-1SP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 7.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.923 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.37 |  |  | 245 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 96.2382 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2019-05-01 | 2020-01-21
SMA America | SB7.0-1TP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 7.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.923 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [3/13/2019] | [V2.04.15.R] | 2019-12-02 | [3/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.37 |  |  | 245 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 96.2382 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2019-12-11 | 2020-01-13
SMA America | SB7.7-1SP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 7.7 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.923 | 208 | 96.5 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.37 |  |  | 270 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 96.2354 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2019-05-01 | 2020-01-21
SMA America | SB7.7-1TP-US-41 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 7.7 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.923 | 208 | 96.54 | No Information Submitted | No Information Submitted | UL | [3/13/2019] | [V2.04.15.R] | 2019-12-02 | [3/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.37 |  |  | 270 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 96.2354 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | 2019-12-11 | 2020-01-13
SMA America | SB7.0-1SP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 7.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 7 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.1 |  |  | 245 | 365 | 480 | 0.70973 | 1.4195 | 2.1292 | 3.5486 | 5.323 | 7.0973 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 96.5016 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 97.0775 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677 | 96.8607 | 2018-08-01 | 2019-02-15
SMA America | SB7.0-1SP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 7.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 7 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.1 |  |  | 245 | 365 | 480 | 0.70094 | 1.4019 | 2.1028 | 3.5047 | 5.257 | 7.0094 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 96.5016 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 97.0775 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677 | 96.8607 | 2019-05-01 | 2020-01-21
SMA America | SB7.0-1TP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 7.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 7 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.1 |  |  | 245 | 365 | 480 | 0.70973 | 1.4195 | 2.1292 | 3.5486 | 5.323 | 7.0973 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 96.5016 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 97.0775 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677 | 96.8607 | 2018-08-01 | 2019-02-15
SMA America | SB7.0-1TP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 7.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 7 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [3/13/2019] | [V2.04.15.R] | 2019-12-02 | [3/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.1 |  |  | 245 | 365 | 480 | 0.70094 | 1.4019 | 2.1028 | 3.5047 | 5.257 | 7.0094 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 96.5016 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 97.0775 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677 | 96.8607 | 2019-12-11 | 2020-01-13
SMA America | SBSE7.7-US-50 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.7 kW, 240 Vac Grid Support Utility Interactive Inverters | 7.622 | 240 | 97.5 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.22 |  |  | 180 | 400 | 480 | 0.7622 | 1.5244 | 2.2866 | 3.811 | 5.7165 | 7.622 | 95.3476 | 96.8667 | 97.3793 | 96.977 | 96.5693 | 96.1249 | 96.6959 | 95.0761 | 97.1689 | 97.5056 | 97.6173 | 97.5144 | 97.2864 | 97.4088 | 95.8559 | 97.6306 | 97.9239 | 98.0164 | 97.9176 | 97.5194 | 97.8224 | 2024-04-02
SMA America | SB7.7-1SP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 7.7 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 7.68 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [2/21/2017] | [02.03.00.R] | 2018-10-15 | [2/21/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.1 |  |  | 270 | 365 | 480 | 0.7758 | 1.5516 | 2.3274 | 3.879 | 5.8185 | 7.758 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.6371 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 96.9614 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284 | 96.862 | 2018-08-01 | 2019-02-15
SMA America | SB7.7-1SP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 7.7 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.68 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [03/13/2019] | [V2.04.15.R] | 2019-05-01 | [03/13/2019] | 2020-01-21 | UL | 2019-12-16 | 2020-01-21 |  | Y | N | 5.1 |  |  | 270 | 365 | 480 | 0.77564 | 1.5513 | 2.3269 | 3.8782 | 5.8173 | 7.7564 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.6371 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 96.9614 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284 | 96.862 | 2019-05-01 | 2020-01-21
SMA America | SB7.7-1TP-US-40 {240V} | N | N | Y | Y | Y | N | N | N | 7.7 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 7.68 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | [06/28/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.1 |  |  | 270 | 365 | 480 | 0.7758 | 1.5516 | 2.3274 | 3.879 | 5.8185 | 7.758 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.6371 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 96.9614 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284 | 96.862 | 2018-08-01 | 2019-02-15
SMA America | SB7.7-1TP-US-41 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 7.7 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.68 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [3/13/2019] | [V2.04.15.R] | 2019-12-02 | [3/13/2019] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | Y | N | 5.1 |  |  | 270 | 365 | 480 | 0.77564 | 1.5513 | 2.3269 | 3.8782 | 5.8173 | 7.7564 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.6371 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 96.9614 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284 | 96.862 | 2019-12-11 | 2020-01-13
SMA America | SBSE9.6-US-50 {208V} | Y | Y | N | N | N | N | Y* | N | 9.6 kW, 208Vac Grid Support Utility Interactive Inverter | 8.338 | 208 | 97 | Intertek | [3/7/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2025-03-19 | No Information Submitted |  | N | N | 11.09 |  |  | 168 | 395 | 480 | 0.834 | 1.668 | 2.501 | 4.169 | 6.253 | 8.338 | 94.37 | 96.75 | 97.07 | 96.78 | 96.43 | 96.14 | 96.5 | 94.42 | 96.64 | 97.24 | 97.24 | 97.13 | 97.01 | 97.03 | 95.41 | 97.46 | 97.84 | 97.77 | 97.62 | 97.42 | 97.57 | 2025-05-01
SMA America | SBSE9.6-US-50 {240V} | Y | Y | N | N | N | N | Y* | N | 9.6 kW, 240Vac Grid Support Utility Interactive Inverter | 9.569 | 240 | 97.5 | Intertek | [3/7/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2025-03-19 | No Information Submitted |  | N | N | 11.02 |  |  | 168 | 395 | 480 | 0.957 | 1.914 | 2.871 | 4.784 | 7.176 | 9.569 | 95 | 97.05 | 97.45 | 96.99 | 96.66 | 96.31 | 96.76 | 94.88 | 97.25 | 97.61 | 97.59 | 97.47 | 97.33 | 97.39 | 95.9 | 97.74 | 97.98 | 98.02 | 97.96 | 97.73 | 97.87 | 2025-05-01
SMA America | SBSE11.5-US-50 {208V} | Y | Y | N | N | N | N | Y* | N | 11.5 kW, 208Vac Grid Support Utility Interactive Inverter | 10.053 | 208 | 97 | Intertek | [3/7/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2025-03-19 | No Information Submitted |  | N | N | 11.04 |  |  | 200 | 405 | 480 | 1.005 | 2.011 | 3.016 | 5.026 | 7.54 | 10.053 | 94.82 | 97.1 | 97.35 | 96.92 | 96.6 | 96.26 | 96.7 | 94.41 | 97.1 | 97.21 | 97.31 | 97.13 | 96.93 | 97.06 | 95.96 | 97.65 | 97.82 | 97.7 | 97.52 | 97.18 | 97.52 | 2025-05-01
SMA America | SBSE11.5-US-50 {240V} | Y | Y | N | N | N | N | Y* | N | 11.5 kW, 240Vac Grid Support Utility Interactive Inverter | 11.483 | 240 | 97.5 | Intertek | [3/7/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2025-03-19 | No Information Submitted |  | N | N | 10.97 |  |  | 200 | 405 | 480 | 1.148 | 2.297 | 3.445 | 5.742 | 8.613 | 11.483 | 95.08 | 97.15 | 97.47 | 97.19 | 96.84 | 96.47 | 96.91 | 95.75 | 97.38 | 97.48 | 97.59 | 97.43 | 97.25 | 97.39 | 96.41 | 97.94 | 98.01 | 97.99 | 97.82 | 97.57 | 97.82 | 2025-05-01
SMA America | STP12000TL-US-10 {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 12 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 12 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 300 | 675 | 800 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 96.4293 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 97.6137 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898 | 97.8803 | 2018-08-01 | 2019-02-15
SMA America | STP 13-US-50 {208V} | N | Y | N | N | N | N | Y* |  | 13 kW, 208 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 13 | 208 | 97 | UL | [8/6/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2025-07-01 |  |  | N | N | 4.3 |  |  | 230 | 335 | 640 | 1.3012 | 2.6023 | 3.9035 | 6.5058 | 9.7587 | 13.0116 | 94.9928 | 96.271 | 96.4268 | 96.432 | 96.1018 | 95.5972 | 96.149 | 96.4814 | 97.1612 | 97.2754 | 97.2926 | 96.9998 | 96.5698 | 97.0602 | 93.4882 | 95.4848 | 95.6694 | 95.9022 | 95.5876 | 95.2486 | 95.5574 | 2025-09-11
SMA America | STP15000TL-US-10 {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 15 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 15 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 300 | 675 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 96.448 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 97.694 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572 | 98.0267 | 2018-08-01 | 2019-02-15
SMA America | STP 20-US-50 {480V} | N | Y | N | N | N | N | Y* | N | 20 kW, 480 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 20 | 480 | 97.5 | UL | [6/12/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-09-06 | No Information Submitted |  | N | N | 4.7 |  |  | 350 | 688 | 800 | 2.01 | 4.02 | 6.03 | 10.05 | 15.075 | 20.099 | 93.18 | 95.64 | 96.24 | 96.93 | 97.04 | 97.05 | 96.69 | 96.09 | 97.68 | 97.73 | 98.24 | 98.2 | 98.19 | 98.04 | 95.47 | 97.31 | 97.84 | 98.14 | 98.34 | 98.27 | 98.07 | 2023-09-01 | 2023-11-01
SMA America | STP20000TL-US-10 {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 20 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 380 | 695 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 96.9173 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 98.0588 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422 | 98.0897 | 2018-08-01 | 2019-02-15
SMA America | STP24000TL-US-10 {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 24 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 24 | 480 | 98 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 450 | 712 | 800 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.1621 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 98.4117 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823 | 98.0569 | 2018-08-01 | 2019-02-15
SMA America | STP 25-US-50 {480V} | N | Y | N | N | N | N | Y* | N | 25 kW, 480 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 25 | 480 | 98 | UL | [6/12/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-09-06 | No Information Submitted |  | N | N | 4.7 |  |  | 430 | 708 | 800 | 2.513 | 5.026 | 7.538 | 12.564 | 18.846 | 25.128 | 94.44 | 96.56 | 97 | 97.37 | 97.42 | 97.41 | 97.2 | 97.06 | 98.45 | 98.55 | 98.54 | 98.47 | 98.38 | 98.44 | 96.03 | 97.56 | 98.02 | 98.33 | 98.28 | 98.18 | 98.13 | 2023-09-01 | 2023-11-01
SMA America | STP 27-US-80 {208V} | N | Y | N | N | N | N | Y* |  | 27.5 kW, 208 Vac Grid Support Utility Interactive Inverter | 26.757 | 208 | 97 | UL | [6/5/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2026-05-06 |  |  | N | N | 18.03 |  |  | 300 | 630 | 800 | 2.676 | 5.351 | 8.027 | 13.379 | 20.068 | 26.757 | 96.77 | 96.68 | 97.23 | 97.59 | 96.93 | 96.59 | 97.07 | 96.88 | 97.08 | 97 | 96.76 | 97.1 | 96.86 | 96.99 | 96.98 | 96.98 | 96.78 | 96.71 | 96.7 | 96.03 | 96.7 | 2026-08-21 |  | Y | N | N | N | N | N | Y | N | No Information Submitted
SMA America | STP 30-US-50 {480V} | N | Y | N | N | N | N | Y* | N | 30 kW, 480 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 30 | 480 | 98 | UL | [6/12/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-09-06 | No Information Submitted |  | N | N | 4.7 |  |  | 515 | 714 | 800 | 3.014 | 6.028 | 9.042 | 15.07 | 22.605 | 30.14 | 96 | 96.97 | 97.34 | 97.7 | 97.67 | 97.49 | 97.52 | 97.39 | 98.1 | 98.46 | 98.54 | 98.46 | 98.3 | 98.41 | 96.49 | 97.85 | 98.1 | 98.34 | 98.24 | 98.06 | 98.14 | 2023-09-01 | 2023-11-01
SMA America | STP30000TL-US-10 {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 30 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 30 | 480 | 98 | No Information Submitted | No Information Submitted | UL | [7/6/2017] | [2.03.04.R] | 2018-10-15 | [7/6/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.22 |  |  | 500 | 720 | 800 | 3.001 | 6.002 | 9.003 | 15.005 | 22.5075 | 30.01 | 96.588 | 97.716 | 97.926 | 97.98 | 97.838 | 97.622 | 97.8115 | 97.588 | 98.448 | 98.69 | 98.602 | 98.538 | 98.328 | 98.5167 | 97.026 | 98.06 | 98.452 | 98.386 | 98.282 | 98.08 | 98.2528 | 2018-08-01 | 2019-02-15
SMA America | STP 33-US-41 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 33.3 kW, 480 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 33.3 | 480 | 97.5 | UL | [11/08/2018] | UL | [11/08/2018] | [01.09.03.R] | 2018-12-17 | [11/08/2018] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | N | N | 5.43 |  |  | 330 | 683 | 800 | 3.33 | 6.66 | 9.99 | 16.65 | 24.975 | 33.3 | 94.259 | 96.337 | 96.705 | 96.644 | 96.46 | 96.003 | 96.411 | 94.707 | 96.755 | 97.303 | 97.647 | 97.694 | 97.719 | 97.472 | 95.731 | 97.626 | 98.044 | 98.229 | 98.119 | 97.988 | 98.0064 | 2018-12-17 | 2022-11-01
SMA America | STP 50-US-41 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 50 | 480 | 97.5 | UL | [11/08/2018] | UL | [11/08/2018] | [01.09.03.R] | 2018-12-17 | [11/08/2018] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | N | N | 5.43 |  |  | 500 | 725 | 800 | 5.0006 | 10.0012 | 15.0018 | 25.003 | 37.5045 | 50.006 | 95.552 | 97.123 | 97.41 | 97.362 | 97.005 | 96.688 | 97.0605 | 96.195 | 97.446 | 97.741 | 97.833 | 97.604 | 97.357 | 97.5919 | 97.062 | 98.074 | 98.229 | 98.119 | 97.965 | 97.765 | 97.9884 | 2018-12-17 | 2022-11-01
SMA America | STP 50-US-80 {480V} | N | Y | N | N | N | N | Y* |  | 50 kW, 480 Vac Grid Support Utility Interactive Inverter | 50 | 480 | 97.5 | UL | [6/5/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2026-05-06 |  |  | N | N | 23.8 |  |  | 500 | 720 | 850 | 5.029 | 10.057 | 15.086 | 25.144 | 37.715 | 50.287 | 94.3 | 96.09 | 96.79 | 97.07 | 97.11 | 97.03 | 96.89 | 95.66 | 97.33 | 97.79 | 97.99 | 97.98 | 97.69 | 97.82 | 95.47 | 97.3 | 97.58 | 97.84 | 97.78 | 97.65 | 97.65 | 2026-08-21 |  | Y | N | N | N | N | N | Y | N | No Information Submitted
SMA America | STP50-US-40 {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower CORE1 50 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 50 | 480 | 98 | No Information Submitted | No Information Submitted | UL | [8/14/2017] | [V1.01.19.R] | 2018-10-15 | [8/14/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.1 |  |  | 500 | 725 | 800 | 5.0072 | 10.0144 | 15.0216 | 25.036 | 37.554 | 50.072 | 94.9771 | 97.1941 | 97.7158 | 97.8318 | 97.5793 | 97.2902 | 97.5109 | 96.4618 | 97.7508 | 98.1301 | 98.2175 | 98.0757 | 97.8645 | 98.0206 | 97.214 | 97.859 | 98.0248 | 97.7868 | 98.1846 | 97.8628 | 98.0107 | 2017-09-01 | 2019-02-15
SMA America | SHP FLEX-US-21 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 55 kW, 208 Vac Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | 55.076 | 208 | 97 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22; 3.16.22] | 2024-11-21 | [11/30/2022] | 2024-11-21 | UL | 2019-12-16 | 2024-11-21 | Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | N | N | 2.8744 |  |  | 372 | 583 | 1195 | 5.508 | 11.015 | 16.523 | 27.538 | 41.307 | 55.076 | 97.44 | 97.51 | 97.57 | 97.38 | 96.85 | 96.4 | 97.08 | 95.77 | 97.23 | 97.4 | 97.27 | 96.73 | 96.25 | 96.88 | 94.84 | 96.38 | 96.75 | 96.8 | 96.4 | 95.94 | 96.44 | 2024-11-21 | 2025-01-02
SMA America | STP 62-US-41 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 62.5 kW, 480 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 62.5 | 480 | 97.5 | UL | [11/08/2018] | UL | [11/08/2018] | [01.09.03.R] | 2018-12-17 | [11/08/2018] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | N | N | 5.43 |  |  | 500 | 725 | 800 | 6.25 | 12.5 | 18.75 | 31.25 | 46.875 | 62.5 | 96.186 | 97.249 | 97.41 | 97.376 | 97.171 | 96.538 | 97.1756 | 96.699 | 97.65 | 97.804 | 97.788 | 97.42 | 97.048 | 97.5074 | 97.377 | 98.172 | 98.225 | 98.063 | 97.819 | 97.457 | 97.9008 | 2018-12-17 | 2022-11-01
SMA America | STP 62-US-80 {480V} | N | Y | N | N | N | N | Y* |  | 62.5 kW, 480 Vac Grid Support Utility Interactive Inverter | 62.5 | 480 | 97.5 | UL | [6/5/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2026-05-06 |  |  | N | N | 23.71 |  |  | 500 | 720 | 850 | 6.258 | 12.516 | 18.774 | 31.29 | 46.936 | 62.581 | 95.01 | 96.33 | 96.78 | 97.03 | 96.97 | 97.74 | 96.89 | 96.09 | 97.64 | 97.92 | 98.04 | 97.9 | 97.82 | 97.84 | 96.2 | 97.46 | 97.81 | 97.87 | 97.71 | 97.54 | 97.67 | 2026-08-21 |  | Y | N | N | N | N | N | Y | N | No Information Submitted
SMA America | STP 70-US-80 {480V} | N | Y | N | N | N | N | Y* |  | 70 kW, 480 Vac Grid Support Utility Interactive Inverter | 70 | 480 | 97.5 | UL | [6/5/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2026-05-06 |  |  | N | N | 23.75 |  |  | 500 | 720 | 850 | 7.047 | 14.093 | 21.14 | 35.233 | 52.85 | 70.466 | 95.33 | 96.58 | 96.79 | 97.12 | 96.92 | 96.65 | 96.85 | 96.24 | 97.94 | 97.94 | 97.98 | 97.88 | 97.58 | 97.83 | 96.38 | 97.56 | 97.85 | 97.83 | 97.61 | 97.37 | 97.62 | 2026-08-21 |  | Y | N | N | N | N | N | Y | N | No Information Submitted
SMA America | SHP FLEX-US-21 {320V} | N | Y | Y | Y | Y | Y | Y* | Y | 84.9 kW, 320 Vac Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | 84.9036 | 320 | 98 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22; 3.16.22] | 2025-03-11 | [11/30/2022] | 2025-03-11 | UL | 2019-12-16 | 2025-03-11 |  | N | N | 2.9752 |  |  | 495 | 680 | 1195 | 8.4904 | 16.9807 | 25.4711 | 42.4518 | 63.6777 | 84.9036 | 98.2876 | 98.398 | 98.4544 | 98.3876 | 98.047 | 97.727 | 98.1786 | 97.023 | 98.0396 | 98.1779 | 98.1114 | 97.7673 | 97.4492 | 97.8568 | 96.1169 | 97.3513 | 97.6637 | 97.7232 | 97.4496 | 97.1553 | 97.4598 | 2025-03-11
SMA America | SHP FLEX-US-21 {380V} | N | Y | Y | Y | Y | Y | Y* | Y | 100.84 kW, 380 Vac Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | 100.842 | 380 | 98 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22; 3.16.22] | 2025-03-11 | [11/30/2022] | 2025-03-11 | UL | 2019-12-16 | 2025-03-11 |  | N | N | 3.071 |  |  | 582 | 745 | 1195 | 10.0842 | 20.1684 | 30.2526 | 50.421 | 75.6315 | 100.842 | 98.6111 | 98.5997 | 98.64 | 98.5735 | 98.267 | 97.9599 | 98.3912 | 97.6622 | 98.3148 | 98.4239 | 98.3458 | 98.0477 | 97.7441 | 98.1382 | 97.0005 | 97.8001 | 98.0254 | 98.043 | 97.785 | 97.4908 | 97.8227 | 2025-03-11
SMA America | SHP FLEX-US-21 {385V} | N | Y | Y | Y | Y | Y | Y* | Y | 100.84 kW, 385 Vac Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | 100.842 | 385 | 98 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22; 3.16.22] | 2025-03-11 | [11/30/2022] | 2025-03-11 | UL | 2019-12-16 | 2025-03-11 |  | N | N | 3.07 |  |  | 582 | 745 | 1195 | 10.0842 | 20.1684 | 30.2526 | 50.421 | 75.6315 | 100.842 | 98.6111 | 98.5997 | 98.64 | 98.5735 | 98.267 | 97.9599 | 98.3912 | 97.6622 | 98.3148 | 98.4239 | 98.3458 | 98.0477 | 97.7441 | 98.1382 | 97.0005 | 97.8001 | 98.0254 | 98.043 | 97.785 | 97.4908 | 97.8227 | 2025-03-11
SMA America | SHP FLEX-US-21 {400V} | N | Y | Y | Y | Y | Y | Y* | Y | 105 kW, 400 Vac Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | 105.6325 | 400 | 98 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22; 3.16.22] | 2024-11-01 | [11/30/2022] | 2024-11-01 | UL | 2019-12-16 | 2024-11-01 | Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | N | N | 2.9 |  |  | 590 | 800 | 1200 | 10.5633 | 21.1265 | 31.6897 | 52.8162 | 79.2244 | 105.6325 | 98.6007 | 98.6994 | 98.7479 | 98.6923 | 98.4183 | 98.1382 | 98.5227 | 97.538 | 98.3793 | 98.4828 | 98.4385 | 98.1487 | 97.8607 | 98.2224 | 96.7617 | 97.8771 | 98.0839 | 98.1357 | 97.8974 | 97.6297 | 97.91 | 2024-11-01 | 2025-01-02
SMA America | SHP FLEX-US-21 {420V} | N | Y | Y | Y | Y | Y | Y* | Y | 112.71 kW, 385 Vac Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | 112.714 | 420 | 98.5 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22; 3.16.22] | 2025-03-11 | [11/30/2022] | 2025-03-11 | UL | 2019-12-16 | 2025-03-11 |  | N | N | 3.1747 |  |  | 630 | 780 | 1195 | 11.2714 | 22.5428 | 33.8142 | 56.357 | 84.5355 | 112.714 | 98.5405 | 98.6789 | 98.7696 | 98.7273 | 98.4643 | 98.2245 | 98.558 | 97.5773 | 98.4304 | 98.5336 | 98.5172 | 98.2495 | 97.9909 | 98.309 | 96.6341 | 97.8771 | 98.1323 | 98.1904 | 97.98 | 97.7456 | 97.9718 | 2025-03-11
SMA America | SHP 125-US-20 {480V} | N | N | Y | Y | Y | Y | Y* | Y | Sunny Highpower PEAK3, 125 kW, 1500 VDC, 480 VAC, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 125 | 480 | 98.5 | No Information Submitted | No Information Submitted | UL | [04/04/2019] | [V02.02.29.R] | 2019-07-01 | [04/04/2019] | 2020-02-03 | UL | 2019-12-16 | 2020-02-03 |  | N | N | 5.37 |  |  | 705 | 830 | 1200 | 12.5007 | 25.0014 | 37.5021 | 62.5035 | 93.7553 | 125.007 | 98.7556 | 98.9976 | 98.8838 | 98.8276 | 98.6062 | 98.2844 | 98.6955 | 98.4402 | 98.8236 | 98.6952 | 98.6274 | 98.4048 | 98.0538 | 98.4912 | 97.4702 | 98.0424 | 98.235 | 98.2842 | 98.1476 | 97.8116 | 98.1376 | 2019-07-01 | 2020-02-03
SMA America | SHP 125-US-21 {480V} | N | Y | Y | Y | Y | Y | Y* | N | 125 kW, 480 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 125 | 480 | 98.5 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22, 3.16.22] | 2023-07-11 | [11/30/2022] | 2023-07-11 | UL | 2019-12-16 | No Information Submitted |  | N | N | 2.42 |  |  | 705 | 830 | 1200 | 12.522 | 25.043 | 37.565 | 62.608 | 93.911 | 125.215 | 98.76 | 99 | 98.88 | 98.83 | 98.61 | 98.28 | 98.7 | 98.44 | 98.82 | 98.7 | 98.63 | 98.4 | 98.05 | 98.49 | 97.47 | 98.04 | 98.24 | 98.28 | 98.15 | 97.81 | 98.14 | 2023-07-11
SMA America | SHP FLEX-US-21 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 125 kW, 480 Vac Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | 125.007 | 480 | 98.5 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22; 3.16.22] | 2025-01-02 | [11/30/2022] | 2025-01-02 | UL | 2019-12-16 | 2025-01-02 | Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | N | N | 5.37 |  |  | 705 | 830 | 1200 | 12.5007 | 25.0014 | 37.5021 | 62.5035 | 93.7553 | 125.007 | 98.7556 | 98.9976 | 98.8838 | 98.8276 | 98.6062 | 98.2844 | 98.6955 | 98.4402 | 98.8236 | 98.6952 | 98.6274 | 98.4048 | 98.0538 | 98.4912 | 97.4702 | 98.0424 | 98.235 | 98.2842 | 98.1476 | 97.8116 | 98.1376 | 2025-01-02
SMA America | SHP 150-US-20 {600V} | N | N | Y | Y | Y | Y | Y* | Y | Sunny Highpower PEAK3, 150 kW, 1500 VDC, 600 VAC, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 150 | 600 | 99 | No Information Submitted | No Information Submitted | UL | [04/04/2019] | [V02.02.29.R] | 2019-07-01 | [04/04/2019] | 2020-02-03 | UL | 2019-12-16 | 2020-02-03 |  | N | N | 6.63 |  |  | 880 | 960 | 1200 | 15.0079 | 30.0157 | 45.0236 | 75.0393 | 112.559 | 150.0787 | 98.7136 | 99.052 | 98.979 | 98.955 | 98.8152 | 98.582 | 98.8603 | 98.722 | 99.0322 | 99.0162 | 98.9622 | 98.7618 | 98.5232 | 98.8344 | 98.0838 | 98.6294 | 98.704 | 98.7056 | 98.5702 | 98.3194 | 98.5857 | 2019-07-01 | 2020-02-03
SMA America | SHP 150-US-21 {600V} | N | Y | Y | Y | Y | Y | Y* | N | 150 kW, 600 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 150 | 600 | 99 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22, 3.16.22] | 2023-03-21 | [11/30/2022] | 2023-03-21 | UL | 2019-12-16 | No Information Submitted |  | N | N | 3.23 |  |  | 880 | 960 | 1200 | 15.0079 | 30.0157 | 45.0236 | 75.0393 | 112.559 | 150.0787 | 98.7136 | 99.052 | 98.979 | 98.955 | 98.8152 | 98.582 | 98.8603 | 98.722 | 99.0322 | 99.0162 | 98.9622 | 98.7618 | 98.5232 | 98.8344 | 98.0838 | 98.6294 | 98.704 | 98.7056 | 98.5702 | 98.3194 | 98.5857 | 2023-03-21
SMA America | SHP FLEX-US-21 {600V} | N | Y | Y | Y | Y | Y | Y* | Y | 150 kW, 600 Vac Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | 150.0787 | 600 | 99 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22; 3.16.22] | 2025-01-02 | [11/30/2022] | 2025-01-02 | UL | 2019-12-16 | 2025-01-02 | Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | N | N | 6.63 |  |  | 880 | 960 | 1200 | 15.0079 | 30.0157 | 45.0236 | 75.0393 | 112.559 | 150.0787 | 98.7136 | 99.052 | 98.979 | 98.955 | 98.8152 | 98.582 | 98.8603 | 98.722 | 99.0322 | 99.0162 | 98.9622 | 98.7618 | 98.5232 | 98.8344 | 98.0838 | 98.6294 | 98.704 | 98.7056 | 98.5702 | 98.3194 | 98.5857 | 2025-01-02
SMA America | SHP 165-US-21 {630V} | N | Y | Y | Y | Y | Y | Y* | N | 165 kW, 630 Vac, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 165 | 630 | 99 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22, 3.16.22] | 2023-03-21 | [11/30/2022] | 2023-03-21 | UL | 2019-12-16 | No Information Submitted |  | N | N | 4.16 |  |  | 925 | 994 | 1200 | 16.5662 | 33.1324 | 49.6987 | 82.8311 | 124.2466 | 165.6622 | 98.6206 | 98.8613 | 98.9603 | 98.9539 | 98.8451 | 98.6221 | 98.8625 | 98.474 | 98.8841 | 98.9634 | 98.8763 | 98.7697 | 98.5541 | 98.7985 | 98.4527 | 98.7551 | 98.8071 | 98.7221 | 98.6029 | 98.3606 | 98.6419 | 2023-03-21
SMA America | SHP FLEX-US-21 {630V} | N | Y | Y | Y | Y | Y | Y* | Y | 165 kW, 630 Vac Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | 165.6622 | 630 | 99 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22; 3.16.22] | 2025-01-02 | [11/30/2022] | 2025-01-02 | UL | 2019-12-16 | 2025-01-02 | Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | N | N | 4.16 |  |  | 925 | 994 | 1200 | 16.5662 | 33.1324 | 49.6987 | 82.8311 | 124.2466 | 165.6622 | 98.6206 | 98.8613 | 98.9603 | 98.9539 | 98.8451 | 98.6221 | 98.8625 | 98.474 | 98.8841 | 98.9634 | 98.8763 | 98.7697 | 98.5541 | 98.7985 | 98.4527 | 98.7551 | 98.8071 | 98.7221 | 98.6029 | 98.3606 | 98.6419 | 2025-01-02
SMA America | SHP 172-US-21 {660V} | N | Y | Y | Y | Y | Y | Y* | N | 172 kW, 1500 VDC, 660 VAC, 3-phase, transformerless, Grid Support Utility Interactive Inverter | 172 | 660 | 99 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22, 3.16.22] | 2023-03-21 | [11/30/2022] | 2023-03-21 | UL | 2019-12-16 | No Information Submitted |  | N | N | 4.24 |  |  | 968 | 1089 | 1200 | 17.281 | 34.562 | 51.843 | 86.405 | 129.6075 | 172.81 | 98.8353 | 99.1077 | 99.1251 | 99.0193 | 98.901 | 98.7013 | 98.9505 | 98.7181 | 99.0086 | 98.985 | 98.8849 | 98.7617 | 98.5564 | 98.8147 | 98.4304 | 98.7249 | 98.7067 | 98.7269 | 98.6383 | 98.4346 | 98.6509 | 2023-03-21
SMA America | SHP FLEX-US-21 {660V} | N | Y | Y | Y | Y | Y | Y* | Y | 172 kW, 660 Vac Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | 172.81 | 660 | 99 | UL | [11/30/2022] | UL | [11/30/2022] | [3.15.22; 3.16.22] | 2025-01-02 | [11/30/2022] | 2025-01-02 | UL | 2019-12-16 | 2025-01-02 | Grid Support Utility Interactive Inverter with a Nominal AC voltage range of 200 Vac - 600 Vac, and power output 50 kW - 172 kW. | N | N | 4.24 |  |  | 968 | 1089 | 1200 | 17.281 | 34.562 | 51.843 | 86.405 | 129.6075 | 172.81 | 98.8353 | 99.1077 | 99.1251 | 99.0193 | 98.901 | 98.7013 | 98.9505 | 98.7181 | 99.0086 | 98.985 | 98.8849 | 98.7617 | 98.5564 | 98.8147 | 98.4304 | 98.7249 | 98.7067 | 98.7269 | 98.6383 | 98.4346 | 98.6509 | 2025-01-02
SMA America | SC-1850-US {385V} | N | N | Y | Y | N | N | N | N | Sunny Central 1850 kW, 385 Vac Grid Support Utility Interactive Inverter | 1661 | 385 | 97 | No Information Submitted | No Information Submitted | UL | [10/16/2017] | [04.00.25.R] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted efficiency includes transformer efficiency of Eaton 34.5kV. | Y | N | 294 |  |  | 570 | 665 | 950 | 166.1 | 332.2 | 498.3 | 830.5 | 1245.75 | 1661 | 96.09 | 97.54 | 97.81 | 97.79 | 97.59 | 97.25 | 97.58 | 95.5 | 97.22 | 97.55 | 97.62 | 97.45 | 97.13 | 97.39 | 93.24 | 96.22 | 96.74 | 97.07 | 96.98 | 96.67 | 96.77 | 2018-04-16 | 2019-02-15
SMA America | SC-2200-US {385V} | N | N | Y | Y | N | N | N | N | Sunny Central 2200 kW, 385 Vac Grid Support Utility Interactive Inverter | 2079 | 385 | 97 | No Information Submitted | No Information Submitted | UL | [10/16/2017] | [04.00.25.R] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted efficiency includes transformer efficiency of Eaton 34.5kV. | Y | N | 297 |  |  | 570 | 665 | 950 | 207.9 | 415.8 | 623.7 | 1039.5 | 1559.25 | 2079 | 96.63 | 97.68 | 97.8 | 97.69 | 97.33 | 96.68 | 97.42 | 96.07 | 97.38 | 97.58 | 97.53 | 97.21 | 96.57 | 97.25 | 94.45 | 96.53 | 96.96 | 97.05 | 96.73 | 96.18 | 96.69 | 2018-04-16 | 2019-02-15
SMA America | SC 2500-EV-US {550V} | N | N | Y | Y | N | N | N | N | Sunny Central 2500 kW, 550 Vac Grid Support Utility Interactive Inverter | 2353.87 | 550 | 97 | No Information Submitted | No Information Submitted | UL | [08/30/2017] | [04.00.25.R] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted efficiency includes transformer efficiency of Eaton 34.5 kV. | Y | N | 370 |  |  | 850 | 994 | 1425 | 235.39 | 470.77 | 706.16 | 1176.94 | 1765.4 | 2353.87 | 96.42 | 97.63 | 97.83 | 97.79 | 97.42 | 96.82 | 97.49 | 95.86 | 97.35 | 97.63 | 97.65 | 97.28 | 96.74 | 97.32 | 94.25 | 96.58 | 97.07 | 97.2 | 96.81 | 96.42 | 96.79 | 2018-05-01 | 2019-02-15
SMA America | SC 2750-EV-US {600V} | N | N | Y | Y | N | N | N | N | Sunny Central 2750 kW, 600Vac, multi-mode, 3-phase Grid Support Utility Interactive Inverter | 2600 | 600 | 97.5 | No Information Submitted | No Information Submitted | UL | [08/30/2017] | [04.00.25.R] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted efficiency includes transformer efficiency of Eaton 34.5kV. | Y | N | 379.32 |  |  | 875 | 957 | 1200 | 260 | 520 | 780 | 1300 | 1950 | 2600 | 95.6543 | 97.2785 | 97.676 | 97.8338 | 97.6424 | 97.2188 | 97.5677 | 95.3931 | 97.1422 | 97.5611 | 97.7454 | 97.5481 | 97.0711 | 97.4608 | 94.4709 | 96.7352 | 97.0588 | 97.4894 | 97.3596 | 96.8887 | 97.1805 | 2018-08-15 | 2019-02-15
SMA America | SC 2660 UP-US 600V 2566A {600V} | Y | Y | Y | Y | Y | N | N | N | 2616 kW, 600 Vac, 3 Phase Grid Support Utility Interactive PV Inverter with liquid-immersed distribution transformer. | 2616.157 | 600 | 97.5 | UL | [12/15/2022] | UL | [12/15/2022] | [09.00.35.R] | 2023-06-01 | [12/15/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 252.66 |  |  | 880 | 970 | 1200 | 261.6157 | 523.2314 | 784.8471 | 1308.0785 | 1962.1178 | 2616.157 | 96.7266 | 97.7505 | 97.8883 | 97.6512 | 97.2701 | 96.5949 | 97.3928 | 96.4802 | 97.6455 | 97.8062 | 97.5795 | 97.1869 | 96.4804 | 97.303 | 95.8007 | 97.2842 | 97.5299 | 97.4109 | 97.0243 | 96.3333 | 97.0956 | 2023-06-01
SMA America | SC 2800 UP-US 630V 2566A {630V} | Y | Y | Y | Y | Y | N | N | N | 2747 kW, 600 Vac, 3 Phase Grid Support Utility Interactive PV Inverter with liquid-immersed distribution transformer. | 2747.472 | 630 | 97.5 | UL | [12/15/2022] | UL | [12/15/2022] | [09.00.35.R] | 2023-06-01 | [12/15/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 247.1 |  |  | 921 | 1000 | 1200 | 274.7472 | 549.4944 | 824.2416 | 1373.736 | 2060.604 | 2747.472 | 96.7339 | 97.7847 | 97.9214 | 97.732 | 97.3221 | 96.6649 | 97.4468 | 96.5234 | 97.6802 | 97.8378 | 97.6565 | 97.2468 | 96.562 | 97.3622 | 95.9377 | 97.3937 | 97.6166 | 97.504 | 97.11 | 96.4357 | 97.1871 | 2023-06-01
SMA America | SC 2930 UP-US 660V 2566A {660V} | Y | Y | Y | Y | Y | N | N | N | 2930 KVA, 660 Vac, Grid Support Utility Interactive Inverter connected to grid via a 2630 kVA medium voltage transformer. | 2841.88 | 660 | 97.5 | UL | [12/15/2022] | UL | [12/15/2022] | [09.00.35R] | 2023-02-21 | [12/15/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 247.96 |  |  | 962 | 1030 | 1200 | 284.188 | 568.376 | 852.564 | 1420.94 | 2131.41 | 2841.88 | 96.7417 | 97.8244 | 97.9663 | 97.7423 | 97.3866 | 96.7362 | 97.4944 | 96.5595 | 97.7327 | 97.8875 | 97.6725 | 97.3054 | 96.6327 | 97.4102 | 96.0753 | 97.4928 | 97.7086 | 97.5669 | 97.1962 | 96.5348 | 97.2725 | 2023-02-21
SMA America | SC 3060 UP-US 690V 2566A {690V} | Y | Y | Y | Y | Y | N | N | N | 2618 kW, 600 Vac, 3 Phase Grid Support Utility Interactive PV Inverter with liquid-immersed distribution transformer. | 2951.143 | 690 | 97.5 | UL | [12/15/2022] | UL | [12/15/2022] | [09.00.35.R] | 2023-06-01 | [12/15/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 255.77 |  |  | 1003 | 1062 | 1200 | 295.1143 | 590.2286 | 885.3429 | 1475.5715 | 2213.3573 | 2951.143 | 96.7455 | 97.8341 | 97.9875 | 97.7846 | 97.4312 | 96.797 | 97.5332 | 96.588 | 97.7464 | 97.9211 | 97.7151 | 97.3553 | 96.698 | 97.4548 | 96.2041 | 97.566 | 97.7733 | 97.6338 | 97.271 | 96.6148 | 97.3467 | 2023-06-01
SMA America | SC 4000 UP-US 600V 3850A {600V} | Y | N | Y | Y | Y | N | N | N | 4000 kVA, 600 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter | 3650.134 | 600 | 98.5 | No Information Submitted | No Information Submitted | UL | [09/06/2019] | [06.00.33.R] | 2020-04-21 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 453.5 |  |  | 880 | 970 | 1200 | 365.0134 | 730.0268 | 1095.0402 | 1825.067 | 2737.6005 | 3650.134 | 98.2807 | 98.7001 | 98.7205 | 98.6249 | 98.4911 | 98.1606 | 98.5322 | 98.0525 | 98.5891 | 98.6273 | 98.5552 | 98.3953 | 98.0229 | 98.4341 | 97.3227 | 98.2881 | 98.4129 | 98.4176 | 98.2202 | 97.8437 | 98.2334 | 2020-04-21
SMA America | SC 4200 UP-US 630V 3850A {630V} | Y | N | Y | Y | Y | N | N | N | 4200 kVA, 630 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter | 3832.828 | 630 | 98.5 | No Information Submitted | No Information Submitted | UL | [09/06/2019] | [06.00.33.R] | 2020-04-21 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 451.8 |  |  | 921 | 1001 | 1200 | 383.2828 | 766.5656 | 1149.8484 | 1916.414 | 2874.621 | 3832.828 | 98.2694 | 98.7021 | 98.6674 | 98.6466 | 98.5287 | 98.2119 | 98.5526 | 97.9903 | 98.5997 | 98.6622 | 98.5939 | 98.4546 | 98.0872 | 98.4791 | 97.504 | 98.3658 | 98.3947 | 98.4009 | 98.3081 | 97.9519 | 98.2909 | 2020-04-21
SMA America | SC 4400 UP-US 660V 3850A {660V} | Y | N | Y | Y | Y | N | N | N | 4400 kVA, 660 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter | 4017.113 | 660 | 98.5 | No Information Submitted | No Information Submitted | UL | [09/06/2019] | [06.00.33.R] | 2020-04-21 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 465.17 |  |  | 962 | 1032 | 1200 | 401.7113 | 803.4226 | 1205.1339 | 2008.5565 | 3012.8347 | 4017.113 | 98.287 | 98.7337 | 98.7105 | 98.7078 | 98.6023 | 98.295 | 98.616 | 98.1038 | 98.6371 | 98.6292 | 98.6406 | 98.5024 | 98.149 | 98.5198 | 97.5982 | 98.4496 | 98.5884 | 98.4873 | 98.3886 | 98.0401 | 98.3873 | 2020-04-21
SMA America | SC 4600 UP-US 690V 3850A {690V} | Y | N | Y | Y | Y | N | N | N | 4600 kVA, 690 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter | 4198.235 | 690 | 98.5 | No Information Submitted | No Information Submitted | UL | [09/06/2019] | [06.00.33.R] | 2020-04-21 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 471.07 |  |  | 1003 | 1062 | 1200 | 419.8235 | 839.647 | 1259.4705 | 2099.1175 | 3148.6762 | 4198.235 | 98.2728 | 98.7421 | 98.7243 | 98.7352 | 98.6471 | 98.3477 | 98.6497 | 98.1499 | 98.6747 | 98.6863 | 98.6911 | 98.5653 | 98.2147 | 98.5776 | 97.7407 | 98.5298 | 98.644 | 98.5955 | 98.4551 | 98.1264 | 98.466 | 2020-04-21
SolarEdge Technologies Ltd. | SE3000H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.0 kW, 240 Vac HD-Wave technology hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 2.962 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 0 |  |  | 360 | 395 | 480 | 0.3 | 0.6 | 0.9 | 1.6 | 2.1 | 2.8 | 95.67 | 98.01 | 98.63 | 99.01 | 99.19 | 99.19 | 98.89 | 95.39 | 97.88 | 98.54 | 98.96 | 99.16 | 99.16 | 98.83 | 95.93 | 98.04 | 98.57 | 99 | 99.08 | 99.17 | 98.83 | 2017-07-01 | 2025-07-01
SolarEdge Technologies Ltd. | SE3000x {240V} | N | N | Y | Y | Y | N | N | N | 3 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 3.01 | 240 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 3.39 |  |  | 100 | 388 | 480 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 95.1 | 97.1 | 97.5 | 97.8 | 97.8 | 97.7 | 97.6 | 94.8 | 96.8 | 97.4 | 97.7 | 97.7 | 97.6 | 97.5 | 93.4 | 96.4 | 97 | 97.4 | 97.5 | 97.5 | 97.2 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3000x {208V} | N | N | Y | Y | Y | N | N | N | 3 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 3.02 | 208 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 3.71 |  |  | 305 | 350 | 480 | 0.3 | 0.6 | 0.91 | 1.51 | 2.27 | 3.02 | 96 | 97.4 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 95.6 | 97.1 | 97.5 | 97.6 | 97.5 | 97.3 | 97.4 | 93.6 | 96.3 | 96.9 | 97.2 | 97.2 | 97.1 | 97 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3300x {240V} | N | N | Y | Y | Y | N | N | N | 3.3 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 3.251 | 240 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.46 |  |  | 370 | 435 | 500 | 0.33 | 0.65 | 0.98 | 1.63 | 2.44 | 3.25 | 95.3 | 97.1 | 97.5 | 97.6 | 97.6 | 97.5 | 97.5 | 94.9 | 96.8 | 97.3 | 97.5 | 97.5 | 97.3 | 97.3 | 94.2 | 96.5 | 96.9 | 97.3 | 97.4 | 97.2 | 97.1 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3800H-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.25 kW, 208 Vac HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 3.255 | 208 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | N | N | 4.12 |  |  | 360 | 395 | 480 | 0.3255 | 0.651 | 0.9765 | 1.6275 | 2.4413 | 3.255 | 89.795 | 99.3907 | 99.3812 | 99.2769 | 99.0026 | 98.7791 | 98.7455 | 92.1061 | 99.3518 | 99.377 | 99.2454 | 98.986 | 98.7542 | 98.8189 | 95.5802 | 99.4287 | 99.3924 | 99.2524 | 98.9976 | 98.7297 | 98.9699 | 2018-06-01 | 2025-08-01
SolarEdge Technologies Ltd. | SE3300x {208V} | N | N | Y | Y | Y | N | N | N | 3.3 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 3.288 | 208 | 97 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.55 |  |  | 320 | 410 | 500 | 0.33 | 0.66 | 0.99 | 1.64 | 2.47 | 3.29 | 95.5 | 97.2 | 97.3 | 97.4 | 97.2 | 97.4 | 97.2 | 94.8 | 96.7 | 97 | 97.2 | 97 | 96.8 | 96.9 | 93.5 | 96.3 | 96.6 | 96.9 | 96.9 | 96.8 | 96.7 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | NX3800T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.33 kW, 208 Vac Grid Support Utility Interactive Inverter | 3.33 | 208 | 98 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.33296 | 0.66592 | 0.99888 | 1.6648 | 2.4972 | 3.3296 | 93.4328 | 97.002 | 97.904 | 98.587 | 98.9016 | 98.945 | 98.4043 | 93.0028 | 96.7768 | 97.7436 | 98.4956 | 98.8352 | 98.908 | 98.3003 | 91.7688 | 96.19 | 97.312 | 98.2424 | 98.662 | 98.7662 | 98.0178 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE3800H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 3.747 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [04/02/2020] | [2.0.820] | 2018-10-15 | [04/02/2020] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 0 |  |  | 360 | 395 | 480 | 0.3 | 0.8 | 1.2 | 2 | 2.8 | 3.6 | 96.56 | 98.4 | 98.82 | 99.18 | 99.19 | 99.2 | 99 | 96.34 | 98.3 | 98.75 | 99.14 | 99.16 | 99.12 | 98.95 | 96.72 | 98.57 | 98.82 | 99.07 | 99.17 | 99.08 | 98.97 | 2017-07-01 | 2025-07-01
SolarEdge Technologies Ltd. | SE3800A-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 3.79 | 240 | 98 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.507] | 2018-10-15 | [6/7/2017] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 | Formerly SolarEdge Technologies Ltd. SE3800x {240V} | Y | N | 2.24 |  |  | 360 | 400 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.84 | 3.79 | 96.1 | 97.6 | 98 | 98.1 | 98.1 | 98.2 | 98 | 95.7 | 97.3 | 97.8 | 98.1 | 98 | 98.2 | 97.9 | 94.6 | 96.8 | 97.5 | 97.9 | 97.9 | 97.8 | 97.6 | 2017-07-01 | 2024-09-23
SolarEdge Technologies Ltd. | NX3800T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.84 kW, 240 Vac Grid Support Utility Interactive Inverter | 3.84 | 240 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 0.38396 | 0.76793 | 1.1519 | 1.9198 | 2.8797 | 3.8396 | 95.8904 | 98.106 | 98.149 | 98.7118 | 98.9438 | 99.0086 | 98.6389 | 95.5838 | 97.9452 | 97.9922 | 98.6262 | 98.8862 | 98.9632 | 98.549 | 94.8538 | 97.5384 | 97.6382 | 98.4694 | 98.7356 | 98.8414 | 98.3382 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE3800A-US {208V} | N | N | Y | Y | Y | N | N | N | 3.8 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter | 3.99 | 208 | 97 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Formerly SolarEdge Technologies Ltd. SE3800x {208V} | Y | N | 5.1 |  |  | 320 | 410 | 500 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 95.5 | 97.2 | 97.3 | 97.3 | 97.4 | 97.1 | 97.3 | 94.8 | 96.7 | 97.1 | 97.2 | 96.8 | 97 | 96.9 | 93.5 | 96.3 | 96.8 | 96.9 | 96.8 | 96.4 | 96.6 | 2017-07-01 | 2020-01-21
SolarEdge Technologies Ltd. | NX5000T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 4.3 kW, 208 Vac Grid Support Utility Interactive Inverter | 4.3 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.43 | 0.86 | 1.29 | 2.15 | 3.225 | 4.3 | 94.33 | 97.39 | 98.15 | 98.73 | 98.92 | 98.94 | 98.53 | 93.96 | 97.19 | 98.01 | 98.64 | 98.87 | 98.91 | 98.44 | 92.9 | 96.67 | 97.64 | 98.42 | 98.72 | 98.78 | 98.2 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE5000H-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4.97 kW, 208 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 4.979 | 208 | 98.5 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 4.51 |  |  | 360 | 395 | 480 | 0.4 | 1 | 1.6 | 2.7 | 3.6 | 4.9 | 96.58 | 98.34 | 98.72 | 98.82 | 98.82 | 98.91 | 98.7 | 96.34 | 98.22 | 98.64 | 98.76 | 98.77 | 98.64 | 98.62 | 95.89 | 97.99 | 98.46 | 98.68 | 98.7 | 98.57 | 98.51 | 2017-07-01 | 2025-07-01
SolarEdge Technologies Ltd. | SE5000x {208V} | N | N | Y | Y | Y | N | N | N | 5 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 4.98 | 208 | 97 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.46 |  |  | 320 | 410 | 500 | 0.5 | 1 | 1.49 | 2.49 | 3.73 | 4.98 | 96.6 | 97.3 | 97.4 | 97.2 | 97.1 | 96.6 | 97.1 | 95.9 | 97 | 97.2 | 97 | 97 | 96.6 | 97 | 96.2 | 96.6 | 96.9 | 96.9 | 96.4 | 96.5 | 96.5 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | NX5000T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 4.99 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.99 | 240 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.904 |  |  | 370 | 395 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.749 | 4.999 | 96.96 | 98.28 | 98.53 | 98.88 | 98.98 | 98.97 | 98.79 | 96.72 | 98.14 | 98.42 | 98.81 | 98.93 | 98.93 | 98.72 | 96.13 | 97.79 | 98.16 | 98.69 | 98.82 | 98.84 | 98.56 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | NX5700T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 4.99 kW, 208 Vac Grid Support Utility Interactive Inverter | 4.99 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.49899 | 0.99797 | 1.497 | 2.4949 | 3.7424 | 4.9899 | 95.533 | 97.9198 | 98.4648 | 98.9132 | 98.9548 | 98.9416 | 98.698 | 95.2344 | 97.7554 | 98.356 | 98.8382 | 98.917 | 98.9062 | 98.6272 | 94.3994 | 97.3232 | 98.0848 | 98.6696 | 98.7984 | 98.8096 | 98.4366 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE5000x {240V} | N | N | Y | Y | Y | N | N | N | 5 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 4.99 | 240 | 98 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 2.24 |  |  | 370 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 96.7 | 97.9 | 98.1 | 98.1 | 98.3 | 98.1 | 98.1 | 96.4 | 97.7 | 98 | 98 | 98.2 | 98 | 98 | 95.7 | 97.4 | 97.7 | 97.8 | 97.8 | 97.9 | 97.7 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE5700H-US {208V} | Y | Y | N | N | N | N | Y* |  | 4.99 kW, 208 Vac, 1-phase, Grid Support Utility Interactive Inverter | 4.99 | 208 | 98.5 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2019-12-16 |  |  | N | N | 5.71 |  |  | 360 | 395 | 460 | 0.4993 | 0.99859 | 1.4979 | 2.4965 | 3.7447 | 4.993 | 96.0984 | 98.1874 | 98.6054 | 98.7944 | 98.8246 | 98.7232 | 98.646 | 95.7494 | 98.0414 | 98.5188 | 98.746 | 98.7856 | 98.6894 | 98.5818 | 95.305 | 97.886 | 98.391 | 98.6788 | 98.7096 | 98.6182 | 98.483 | 2025-09-22
SolarEdge Technologies Ltd. | SE5000H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 5.052 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 4.52 |  |  | 360 | 395 | 480 | 0.4 | 1 | 1.6 | 2.7 | 3.6 | 4.9 | 96.65 | 98.42 | 98.79 | 99 | 98.97 | 99.11 | 98.84 | 96.38 | 98.28 | 98.7 | 98.94 | 98.92 | 98.86 | 98.76 | 96.03 | 98.07 | 98.57 | 98.87 | 98.87 | 98.81 | 98.68 | 2017-07-01 | 2025-07-01
SolarEdge Technologies Ltd. | SE6000H-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.05 kW, 208 Vac HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 5.054 | 208 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | N | N | 4.52 |  |  | 360 | 395 | 480 | 0.5054 | 1.0108 | 1.5162 | 2.527 | 3.7905 | 5.054 | 96.6546 | 98.421 | 98.7873 | 99.0003 | 98.9676 | 99.1108 | 98.8401 | 96.3757 | 98.2834 | 98.7004 | 98.9384 | 98.9206 | 98.8604 | 98.7612 | 96.0285 | 98.0689 | 98.5658 | 98.8689 | 98.8702 | 98.8054 | 98.6764 | 2018-06-01 | 2025-07-01
SolarEdge Technologies Ltd. | NX6000T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.2 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.2 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.2 |  |  | 370 | 395 | 450 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 95.56 | 97.93 | 98.5 | 98.89 | 98.97 | 98.93 | 98.7 | 95.25 | 97.77 | 98.39 | 98.83 | 98.93 | 98.89 | 98.63 | 94.42 | 97.35 | 98.09 | 98.66 | 98.8 | 98.8 | 98.44 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE6000x {208V} | N | N | Y | Y | Y | N | N | N | 6 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 5.33 | 208 | 97 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.22 |  |  | 320 | 410 | 500 | 0.53 | 1.07 | 1.6 | 2.66 | 3.99 | 5.33 | 96.6 | 97.3 | 97.4 | 97.2 | 97.1 | 96.4 | 97.1 | 95.9 | 97 | 97.2 | 97 | 97 | 96.4 | 97 | 96.2 | 96.6 | 96.9 | 96.9 | 96.4 | 96.3 | 96.5 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE5700H-US {240V} | Y | Y | N | N | N | N | Y* | Y | 5.7 kW, 240 Vac, 1-phase, Grid Support Utility Interactive Inverter, with PCS functionality. | 5.7 | 240 | 99 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-09-13 | 2023-12-01 |  | N | N | 4.51 |  |  | 360 | 395 | 480 | 0.57 | 1.14 | 1.71 | 2.85 | 4.275 | 5.7 | 97.18 | 98.62 | 98.91 | 98.96 | 98.96 | 99 | 98.87 | 96.96 | 98.52 | 98.83 | 98.9 | 98.91 | 98.97 | 98.8 | 96.66 | 98.33 | 98.71 | 98.84 | 98.86 | 98.72 | 98.72 | 2023-12-01 | 2025-07-01
SolarEdge Technologies Ltd. | NX5700T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.76 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.76 | 240 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 0.57593 | 1.1519 | 1.7278 | 2.8797 | 4.3195 | 5.7593 | 97.1958 | 98.1446 | 98.6468 | 98.9328 | 99.0058 | 98.9938 | 98.8313 | 96.9622 | 98.0012 | 98.549 | 98.8746 | 98.9594 | 98.9646 | 98.7648 | 96.3848 | 97.6476 | 98.313 | 98.7374 | 98.8688 | 98.8804 | 98.6147 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE6000x {240V} | N | N | Y | Y | Y | N | N | N | 6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 5.99 | 240 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 3.52 |  |  | 370 | 435 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 5.99 | 96.5 | 97.6 | 97.7 | 97.5 | 97.3 | 97 | 97.4 | 96 | 97.4 | 97.5 | 97.3 | 97.3 | 97 | 97.3 | 95.7 | 97.1 | 97.3 | 97.2 | 97.3 | 96.9 | 97.2 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | NX6000T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 6 | 240 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.904 |  |  | 370 | 395 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 97.21 | 98.28 | 98.63 | 98.93 | 99 | 98.98 | 98.83 | 96.98 | 98.15 | 98.53 | 98.87 | 98.96 | 98.95 | 98.77 | 96.42 | 97.81 | 98.29 | 98.74 | 98.86 | 98.86 | 98.62 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE6000H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, 1-phase, HD-Wave technology hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 6.046 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 4.52 |  |  | 360 | 395 | 480 | 0.5 | 1.3 | 1.9 | 3 | 4.3 | 5.8 | 97.17 | 98.61 | 98.9 | 98.95 | 98.95 | 98.98 | 98.96 | 96.95 | 98.51 | 98.82 | 98.89 | 98.9 | 98.95 | 98.79 | 96.65 | 98.32 | 98.7 | 98.83 | 98.85 | 98.71 | 98.7 | 2017-07-01 | 2025-07-01
SolarEdge Technologies Ltd. | SE7600H-US {208V} | Y | Y | N | N | N | N | Y* |  | 6.59 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter | 6.59 | 208 | 98.5 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2019-12-16 |  |  | N | N | 5.71 |  |  | 360 | 395 | 460 | 0.65918 | 1.3184 | 1.9775 | 3.2959 | 4.9438 | 6.5918 | 97.0038 | 98.4596 | 98.7174 | 98.8268 | 98.6934 | 98.4912 | 98.6349 | 96.7882 | 98.361 | 98.6352 | 98.7766 | 98.6706 | 98.4698 | 98.5878 | 96.481 | 98.2284 | 98.5526 | 98.6966 | 98.6182 | 98.4124 | 98.5115 | 2025-09-22
SolarEdge Technologies Ltd. | NX7600T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.65 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.65 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.66492 | 1.3298 | 1.9948 | 3.3246 | 4.9869 | 6.6492 | 96.573 | 98.3252 | 98.7826 | 98.9396 | 98.9402 | 98.8222 | 98.7898 | 96.3114 | 98.2062 | 98.7028 | 98.8978 | 98.9112 | 98.7916 | 98.7382 | 95.6876 | 97.8886 | 98.3998 | 98.7664 | 98.8094 | 98.7146 | 98.5756 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE7600A-US {208V} | N | N | Y | Y | Y | N | N | N | 7.6 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter | 7.56 | 208 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.75 |  |  | 325 | 375 | 480 | 0.756 | 1.512 | 2.268 | 3.78 | 5.67 | 7.56 | 96.3 | 97.4 | 97.6 | 97.6 | 97.5 | 97.3 | 97.5 | 96 | 97.2 | 97.5 | 97.5 | 97.4 | 97.2 | 97.3 | 95.2 | 96.8 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE7600H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, with PCS functionality. | 7.616 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [04/02/2020] | [2.0.820] | 2018-10-15 | [04/02/2020] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 4.52 |  |  | 360 | 395 | 480 | 0.7 | 1.6 | 2.4 | 3.6 | 5.5 | 7.3 | 97.72 | 98.8 | 98.97 | 98.97 | 99.04 | 98.73 | 98.94 | 97.52 | 98.7 | 98.91 | 98.93 | 99.02 | 98.69 | 98.89 | 97.24 | 98.57 | 98.83 | 98.87 | 98.75 | 98.71 | 98.71 | 2017-07-01 | 2025-07-01
SolarEdge Technologies Ltd. | SE7600A-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 7.625 | 240 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.507] | 2018-10-15 | [6/7/2017] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 2.16 |  |  | 360 | 400 | 480 | 0.7625 | 1.525 | 2.288 | 3.813 | 5.719 | 7.625 | 97 | 97.9 | 98 | 97.9 | 97.7 | 97.3 | 97.7 | 96.6 | 97.8 | 97.9 | 97.9 | 97.6 | 97.3 | 97.7 | 95.7 | 97.4 | 97.6 | 97.6 | 97.5 | 97.1 | 97.5 | 2017-07-01 | 2020-01-21
SolarEdge Technologies Ltd. | NX7600T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 7.68 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.68 | 240 | 99 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 0.76789 | 1.5358 | 2.3037 | 3.8394 | 5.7592 | 7.6789 | 97.8732 | 98.55 | 98.832 | 99.0034 | 98.9984 | 98.9066 | 98.9075 | 97.6892 | 98.4318 | 98.7504 | 98.958 | 98.9606 | 98.881 | 98.8536 | 97.2498 | 98.1646 | 98.5614 | 98.8644 | 98.8864 | 98.823 | 98.7381 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | NX9600T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 8.32 kW, 208 Vac Grid Support Utility Interactive Inverter | 8.32 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.8319 | 1.6638 | 2.4957 | 4.1595 | 6.2393 | 8.319 | 97.2646 | 98.5754 | 98.879 | 98.9498 | 98.8478 | 98.673 | 98.7873 | 97.0328 | 98.488 | 98.8118 | 98.9178 | 98.8232 | 98.656 | 98.745 | 96.4846 | 98.2328 | 98.6462 | 98.7732 | 98.7394 | 98.5662 | 98.6111 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | NX10000T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 8.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 8.6 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.85995 | 1.7199 | 2.5799 | 4.2998 | 6.4496 | 8.5995 | 97.3222 | 98.6092 | 98.9072 | 98.9602 | 98.8338 | 98.6492 | 98.7882 | 97.1264 | 98.5116 | 98.8468 | 98.9284 | 98.8138 | 98.6296 | 98.75 | 96.5894 | 98.2678 | 98.6914 | 98.7858 | 98.7288 | 98.535 | 98.618 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE10000H-US {208V} | Y | Y | N | N | N | N | Y* |  | 8.69 kW, 208 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter | 8.69 | 208 | 98.5 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2019-12-16 |  |  | N | N | 5.71 |  |  | 360 | 395 | 460 | 0.86943 | 1.7389 | 2.6083 | 4.3471 | 6.5207 | 8.6943 | 97.7128 | 98.7498 | 98.8938 | 98.8578 | 98.5768 | 98.3014 | 98.6342 | 97.533 | 98.669 | 98.835 | 98.8134 | 98.5516 | 98.2296 | 98.5896 | 97.3006 | 98.5502 | 98.7378 | 98.7388 | 98.509 | 98.176 | 98.5218 | 2025-09-22
SolarEdge Technologies Ltd. | SE9KUS {208V} | N | N | Y | Y | Y | Y | Y* | Y | 9 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter | 8.963 | 208 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [9/20/2017] | [2.19.1207] | 2018-10-15 | [9/20/2017] | 2020-02-03 | Intertek | 2019-12-16 | 2020-02-03 |  | Y | N | 3.08 |  |  | 384 | 424 | 504 | 0.9 | 1.79 | 2.69 | 4.48 | 6.72 | 8.96 | 95.2 | 96.5 | 96.8 | 96.6 | 96.3 | 96.1 | 96.4 | 94.9 | 96.3 | 96.7 | 96.5 | 96.3 | 96 | 96.3 | 94.3 | 96 | 96.4 | 96.4 | 96.1 | 95.8 | 96.1 | 2017-07-01 | 2020-02-03
SolarEdge Technologies Ltd. | SE9600H-US {240V} | Y | Y | N | N | N | N | N | N | 9.6 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 9.5685 | 240 | 99 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 6 |  |  | 360 | 395 | 460 | 0.95685 | 1.9137 | 2.8705 | 4.7842 | 7.1764 | 9.5685 | 97.9766 | 98.9434 | 99.0536 | 98.9918 | 98.7734 | 98.5294 | 98.8173 | 97.829 | 98.895 | 99.031 | 98.9754 | 98.7742 | 98.5144 | 98.8025 | 97.595 | 98.809 | 98.9796 | 98.9562 | 98.7668 | 98.49 | 98.7735 | 2025-07-01
SolarEdge Technologies Ltd. | SE9600H-US {208V} | Y | Y | N | N | N | N | N | N | 9.57 kW, 208 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter | 9.5783 | 208 | 98.5 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.71 |  |  | 360 | 395 | 460 | 0.95783 | 1.9157 | 2.8735 | 4.7892 | 7.1838 | 9.5783 | 97.9964 | 98.9244 | 98.9876 | 98.846 | 98.53 | 98.1958 | 98.6329 | 97.873 | 98.877 | 98.9758 | 98.8386 | 98.5382 | 98.1722 | 98.6258 | 97.6706 | 98.8012 | 98.9366 | 98.8252 | 98.5256 | 98.1514 | 98.5987 | 2025-07-01
SolarEdge Technologies Ltd. | NX9600T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.6 | 240 | 99 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 0.95996 | 1.9199 | 2.8799 | 4.7998 | 7.1997 | 9.5996 | 98.2748 | 98.6916 | 98.9372 | 99.0048 | 98.936 | 98.7794 | 98.9041 | 98.1384 | 98.6026 | 98.8864 | 98.9708 | 98.9134 | 98.7596 | 98.868 | 97.7824 | 98.4554 | 98.7438 | 98.8868 | 98.8568 | 98.7118 | 98.7792 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE10KUS {480V} | N | N | Y | Y | Y | N | N | N | 10 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 9.85 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [6/8/2017] | [2.19.759] | 2018-10-15 | [6/8/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 3.13 |  |  | 100 | 882 | 962 | 0.98 | 1.97 | 2.95 | 4.92 | 7.38 | 9.85 | 95.5 | 97.4 | 97.8 | 98.1 | 98.1 | 98 | 97.9 | 95.1 | 97.3 | 97.7 | 98 | 98 | 97.9 | 97.8 | 94.2 | 97 | 97.5 | 97.9 | 98 | 97.9 | 97.7 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE10000A-US {208V} | N | N | Y | Y | Y | N | N | N | 10 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter | 9.93 | 208 | 97 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.75 |  |  | 325 | 375 | 480 | 0.993 | 1.986 | 2.979 | 4.965 | 7.448 | 9.93 | 96.8 | 97.6 | 97.7 | 97.5 | 97.4 | 97.1 | 97.4 | 96.5 | 97.4 | 97.5 | 97.4 | 97.2 | 96.9 | 97.3 | 96.2 | 97 | 97.2 | 97.1 | 96.9 | 96.7 | 96.9 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE10000A-US {240V} | N | N | Y | Y | Y | N | N | N | 10 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 9.94 | 240 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.95 |  |  | 360 | 400 | 480 | 0.99 | 1.99 | 2.98 | 4.97 | 7.46 | 9.94 | 96.8 | 97.6 | 97.8 | 97.8 | 97.7 | 97.5 | 97.7 | 96.6 | 97.5 | 97.7 | 97.6 | 97.6 | 97.4 | 97.6 | 96.4 | 97.3 | 97.5 | 97.4 | 97.4 | 97.2 | 97.3 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | NX11500T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 9.98 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.98 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.99797 | 1.9959 | 2.9939 | 4.9899 | 7.4848 | 9.9797 | 97.6712 | 98.8168 | 98.937 | 98.9454 | 98.7348 | 98.4884 | 98.7525 | 97.5094 | 98.7378 | 98.891 | 98.9178 | 98.718 | 98.4718 | 98.7211 | 97.04 | 98.432 | 98.743 | 98.8082 | 98.6416 | 98.4134 | 98.6028 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE10000H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 9.994 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.820] | 2021-02-22 | [01/17/2018] | 2021-02-22 | Intertek | 2019-12-16 | 2020-01-21 |  | N | N | 6 |  |  | 360 | 395 | 480 | 0.999 | 1.999 | 2.998 | 4.997 | 7.496 | 9.994 | 97.86 | 98.83 | 98.94 | 99.23 | 98.95 | 98.63 | 98.94 | 97.69 | 98.74 | 98.88 | 99.18 | 98.91 | 98.55 | 98.89 | 97.44 | 98.54 | 98.68 | 98.7 | 98.62 | 98.1 | 98.57 | 2018-04-02 | 2025-07-01
SolarEdge Technologies Ltd. | NX10000T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10 | 240 | 99 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 0.99989 | 1.9998 | 2.9997 | 4.9995 | 7.4992 | 9.9989 | 98.3682 | 98.7656 | 98.981 | 99.0276 | 98.9244 | 98.7572 | 98.9143 | 98.2162 | 98.6898 | 98.9082 | 98.9892 | 98.9104 | 98.7336 | 98.879 | 97.8728 | 98.5094 | 98.7818 | 98.9028 | 98.8538 | 98.6872 | 98.7907 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE11400H-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.00 kW, 208 Vac, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 10.001 | 208 | 98.5 | Intertek | [9/23/2024] | Intertek | [04/02/2020] | [2.0.820] | 2021-02-22 | [04/02/2020] | 2021-02-22 | Intertek | 2019-12-16 | 2020-06-22 |  | N | N | 5.71 |  |  | 360 | 395 | 480 | 1.0001 | 2.0001 | 3.0002 | 5.0003 | 7.5004 | 10.0006 | 97.7682 | 98.7285 | 98.8322 | 99.0698 | 98.6681 | 98.1747 | 98.7145 | 97.6539 | 98.6608 | 98.771 | 98.9695 | 98.5754 | 98.0908 | 98.6248 | 97.439 | 98.5357 | 98.6979 | 98.696 | 98.62 | 98.0972 | 98.5677 | 2020-06-22 | 2025-07-01
SolarEdge Technologies Ltd. | SE10KUS {208V} | N | Y | N | N | N | N | Y* | N | 10.03 kW, 208 Vac, Grid Support Utility Interactive Inverter | 10.0337 | 208 | 97 | Intertek | [12/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2022-12-09 | No Information Submitted |  | N | N | 0.01 |  |  | 400 | 460 | 600 | 1.0034 | 2.0067 | 3.0101 | 5.0169 | 7.5253 | 10.0337 | 94.656 | 96.812 | 97.208 | 97.38 | 97.366 | 97.25 | 97.2081 | 93.772 | 96.36 | 96.858 | 97.1 | 97.104 | 96.992 | 96.8976 | 91.782 | 95.566 | 96.232 | 96.632 | 96.702 | 96.606 | 96.3725 | 2023-02-13
SolarEdge Technologies Ltd. | NX13000T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.2 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.2 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 1.1199 | 2.2399 | 3.3598 | 5.5996 | 8.3994 | 11.1993 | 97.9458 | 98.8688 | 98.9528 | 98.9134 | 98.6726 | 98.319 | 98.7198 | 97.76 | 98.7988 | 98.9108 | 98.8884 | 98.6586 | 98.3134 | 98.6909 | 97.3184 | 98.62 | 98.7836 | 98.8 | 98.561 | 98.2568 | 98.5759 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE11400A-US {240V} | N | N | Y | Y | Y | N | N | N | 11.4 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 11.39 | 240 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.326] | 2018-10-15 | [6/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 5.95 |  |  | 360 | 400 | 480 | 1.139 | 2.278 | 3.417 | 5.695 | 8.543 | 11.39 | 96.9 | 97.7 | 97.8 | 97.8 | 97.6 | 97.4 | 97.7 | 96.8 | 97.6 | 97.7 | 97.6 | 97.5 | 97.3 | 97.5 | 96.5 | 97.4 | 97.5 | 97.5 | 97.3 | 97.1 | 97.3 | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE11400H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 11.393 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.820] | 2021-02-22 | [01/17/2018] | 2021-02-22 | Intertek | 2019-12-16 | 2020-01-21 |  | N | N | 6 |  |  | 360 | 395 | 480 | 1.139 | 2.279 | 3.418 | 5.697 | 8.545 | 11.393 | 97.88 | 98.84 | 98.95 | 99.16 | 98.82 | 98.41 | 98.85 | 97.91 | 98.83 | 98.93 | 99.17 | 98.83 | 98.4 | 98.85 | 97.42 | 98.63 | 98.79 | 98.82 | 98.8 | 98.39 | 98.72 | 2018-04-02 | 2025-07-01
SolarEdge Technologies Ltd. | NX11500T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.52 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.52 | 240 | 99 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 1.1519 | 2.3038 | 3.4557 | 5.7595 | 8.6392 | 11.5189 | 97.9908 | 98.8782 | 99.0282 | 99.0236 | 98.868 | 98.6448 | 98.8742 | 97.8258 | 98.7932 | 98.9742 | 98.995 | 98.8484 | 98.623 | 98.8393 | 98.1314 | 98.616 | 98.8468 | 98.908 | 98.7902 | 98.58 | 98.7762 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | NX13000T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 13 kW, 240 Vac Grid Support Utility Interactive Inverter | 13 | 240 | 99 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 1.2999 | 2.5998 | 3.8998 | 6.4996 | 9.7494 | 12.9992 | 98.2158 | 98.9684 | 99.0612 | 99.0086 | 98.7758 | 98.4758 | 98.8312 | 98.0694 | 98.9106 | 99.0222 | 98.9846 | 98.7688 | 98.4686 | 98.8086 | 97.7142 | 98.7448 | 98.9074 | 98.9096 | 98.7254 | 98.4376 | 98.7321 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE14.4KUS {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 14.4 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter | 14.51 | 208 | 97 | Intertek | [12/19/2022] | Intertek | [9/20/2017] | [2.19.1207] | 2018-10-15 | [9/20/2017] | 2020-02-03 | Intertek | 2019-12-16 | 2020-02-03 |  | Y | N | 4.16 |  |  | 400 | 460 | 600 | 1.45 | 2.9 | 4.35 | 7.26 | 10.88 | 14.51 | 95.9 | 97.3 | 97.5 | 97.5 | 97 | 96.6 | 97.1 | 95.2 | 97.1 | 97.2 | 97.3 | 97.2 | 96.8 | 97.1 | 94.7 | 96.3 | 96.7 | 96.9 | 96.4 | 96.2 | 96.4 | 2017-07-01 | 2023-02-01
SolarEdge Technologies Ltd. | SE43.2KUS {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 43.2 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of three SE14.4KUS installed together rated max output power = 43.2kW) | 14.51 | 208 | 97 | Intertek | [10/22/2022] | Intertek | [11/2/2017] | [2.19.1207] | 2018-10-15 | [11/2/2017] | 2020-02-03 | Intertek | 2019-12-16 | 2020-02-03 | Performance data is the same as SE14.4KUS. | Y | N | 4.16 |  |  | 400 | 460 | 600 | 1.451 | 2.902 | 4.353 | 7.255 | 10.8825 | 14.51 | 95.8927 | 97.2782 | 97.4837 | 97.462 | 97.0093 | 96.6434 | 97.1118 | 95.2252 | 97.0865 | 97.1922 | 97.3046 | 97.1963 | 96.8019 | 97.1145 | 94.6669 | 96.2868 | 96.6724 | 96.8566 | 96.3889 | 96.1759 | 96.4365 | 2018-02-01 | 2023-02-01
SolarEdge Technologies Ltd. | SE17.3KUS {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 17.3 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter | 16.564 | 208 | 97 | Intertek | [12/19/2022] | Intertek | [07/07/2020] | [2.20.223] | 2020-08-11 | [07/07/2020] | 2020-08-11 | Intertek | 2020-06-22 | 2020-08-11 |  | N | N | 5.28 |  |  | 400 | 460 | 600 | 1.6564 | 3.3128 | 4.9691 | 8.2819 | 12.4228 | 16.5638 | 96.254 | 97.276 | 97.532 | 97.31 | 96.986 | 96.694 | 97.0902 | 95.77 | 97.01 | 97.108 | 97.13 | 96.79 | 96.474 | 96.854 | 94.76 | 96.44 | 96.656 | 96.86 | 96.53 | 96.138 | 96.5195 | 2020-08-11 | 2023-02-01
SolarEdge Technologies Ltd. | SE50KUS {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of three SE17.3KUS installed together rated max output power = 50kW). | 16.564 | 208 | 97 | Intertek | [10/22/2022] | Intertek | [11/03/2021] | [2.19.1207] | 2021-12-13 | [11/03/2021] | 2021-12-13 | Intertek | 2021-05-17 | 2021-12-13 | Performance data is the same as SE17.3KUS. | N | N | 5.28 |  |  | 400 | 460 | 600 | 1.6564 | 3.3128 | 4.9691 | 8.2819 | 12.4228 | 16.5638 | 96.254 | 97.276 | 97.532 | 97.31 | 96.986 | 96.694 | 97.0902 | 95.77 | 97.01 | 97.108 | 97.13 | 96.79 | 96.474 | 96.854 | 94.76 | 96.44 | 96.656 | 96.86 | 96.53 | 96.138 | 96.5195 | 2021-12-13 | 2023-02-01
SolarEdge Technologies Ltd. | SE20KUS {480V} | N | N | Y | Y | Y | Y | Y* | Y | 20 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 20.05 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [9/20/2017] | [2.19.1207] | 2018-10-15 | [9/20/2017] | 2020-02-03 | Intertek | 2019-12-16 | 2020-02-03 |  | Y | N | 3.48 |  |  | 842 | 882 | 962 | 2.01 | 4.01 | 6.02 | 10.03 | 15.04 | 20.05 | 96.6 | 97.6 | 97.9 | 98 | 98 | 97.9 | 97.9 | 96.6 | 97.5 | 97.9 | 98 | 98 | 97.9 | 97.9 | 96 | 97.3 | 97.7 | 97.9 | 97.8 | 97.8 | 97.7 | 2017-07-01 | 2020-02-03
SolarEdge Technologies Ltd. | SE30KUS {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 30.159 | 480 | 98.5 | Intertek | [12/19/2022] | Intertek | [9/20/2017] | [2.19.1207] | 2018-10-15 | [9/20/2017] | 2020-02-03 | Intertek | 2019-12-16 | 2020-02-03 |  | N | N | 7.06 |  |  | 790 | 850 | 950 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.4085 | 98.3647 | 98.5506 | 98.5075 | 98.4804 | 98.3856 | 98.4411 | 97.0794 | 98.2049 | 98.429 | 98.4194 | 98.4029 | 98.314 | 98.3422 | 96.4164 | 97.9007 | 98.2089 | 98.2953 | 98.2622 | 98.2 | 98.1677 | 2018-01-02 | 2023-02-01
SolarEdge Technologies Ltd. | SE100KUS {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of three SE33.3KUS installed together rated max output power = 100kW). | 33.3 | 480 | 98.5 | Intertek | [10/22/2022] | Intertek | [11/2/2017] | [2.19.1207] | 2018-10-15 | [11/2/2017] | 2020-02-03 | Intertek | 2019-12-16 | 2020-02-03 | Performance data is the same as SE33.3KUS. | Y | N | 5.05 |  |  | 790 | 850 | 950 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.1892 | 98.2429 | 98.8889 | 98.5098 | 98.6777 | 98.4615 | 98.5757 | 96.664 | 98.0844 | 98.1132 | 98.5059 | 98.3704 | 98.1595 | 98.2749 | 96.3383 | 97.844 | 97.8428 | 98.4706 | 98.3128 | 98.1595 | 98.1794 | 2018-02-01 | 2023-02-01
SolarEdge Technologies Ltd. | SE33.3KUS {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 33.3 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 33.3 | 480 | 98.5 | Intertek | [12/19/2022] | Intertek | [9/20/2017] | [2.19.1207] | 2018-10-15 | [9/20/2017] | 2020-02-03 | Intertek | 2019-12-16 | 2020-02-03 |  | Y | N | 5.05 |  |  | 790 | 850 | 950 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.2 | 98.2 | 98.9 | 98.5 | 98.7 | 98.5 | 98.6 | 96.7 | 98.1 | 98.1 | 98.5 | 98.4 | 98.2 | 98.3 | 96.3 | 97.8 | 97.8 | 98.5 | 98.3 | 98.2 | 98.2 | 2017-07-01 | 2023-02-01
SolarEdge Technologies Ltd. | SE66.6KUS {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 66.6 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of two SE33.3KUS installed together rated max output power = 66.6kW). | 33.3 | 480 | 98.5 | Intertek | [10/22/2022] | Intertek | [11/2/2017] | [2.19.1207] | 2018-10-15 | [11/2/2017] | 2020-02-03 | Intertek | 2019-12-16 | 2020-02-03 | Performance data is the same as SE33.3KUS. | Y | N | 5.05 |  |  | 790 | 850 | 950 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.1892 | 98.2429 | 98.8889 | 98.5098 | 98.6777 | 98.4615 | 98.5757 | 96.664 | 98.0844 | 98.1132 | 98.5059 | 98.3704 | 98.1595 | 98.2749 | 96.3383 | 97.844 | 97.8428 | 98.4706 | 98.3128 | 98.1595 | 98.1794 | 2018-02-01 | 2023-02-01
SolarEdge Technologies Ltd. | SE120KUS {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 120 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of three SE40KUS installed together rated max output power = 120kW). | 40.252 | 480 | 98.5 | Intertek | [10/22/2022] | Intertek | [06/28/2021] | [2.19.1207] | 2021-07-01 | [06/28/2021] | 2021-07-01 | Intertek | 2021-05-17 | 2021-07-01 |  | N | N | 7.43 |  |  | 790 | 850 | 950 | 4.0252 | 8.0504 | 12.0757 | 20.1261 | 30.1892 | 40.2522 | 97.42 | 98.37 | 98.696 | 98.6 | 98.41 | 98.326 | 98.4384 | 97.096 | 98.21 | 98.58 | 98.5 | 98.31 | 98.172 | 98.3218 | 96.51 | 97.948 | 98.39 | 98.35 | 98.162 | 97.994 | 98.1437 | 2021-07-01 | 2023-02-01
SolarEdge Technologies Ltd. | SE40KUS {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 40.252 | 480 | 98.5 | Intertek | [12/19/2022] | Intertek | [07/07/2020] | [2.20.223] | 2020-08-11 | [07/07/2020] | 2020-08-11 | Intertek | 2020-06-22 | 2020-08-11 |  | N | N | 7.43 |  |  | 790 | 850 | 950 | 4.0252 | 8.0504 | 12.0757 | 20.1261 | 30.1892 | 40.2522 | 97.42 | 98.37 | 98.696 | 98.6 | 98.41 | 98.326 | 98.4384 | 97.096 | 98.21 | 98.58 | 98.5 | 98.31 | 98.172 | 98.3218 | 96.51 | 97.948 | 98.39 | 98.35 | 98.162 | 97.994 | 98.1437 | 2020-08-11 | 2023-02-01
SolarEdge Technologies Ltd. | SE80KUS {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 80 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of two SE40KUS installed together rated max output power = 80kW). | 40.252 | 480 | 98.5 | Intertek | [10/22/2022] | Intertek | [06/28/2021] | [2.19.1207] | 2021-07-01 | [06/28/2021] | 2021-07-01 | Intertek | 2021-05-17 | 2021-07-01 |  | N | N | 7.43 |  |  | 790 | 850 | 950 | 4.0252 | 8.0504 | 12.0757 | 20.1261 | 30.1892 | 40.2522 | 97.42 | 98.37 | 98.696 | 98.6 | 98.41 | 98.326 | 98.4384 | 97.096 | 98.21 | 98.58 | 98.5 | 98.31 | 98.172 | 98.3218 | 96.51 | 97.948 | 98.39 | 98.35 | 98.162 | 97.994 | 98.1437 | 2021-07-01 | 2023-02-01
SolarEdge Technologies Ltd. | SE110KUS {480V} | N | Y | N | N | N | N | Y* | Y | 110 kW, 480 Vac, 3-phase, Grid Support Utility Interactive Inverter | 109.9881 | 480 | 98.5 | Intertek | [3/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2019-12-16 | 2023-11-21 |  | N | N | 7.3 |  |  | 795 | 850 | 950 | 10.9988 | 21.9976 | 32.9964 | 54.9941 | 82.4911 | 109.9881 | 96.76 | 98.31 | 98.536 | 98.604 | 98.43 | 98.41 | 98.4055 | 96.4 | 98.16 | 98.43 | 98.532 | 98.38 | 98.38 | 98.3277 | 95.666 | 97.87 | 98.23 | 98.36 | 98.29 | 98.082 | 98.1611 | 2023-11-21
SolarEdge Technologies Ltd. | SE250KUS {600V} | N | Y | N | N | N | N | Y* | Y | 250 kW, 600 Vac, 3-phase, Grid Support Utility Interactive Inverter | 249.907 | 600 | 99 | Intertek | [11/8/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2024-12-16 | 2025-03-31 |  | N | N | 21.61 |  |  | 1090 | 1250 | 1320 | 24.991 | 49.981 | 74.972 | 124.953 | 187.43 | 249.907 | 97.9 | 98.79 | 98.97 | 98.99 | 98.91 | 98.76 | 98.88 | 97.16 | 98.48 | 98.77 | 98.89 | 98.84 | 98.7 | 98.75 | 96.87 | 98.35 | 98.69 | 98.84 | 98.81 | 98.68 | 98.7 | 2025-04-01
SolarEdge Technologies Ltd. | SE285KUS {600V} | N | Y | N | N | N | N | Y* | Y | 285 kW, 600 Vac, 3-phase, Grid Support Utility Interactive Inverter | 284.159 | 600 | 99 | Intertek | [11/8/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2024-12-16 | 2025-03-31 |  | N | N | 21.6 |  |  | 1090 | 1250 | 1320 | 28.416 | 56.832 | 85.248 | 142.08 | 213.12 | 284.159 | 98.1 | 98.88 | 99.01 | 98.97 | 98.86 | 98.65 | 98.86 | 97.47 | 98.6 | 98.84 | 98.88 | 98.81 | 98.6 | 98.75 | 97.22 | 98.49 | 98.77 | 98.85 | 98.78 | 98.6 | 98.71 | 2025-04-01
SolarEdge Technologies Ltd. | SE330KUS {690V} | N | Y | N | N | N | N | Y* | Y | 330 kW, 690 Vac, Grid Support Utility Interactive Inverter | 329.741 | 690 | 99 | Intertek | [11/8/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2024-12-06 | 2025-07-11 |  | N | N | 20.9 |  |  | 1200 | 1260 | 1400 | 32.974 | 65.948 | 98.922 | 164.87 | 247.306 | 329.741 | 97.96 | 98.85 | 99.05 | 99.16 | 99.03 | 98.87 | 99 | 97.69 | 98.74 | 98.97 | 99.09 | 99 | 98.82 | 98.94 | 97.14 | 98.51 | 98.81 | 98.91 | 98.94 | 98.78 | 98.82 | 2025-07-11
Solaria Corporation | Solaria PowerXT-345R-AC {240V} | N | N | Y | Y | Y | N | N | N | 345 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-345R-PD. Microinverter IQ7PLUS-72-x-ACM-US {240V}. | 0.29 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/03/2018] | [V02.10.00];[V02.12.00];[V02.14.02] | 2018-10-15 | [05/03/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | 2018-06-01 | 2019-05-01
Solaria Corporation | Solaria PowerXT-350R-AC {240V} | N | N | Y | Y | Y | N | N | N | 350 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-350R-PD. Microinverter IQ7PLUS-72-x-ACM-US {240V}. | 0.29 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/03/2018] | [V02.10.00];[V02.12.00];[V02.14.02] | 2018-10-15 | [05/03/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | 2018-06-01 | 2019-05-01
Solaria Corporation | Solaria PowerXT-355R-AC {240V} | N | N | Y | Y | Y | N | N | N | 355 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-355R-PD. Microinverter IQ7PLUS-72-x-ACM-US {240V}. | 0.29 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/03/2018] | [V02.10.00];[V02.12.00];[V02.14.02] | 2018-10-15 | [05/03/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | 2018-06-01 | 2019-05-01
Solaria Corporation | Solaria PowerXT-360R-AC {240V} | N | N | Y | Y | Y | N | N | N | 360 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-360R-PD. Microinverter IQ7PLUS-72-x-ACM-US {240V} {SI1}. | 0.29 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/03/2018] | [V02.10.00];[V02.12.00];[V02.14.02] | 2018-10-15 | [05/03/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | 2018-06-01 | 2019-05-01
Solaria Corporation | Solaria PowerXT-365R-AC {240V} | N | N | Y | Y | Y | N | N | N | 365 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-365R-PD. Microinverter IQ7PLUS-72-x-ACM-US {240V}. | 0.29 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/03/2018] | [V02.10.00];[V02.12.00];[V02.14.02] | 2019-05-01 | [05/03/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | 2019-05-01
Solaria Corporation | Solaria PowerXT-395R-PM-AC {240V} | N | N | Y | Y | Y | Y | Y* | Y | 395 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Solaria PowerXT-395R-PM. Microinverter: IQ7A-72-2-US {240V} | 0.3487 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/23/2020] | [V04.18.02] | 2020-06-01 | [04/23/2020] | 2020-06-01 | UL | 2020-03-18 | 2020-06-01 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2020-06-01
Solaria Corporation | Solaria PowerXT-400R-PM-AC {240V} | N | N | Y | Y | Y | Y | Y* | Y | 400 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Solaria PowerXT-400R-PM. Microinverter: IQ7A-72-2-US {240V} | 0.3487 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/23/2020] | [V04.18.02] | 2020-06-01 | [04/23/2020] | 2020-06-01 | UL | 2020-03-18 | 2020-06-01 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2020-06-01
Solaria Corporation | Solaria PowerXT-410R-PM-AC {240V} | N | N | Y | Y | Y | Y | Y* | Y | 410 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Solaria PowerXT-410R-PM. Microinverter: IQ7A-72-2-US {240V} | 0.3487 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/23/2020] | [V04.18.02] | 2020-06-01 | [04/23/2020] | 2020-06-01 | UL | 2020-03-18 | 2020-06-01 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2020-06-01
Solaria Corporation | Solaria PowerXT-420R-PM-AC {240V} | N | N | Y | Y | Y | Y | Y* | Y | 420 W, 240 Vac, Grid Support Utility Interactive, monocrystalline ACPV, black backsheet. DC module: Solaria PowerXT-420R-PM. Microinverter: IQ7A-72-2-US {240V} | 0.3487 | 240 | 97 | No Information Submitted | No Information Submitted | UL | [04/23/2020] | [V04.18.02] | 2020-06-01 | [04/23/2020] | 2020-06-01 | UL | 2020-03-18 | 2020-06-01 | This component is specific to ACPV modules and is not available as an individual unit. | N | Y | 0.019 |  |  | 38 | 40.5 | 43 | 0.03487 | 0.06974 | 0.10461 | 0.17435 | 0.26152 | 0.3487 | 95.1546 | 95.8056 | 96.6492 | 97.1481 | 96.9702 | 96.471 | 96.8132 | 95.0679 | 95.7094 | 96.5708 | 97.1127 | 96.977 | 96.4639 | 96.7913 | 95.0012 | 95.633 | 96.4691 | 97.072 | 96.9595 | 96.4604 | 96.7547 | 2020-06-01
SolarJuice American Inc. | S4A-H60 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 5.57 | 240 | 94 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 25 |  |  | 240 | 335 | 425 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 93.8526 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 94.3396 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888 | 94.1609 | 2021-07-12
SolarJuice American Inc. | S4A-H70 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 6.666 | 240 | 94.5 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 25 |  |  | 290 | 360 | 425 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 94.3168 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 94.5405 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836 | 94.4389 | 2021-07-12
SolarJuice American Inc. | S4A-H76 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 7.642 | 240 | 95.5 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 44 |  |  | 304 | 402 | 500 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 95.4058 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 95.4118 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449 | 96.1997 | 2021-07-12
SolarJuice American Inc. | S4A-H86 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 8.604 | 240 | 96 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 40 |  |  | 258 | 379 | 500 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 95.2714 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 95.7814 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922 | 96.1906 | 2021-07-12
Sol-Ark | SA-MP-1000-208/240V {208V} | N | Y | N | N | N | N | N | N | 1000 kW, 208Vac Grid Support Utility Interactive Microinverter | 1.001 | 208 | 95.5 | TUV Rheinland of North America | [11/11/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 2.47 |  |  | 40 | 47.5 | 55 | 0.1 | 0.2 | 0.3 | 0.5 | 0.75 | 1.001 | 90.94 | 91.8 | 93.95 | 96.15 | 96.33 | 95.71 | 95.53 | 92.07 | 93.03 | 94.24 | 96.29 | 96.51 | 95.8 | 95.8 | 90.9 | 91.82 | 93.87 | 95.91 | 96.06 | 95.24 | 95.31 | 2025-04-01
Sol-Ark | SA-MP-1000-208/240V {240V} | N | Y | N | N | N | N | N | N | 1000 W, 240Vac Grid Support Utility Interactive Microinverter | 1.009 | 240 | 96 | TUV Rheinland of North America | [11/11/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 2.31 |  |  | 40 | 47.5 | 55 | 0.101 | 0.202 | 0.303 | 0.504 | 0.756 | 1.009 | 91.18 | 91.89 | 94.19 | 96.36 | 96.53 | 95.92 | 95.74 | 92.3 | 93.23 | 94.44 | 96.49 | 96.72 | 96 | 96.01 | 91.14 | 92.02 | 94.14 | 96.13 | 96.28 | 95.45 | 95.53 | 2025-04-01
Sol-Ark | 5K-120V/8K-230V-1P {120V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 120 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 4.7871 | 120 | 96.5 | TUV Rheinland | [7/8/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-01-18 | 2024-05-13 |  | N | N | 11.7 |  |  | 200 | 312.5 | 425 | 0.47871 | 0.95742 | 1.4361 | 2.3936 | 3.5903 | 4.7871 | 94.422 | 96.792 | 97.112 | 96.518 | 95.908 | 95.576 | 96.1487 | 94.832 | 97.148 | 97.55 | 96.838 | 96.532 | 95.88 | 96.6486 | 94.292 | 96.732 | 97.052 | 96.49 | 95.946 | 95.406 | 96.1391 | 2022-11-14 | 2024-05-13
Sol-Ark | 5K-120V/8K-230V-1P {240V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 7.9703 | 240 | 96.5 | TUV Rheinland | [7/8/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-01-18 | 2024-05-13 |  | N | N | 19.3 |  |  | 200 | 312.5 | 425 | 0.79703 | 1.5941 | 2.3911 | 3.9851 | 5.9777 | 7.9703 | 94.432 | 96.79 | 97.304 | 96.606 | 96.184 | 95.546 | 96.3353 | 94.82 | 97.058 | 97.568 | 96.802 | 96.458 | 95.99 | 96.6045 | 94.374 | 96.7 | 97.082 | 96.412 | 95.828 | 95.31 | 96.0607 | 2022-11-14 | 2024-05-13
Sol-Ark | Limitless 10K-LV {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 8.635 | 208 | 96.5 | SGS | [5/26/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.29 |  |  | 250 | 370 | 425 | 0.863 | 1.727 | 2.59 | 4.317 | 6.476 | 8.635 | 93.23 | 95.85 | 97.56 | 97.12 | 96.74 | 96.5 | 96.72 | 93.44 | 95.99 | 97.57 | 97.08 | 96.45 | 96.25 | 96.56 | 93.32 | 95.87 | 97.57 | 96.95 | 96.68 | 96.43 | 96.66 | 2024-08-01
Sol-Ark | Sol-Ark-12K-P {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 8.818 | 208 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-12-23 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.88181 | 1.7636 | 2.6454 | 4.409 | 6.6136 | 8.8181 | 91.4663 | 94.7338 | 95.331 | 97.2779 | 97.1712 | 96.8243 | 96.6054 | 91.6795 | 94.935 | 95.479 | 97.4054 | 97.2156 | 96.9037 | 96.696 | 91.8809 | 94.8955 | 95.3141 | 97.2443 | 96.8807 | 97.0098 | 96.4763 | 2019-12-23 | 2023-04-11
Sol-Ark | Sol-Ark-9k-48-ST {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 8.818 | 208 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-12-23 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.88181 | 1.7636 | 2.6454 | 4.409 | 6.6136 | 8.8181 | 91.4663 | 94.7338 | 95.331 | 97.2779 | 97.1712 | 96.8243 | 96.6054 | 91.6795 | 94.935 | 95.479 | 97.4054 | 97.2156 | 96.9037 | 96.696 | 91.8809 | 94.8955 | 95.3141 | 97.2443 | 96.8807 | 97.0098 | 96.4763 | 2019-12-23 | 2023-04-11
Sol-Ark | Sol-Ark-8k-48-ST {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 KW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 8.8181 | 240 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-08-01 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.88181 | 1.7636 | 2.6454 | 4.409 | 6.6136 | 8.8181 | 91.4663 | 94.7338 | 95.331 | 97.2779 | 97.1712 | 96.8243 | 96.6054 | 91.6795 | 94.935 | 95.479 | 97.4054 | 97.2156 | 96.9037 | 96.696 | 91.8809 | 94.8955 | 95.3141 | 97.2443 | 96.8807 | 97.0098 | 96.4763 | 2019-08-01 | 2023-04-11
Sol-Ark | Sol-Ark-12K-P {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 8.982 | 240 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-12-23 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.89822 | 1.7964 | 2.6947 | 4.4911 | 6.7366 | 8.9822 | 91.8174 | 94.8883 | 95.5678 | 97.1321 | 96.9715 | 97.1243 | 96.5341 | 91.6365 | 94.9704 | 95.6697 | 97.5151 | 97.4122 | 97.0522 | 96.8536 | 91.5513 | 95.0486 | 95.8243 | 97.5595 | 97.2251 | 97.0494 | 96.7827 | 2019-12-23 | 2023-04-11
Sol-Ark | Sol-Ark-9k-48-ST {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 8.982 | 240 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-12-23 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.89822 | 1.7964 | 2.6947 | 4.4911 | 6.7366 | 8.9822 | 91.8174 | 94.8883 | 95.5678 | 97.1321 | 96.9715 | 97.1243 | 96.5341 | 91.6365 | 94.9704 | 95.6697 | 97.5151 | 97.4122 | 97.0522 | 96.8536 | 91.5513 | 95.0486 | 95.8243 | 97.5595 | 97.2251 | 97.0494 | 96.7827 | 2019-12-23 | 2023-04-11
Sol-Ark | Sol-Ark-8k-48-ST {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 KW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 8.9822 | 208 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-08-01 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.89822 | 1.7964 | 2.6947 | 4.4911 | 6.7366 | 8.9822 | 91.8174 | 94.8883 | 95.5678 | 97.1321 | 96.9715 | 97.1243 | 96.5341 | 91.6365 | 94.9704 | 95.6697 | 97.5151 | 97.4122 | 97.0522 | 96.8536 | 91.5513 | 95.0486 | 95.8243 | 97.5595 | 97.2251 | 97.0494 | 96.7827 | 2019-08-01 | 2023-04-11
Sol-Ark | Limitless 10K-LV {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 9.97 | 240 | 96.5 | SGS | [5/26/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.29 |  |  | 250 | 370 | 425 | 0.997 | 1.994 | 2.991 | 4.985 | 7.478 | 9.97 | 93.43 | 96.24 | 97.47 | 96.99 | 96.46 | 96.22 | 96.55 | 93.61 | 96.05 | 97.51 | 97.35 | 96.99 | 96.27 | 96.91 | 93.49 | 96.09 | 97.58 | 97.2 | 96.8 | 96.21 | 96.78 | 2024-08-01
Sol-Ark | 12K-2P-LL {240V} | Y | Y | N | N | N | N | Y* |  | 12 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.9628 | 240 | 97 | TUV Rheinland of North America | [5/29/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 46161 |  |  | N | N | 9.45 |  |  | 250 | 337.5 | 425 | 1.1963 | 2.3926 | 3.5888 | 5.9814 | 8.9721 | 11.9628 | 94.45 | 96.14 | 96.65 | 96.83 | 96.76 | 96.58 | 96.63 | 96.43 | 97.6 | 97.91 | 98.02 | 97.67 | 97.55 | 97.71 | 94.82 | 96.68 | 97.18 | 97.52 | 97.51 | 97.31 | 97.31 | 2026-08-11 |  | Y | N | N | N | N | N | N | N | N
Sol-Ark | 12K-2P-LL {208V} | Y | Y | N | N | N | N | Y* |  | 12 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.9853 | 208 | 97.5 | TUV Rheinland of North America | [5/29/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 46161 |  |  | N | N | 8 |  |  | 250 | 337.5 | 425 | 1.1985 | 2.3971 | 3.5956 | 5.9927 | 8.989 | 11.9853 | 94.72 | 96.27 | 96.66 | 96.79 | 96.68 | 96.6 | 96.6 | 96.4 | 97.59 | 97.83 | 97.99 | 97.83 | 97.68 | 97.79 | 94.81 | 96.69 | 97.18 | 97.58 | 97.61 | 97.35 | 97.38 | 2026-08-11 |  | Y | N | N | N | N | N | N | N | N
Sol-Ark | Limitless 15K-LV {208V} | Y | Y | N | N | N | N | Y* | N | 15 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 13.01 | 208 | 96.5 | SGS | [7/27/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-01-12 | No Information Submitted |  | N | N | 21.2 |  |  | 200 | 320 | 425 | 1.3014 | 2.6029 | 3.9043 | 6.5072 | 9.7608 | 13.0145 | 93.374 | 95.8088 | 97.681 | 96.9864 | 96.551 | 96.3162 | 96.6021 | 93.6666 | 95.9928 | 97.712 | 97.172 | 96.6578 | 96.4328 | 96.7281 | 93.469 | 95.9614 | 97.63 | 97.0532 | 96.5632 | 96.3156 | 96.6279 | 2022-08-11 | 2023-02-13
Sol-Ark | Limitless 15K-LV {240V} | Y | Y | N | N | N | N | Y* | N | 15 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 15.04 | 240 | 96.5 | SGS | [7/27/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-01-12 | No Information Submitted |  | N | N | 21.2 |  |  | 200 | 320 | 425 | 1.5044 | 3.0087 | 4.5131 | 7.5219 | 11.2828 | 15.0437 | 93.582 | 95.8704 | 97.6968 | 97.062 | 96.661 | 96.4142 | 96.6945 | 93.693 | 96.1402 | 97.7394 | 97.2496 | 96.7728 | 96.4702 | 96.819 | 93.6154 | 95.9584 | 97.6952 | 97.089 | 96.7006 | 96.4 | 96.726 | 2022-08-11 | 2023-02-13
Sol-Ark | Limitless 18K-2P-LV {208V} | Y | Y | N | N | N | N | Y* | N | 18 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 15.5502 | 208 | 97 | TUV Rheinland of North America | [5/8/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-05-06 | No Information Submitted |  | N | N | 1.37 |  |  | 250 | 337.5 | 425 | 1.555 | 3.11 | 4.6651 | 7.7751 | 11.6626 | 15.5502 | 94.24 | 95.4 | 95.96 | 96.512 | 97.268 | 96.914 | 96.7201 | 94.416 | 95.61 | 96.41 | 97.272 | 97.802 | 97.296 | 97.2533 | 94.276 | 95.506 | 96.258 | 96.876 | 97.468 | 97.092 | 96.9539 | 2025-08-21 | 2025-11-03
Sol-Ark | Limitless 18K-2P-LV {240V} | Y | Y | N | N | N | N | Y* | N | 18 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 17.9442 | 240 | 97 | TUV Rheinland of North America | [5/8/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-05-06 | No Information Submitted |  | N | N | 1.37 |  |  | 250 | 337.5 | 425 | 1.7944 | 3.5888 | 5.3833 | 8.9721 | 13.4582 | 17.9442 | 94.422 | 95.664 | 96.208 | 96.748 | 97.318 | 96.952 | 96.8483 | 94.668 | 95.798 | 96.458 | 97.09 | 97.824 | 97.302 | 97.2523 | 94.432 | 95.7 | 96.304 | 96.902 | 97.482 | 97.042 | 96.9857 | 2025-08-21 | 2025-11-03
Sol-Ark | 30K-3P-208V {120V} | Y | Y | N | N | N | N | Y* | Y | 30 kW, 120 Vac Grid Support Interactive Hybrid Inverter with PCS functionality. | 30.025 | 120 | 96.5 | TUV Rheinland of North America | [3/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-01-23 | 2024-05-13 |  | N | N | 31.9 |  |  | 270 | 385 | 500 | 3.0025 | 6.005 | 9.0076 | 15.0126 | 22.5189 | 30.0252 | 94.448 | 96.852 | 97.246 | 96.534 | 96.014 | 95.534 | 96.2263 | 94.814 | 97.092 | 97.534 | 96.824 | 96.44 | 95.92 | 96.5935 | 94.344 | 96.68 | 97.14 | 96.444 | 95.836 | 95.342 | 96.078 | 2023-05-22 | 2025-07-11
Sol-Ark | 60K-3P-480V {277V} | Y | Y | N | N | N | N | Y* | Y | 60 kW, 277 Vac Grid Support Interactive Hybrid Inverter with PCS functionality. | 60.05 | 277 | 97.5 | TUV Rheinland of North America | [3/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-01-23 | 2024-05-13 |  | N | N | 5.29 |  |  | 540 | 695 | 850 | 6.005 | 12.01 | 18.015 | 30.025 | 45.0375 | 60.05 | 94.422 | 98.066 | 98.602 | 97.896 | 97.376 | 96.784 | 97.5191 | 94.748 | 98.504 | 98.834 | 98.228 | 97.77 | 97.26 | 97.8842 | 94.32 | 98.036 | 98.376 | 97.826 | 97.196 | 96.688 | 97.3715 | 2024-01-02 | 2025-07-11
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Micro 300P {240V} | N | Y | N | N | N | N | Y* | Y | 300 VA, 240 Vac, Grid Support Utility Interactive Microinverter | 0.32 | 240 | 93 | CSA Group | [8/22/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-22 | 2024-10-11 |  | N | Y | 0.06 |  |  | 27.5 | 38 | 45 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 73.44 | 86.09 | 91.93 | 93.38 | 94.8 | 95.18 | 92.88 | 79.89 | 88.02 | 91.4 | 94.01 | 95.24 | 95.84 | 93.57 | 79.92 | 87.84 | 90.79 | 93.45 | 94.98 | 95.51 | 93.22 | 2024-10-11
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Micro 400P {240V} | N | Y | N | N | N | N | Y* | Y | 400 VA, 240 Vac, Grid Support Utility Interactive Microinverter | 0.41 | 240 | 94 | CSA Group | [8/22/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-22 | 2024-10-11 |  | N | Y | 0.06 |  |  | 29 | 38 | 45 | 0.041 | 0.082 | 0.123 | 0.205 | 0.308 | 0.41 | 76.7 | 88.53 | 91.79 | 94.07 | 94.83 | 94.65 | 93.26 | 81.38 | 90.42 | 92.96 | 94.91 | 95.7 | 95.85 | 94.37 | 80.27 | 89.49 | 92.3 | 94.26 | 95.25 | 95.42 | 93.81 | 2024-10-11
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Micro 450P {240V} | N | Y | N | N | N | N | Y* | Y | 450 VA, 240 Vac, Grid Support Utility Interactive Microinverter | 0.458 | 240 | 93.5 | CSA Group | [8/22/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-22 | 2024-10-11 |  | N | Y | 0.06 |  |  | 30 | 38 | 45 | 0.046 | 0.092 | 0.137 | 0.229 | 0.343 | 0.458 | 76.5 | 88.45 | 91.69 | 94.04 | 94.59 | 94.48 | 93.09 | 81.61 | 90.33 | 92.47 | 94.5 | 95.46 | 95.62 | 94.1 | 81.4 | 89.93 | 92.07 | 94.27 | 95.1 | 95.3 | 93.77 | 2024-10-11
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Micro 500P {240V} | N | Y | N | N | N | N | Y* | Y | 500 VA, 240 Vac, Grid Support Utility Interactive Microinverter | 0.506 | 240 | 94 | CSA Group | [8/22/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-22 | 2024-10-11 |  | N | Y | 0.061 |  |  | 30 | 38 | 45 | 0.051 | 0.101 | 0.152 | 0.253 | 0.38 | 0.506 | 78.85 | 89.35 | 92.31 | 94.22 | 94.52 | 94.35 | 93.3 | 83.62 | 91.18 | 93.1 | 94.87 | 95.6 | 95.63 | 94.45 | 83.17 | 90.75 | 92.6 | 94.54 | 95.22 | 95.32 | 94.06 | 2024-10-11
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Micro 600P {240V} | N | Y | N | N | N | N | Y* | Y | 600 VA, 240 Vac,Grid Support Utility Interactive Microinverter | 0.594 | 240 | 94 | CSA Group | [8/22/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-22 | 2024-10-11 |  | N | Y | 0.061 |  |  | 32.5 | 38 | 45 | 0.059 | 0.119 | 0.178 | 0.297 | 0.446 | 0.594 | 80.57 | 89.6 | 92.34 | 94.12 | 94.69 | 93.61 | 93.42 | 82.13 | 90.39 | 92.94 | 94.82 | 95.35 | 95.23 | 94.17 | 82 | 89.82 | 92.34 | 94.43 | 94.96 | 94.96 | 93.76 | 2024-10-11
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-HYB-3.8K-G2 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 3.805 | 240 | 97 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 175.4 | 337.9 | 499.5 | 0.38047 | 0.76094 | 1.1414 | 1.9023 | 2.8535 | 3.8047 | 92.7832 | 95.3783 | 96.1221 | 96.5347 | 96.5885 | 96.4765 | 96.3029 | 94.0899 | 96.2193 | 96.885 | 97.3248 | 97.4661 | 97.4427 | 97.1681 | 91.4685 | 96.3171 | 97.1281 | 97.4492 | 97.6556 | 97.6619 | 97.2348 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-HYB-5.0K-G2 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 5.003 | 240 | 97.5 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 229.9 | 363.7 | 499.9 | 0.50027 | 1.0005 | 1.5008 | 2.5013 | 3.752 | 5.0027 | 94.4996 | 96.2452 | 96.7656 | 97.0082 | 96.9837 | 96.852 | 96.8198 | 95.7546 | 97.2612 | 97.4657 | 97.7249 | 97.7239 | 97.6405 | 97.5871 | 94.8122 | 97.071 | 97.3678 | 97.6591 | 97.7118 | 97.6279 | 97.5072 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-6.0-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Transformerless Hybrid Grid Support Utility Interactive Inverter with PV arc detector | 5.57 | 240 | 94 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2020-11-23 | [10/21/2020] | 2020-11-23 | Intertek | 2020-09-11 | 2020-11-23 |  | N | N | 25 |  |  | 240 | 335 | 425 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 93.8526 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 94.3396 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888 | 94.1609 | 2020-11-23
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-HYB-6.0K-G2 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 6.017 | 240 | 97.5 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 277 | 388.3 | 498.7 | 0.60166 | 1.2033 | 1.805 | 3.0083 | 4.5125 | 6.0166 | 95.0593 | 96.7801 | 97.1224 | 97.2712 | 97.1927 | 97.0029 | 97.0853 | 96.3129 | 97.458 | 97.7478 | 97.8566 | 97.7758 | 97.645 | 97.7085 | 94.8068 | 96.9441 | 97.5246 | 97.7657 | 97.6571 | 97.5829 | 97.5106 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-HYB-7.6K-G2 {208V} | Y | Y | Y | Y | Y | Y | N |  | 7.6 kW, 208 Vac Grid Support Utility-interactive Inverter | 6.6364 | 208 | 97.5 | CSA Group | [12/9/2024] | CSA Group | [12/9/2024] | [V1.05, V1.03, V1.10] | 2025-09-22 | [12/9/2024] | 2025-09-22 | No Information Submitted | No Information Submitted |  |  | N | N | 5.44 |  |  | 235 | 360 | 440 | 0.66364 | 1.3273 | 1.9909 | 3.3182 | 4.9773 | 6.6364 | 95.5469 | 96.9555 | 97.2605 | 97.4473 | 96.9905 | 96.707 | 97.0452 | 96.695 | 97.8863 | 97.9782 | 97.9395 | 97.7927 | 97.5992 | 97.7969 | 96.1754 | 97.2803 | 97.9229 | 97.937 | 97.7703 | 97.6911 | 97.7314 | 2025-09-22 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-7.0-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7.0 kW, 240 Vac Transformerless Hybrid Grid Support Utility Interactive Inverter with PV arc detector | 6.666 | 240 | 94.5 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2020-11-23 | [10/21/2020] | 2020-11-23 | Intertek | 2020-09-11 | 2020-11-23 |  | N | N | 25 |  |  | 290 | 360 | 425 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 94.3168 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 94.5405 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836 | 94.4389 | 2020-11-23
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-HYB-7.6K-G2 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 7.593 | 240 | 97.5 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 234.1 | 365.5 | 498.4 | 0.75932 | 1.5186 | 2.278 | 3.7966 | 5.6949 | 7.5932 | 95.5301 | 96.9355 | 97.2078 | 97.319 | 96.9534 | 96.7056 | 96.9905 | 96.6677 | 97.8357 | 97.9705 | 97.937 | 97.774 | 97.5335 | 97.7786 | 96.0575 | 97.25 | 97.8206 | 97.8742 | 97.7481 | 97.6184 | 97.6843 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-7.6-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 7.642 | 240 | 95.5 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2019-06-01 | [10/21/2020] | 2021-01-21 | Intertek | 2020-09-11 | 2021-01-21 |  | N | N | 44 |  |  | 304 | 402 | 500 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 95.4058 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 95.4118 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449 | 96.1997 | 2019-06-03 | 2021-01-21
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-8.6-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 8.604 | 240 | 96 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2019-06-01 | [10/21/2020] | 2021-01-21 | Intertek | 2020-09-11 | 2021-01-21 |  | N | N | 40 |  |  | 258 | 379 | 500 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 95.2714 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 95.7814 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922 | 96.1906 | 2019-06-03 | 2021-01-21
Solvari, Inc. | SVR-A10-208 {208V} | N | Y | Y | Y | Y | Y | Y* | N | 350 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.303 | 208 | 96.5 | Intertek | [5/7/2024] | Intertek | [5/7/2024] | [4200] | 2024-09-03 | [5/7/2024] | 2024-09-03 | Intertek | 2024-08-13 | No Information Submitted |  | N | Y | 0.2 |  |  | 22 | 35 | 55 | 0.03 | 0.061 | 0.091 | 0.152 | 0.227 | 0.303 | 93.65 | 95.58 | 97.05 | 96.79 | 96.59 | 96.45 | 96.51 | 92.67 | 96.13 | 96.9 | 96.82 | 96.68 | 96.11 | 96.52 | 93.33 | 94.83 | 97.27 | 96.87 | 96.68 | 96.41 | 96.55 | 2024-09-03
Solvari, Inc. | SVR-A11-208 {208V} | N | Y | Y | Y | Y | Y | Y* | N | 400 VA, 208 Vac Grid Support Utility Interactive Microinverter | 0.343 | 208 | 96.5 | Intertek | [5/7/2024] | Intertek | [5/7/2024] | [4200] | 2024-09-03 | [5/7/2024] | 2024-09-03 | Intertek | 2024-08-13 | No Information Submitted |  | N | Y | 0.2 |  |  | 22 | 35 | 55 | 0.034 | 0.069 | 0.103 | 0.171 | 0.257 | 0.343 | 93.64 | 95.63 | 96.89 | 96.8 | 96.6 | 96.48 | 96.5 | 92.73 | 96.22 | 96.83 | 96.89 | 96.68 | 96.14 | 96.53 | 93.22 | 94.85 | 97.24 | 96.87 | 96.66 | 96.42 | 96.53 | 2024-09-03
Solvari, Inc. | SVR-A10-240 {240V} | N | Y | Y | Y | Y | Y | Y* | N | 350 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.346 | 240 | 96.5 | Intertek | [5/7/2024] | Intertek | [5/7/2024] | [4200] | 2024-09-03 | [5/7/2024] | 2024-09-03 | Intertek | 2024-08-13 | No Information Submitted |  | N | Y | 0.3 |  |  | 22 | 35 | 55 | 0.035 | 0.069 | 0.104 | 0.173 | 0.26 | 0.346 | 94.2 | 96.12 | 96.84 | 97.1 | 96.58 | 96.13 | 96.58 | 93.96 | 96.82 | 96.73 | 97.04 | 96.96 | 96.41 | 96.79 | 91.25 | 96.02 | 96.91 | 96.78 | 96.61 | 96.43 | 96.43 | 2024-09-03
Solvari, Inc. | SVR-A11-240 {240V} | N | Y | Y | Y | Y | Y | Y* | N | 400 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.398 | 240 | 96.5 | Intertek | [5/7/2024] | Intertek | [5/7/2024] | [4200] | 2024-09-03 | [5/7/2024] | 2024-09-03 | Intertek | 2024-08-13 | No Information Submitted |  | N | Y | 0.3 |  |  | 22 | 35 | 55 | 0.04 | 0.08 | 0.12 | 0.199 | 0.299 | 0.398 | 94.28 | 96.24 | 96.87 | 97.07 | 96.58 | 96.09 | 96.59 | 94 | 96.86 | 96.64 | 97.05 | 96.99 | 96.42 | 96.8 | 91.29 | 96.09 | 96.93 | 96.75 | 96.64 | 96.41 | 96.45 | 2024-09-03
Sparq Systems | Q1200-4101 {240V} | N | N | Y | Y | Y | N | N | N | 1200 W, 240 Vac, 60Hz Grid Support Utility Interactive Inverter | 1.165 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [06/29/2018] | [1.20.62] | 2018-10-15 | [06/29/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.04 |  |  | 28 | 29 | 31 | 0.12 | 0.24 | 0.36 | 0.6 | 0.9 | 1.2 | 91.2693 | 95.4412 | 96.5736 | 97.1364 | 97.0548 | 96.7999 | 96.6893 | 90.983 | 95.514 | 96.5823 | 97.0419 | 96.9805 | 96.7573 | 96.6212 | 89.75 | 95.2351 | 96.4213 | 97.0117 | 96.9939 | 96.8163 | 96.5424 | 2018-08-01 | 2018-10-15
Sparq Systems | Q1200-4102 {240V} | N | N | Y | Y | Y | N | N | N | 1200 W, 240 Vac, 60 Hz Grid Support Utility Interactive Inverter | 1.203 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [10/31/2018] | [1.20.62] | 2019-02-01 | [10/31/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.04 |  |  | 36 | 37 | 38 | 0.12032 | 0.24064 | 0.36096 | 0.6016 | 0.9024 | 1.2032 | 88.21 | 94.58 | 96.05 | 97.188 | 97.44 | 97.345 | 96.7033 | 87.2763 | 94.772 | 96.19 | 97.21 | 97.36 | 97.235 | 96.6491 | 87.1383 | 95.037 | 96.348 | 97.161 | 97.327 | 97.225 | 96.6475 | 2019-02-01
Sparq Systems | Q2000-4102 {240V} | N | N | Y | Y | Y | N | N | N | 2000 W, 240 Vac, Grid Support Utility Interactive Inverter | 1.72 | 240 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland | [7/22/2022] | [1.20.62] | 2023-03-13 | [7/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0 |  |  | 36.5 | 37.5 | 38.5 | 0.172 | 0.344 | 0.516 | 0.86 | 1.29 | 1.72 | 88.7478 | 95.6906 | 96.8798 | 97.46 | 97.1974 | 96.613 | 96.7719 | 89.4836 | 95.1314 | 97.3918 | 97.244 | 97.073 | 96.973 | 96.7415 | 89.2908 | 95.2642 | 97.2356 | 97.6538 | 97.382 | 96.8818 | 96.967 | 2023-03-13
SPITZER ENERGY COMPANY | SPZ-M800-S {208V} | N | Y | N | N | N | N | N | N | 0.720 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.721 | 208 | 96 | CSA Group | [4/29/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.3 |  |  | 35 | 42 | 50 | 0.072 | 0.144 | 0.216 | 0.361 | 0.541 | 0.721 | 96.19 | 96.15 | 96.38 | 96.43 | 96.21 | 96.24 | 96.27 | 96.3 | 96.28 | 96.22 | 96.54 | 96.12 | 95.87 | 96.22 | 95.33 | 96.13 | 96.04 | 96.35 | 96.15 | 95.8 | 96.13 | 2024-09-03
SPITZER ENERGY COMPANY | SPZ-M800-W {208V} | N | Y | N | N | N | N | N | N | 0.720 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.721 | 208 | 96 | CSA Group | [4/29/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.3 |  |  | 35 | 42 | 50 | 0.072 | 0.144 | 0.216 | 0.361 | 0.541 | 0.721 | 96.19 | 96.15 | 96.38 | 96.43 | 96.21 | 96.24 | 96.27 | 96.3 | 96.28 | 96.22 | 96.54 | 96.12 | 95.87 | 96.22 | 95.33 | 96.13 | 96.04 | 96.35 | 96.15 | 95.8 | 96.13 | 2024-09-03
SPITZER ENERGY COMPANY | SPZ-M800-S {240V} | N | Y | N | N | N | N | N | N | 0.720 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.723 | 240 | 96 | CSA Group | [4/29/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.4 |  |  | 35 | 42 | 50 | 0.072 | 0.145 | 0.217 | 0.362 | 0.542 | 0.723 | 96.26 | 96.22 | 96.15 | 96.42 | 96.37 | 96.1 | 96.33 | 94.72 | 96.24 | 96.23 | 96.44 | 96.22 | 95.86 | 96.19 | 96.1 | 95.95 | 96.26 | 96.12 | 96.16 | 95.84 | 96.13 | 2024-09-03
SPITZER ENERGY COMPANY | SPZ-M800-W {240V} | N | Y | N | N | N | N | N | N | 0.720 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.723 | 240 | 96 | CSA Group | [4/29/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.5 |  |  | 35 | 42 | 50 | 0.072 | 0.145 | 0.217 | 0.362 | 0.542 | 0.723 | 96.26 | 96.22 | 96.15 | 96.42 | 96.37 | 96.1 | 96.33 | 94.72 | 96.24 | 96.23 | 96.44 | 96.22 | 95.86 | 96.19 | 96.1 | 95.95 | 96.26 | 96.12 | 96.16 | 95.84 | 96.13 | 2024-09-03
SPITZER ENERGY COMPANY | SPZ-M1000-S {240V} | N | Y | N | N | N | N | N | N | 0.960 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.958 | 240 | 96.5 | CSA Group | [4/29/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.5 |  |  | 35 | 42 | 50 | 0.096 | 0.192 | 0.287 | 0.479 | 0.718 | 0.958 | 96.24 | 96.29 | 96.11 | 96.46 | 96.34 | 95.09 | 96.27 | 95.22 | 96.38 | 96.26 | 96.55 | 96.41 | 95.56 | 96.33 | 95.93 | 96.25 | 96.33 | 96.35 | 96.15 | 95.6 | 96.18 | 2024-09-03
SPITZER ENERGY COMPANY | SPZ-M1000-W {240V} | N | Y | N | N | N | N | N | N | 0.960 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.958 | 240 | 96.5 | CSA Group | [4/29/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.5 |  |  | 35 | 42 | 50 | 0.096 | 0.192 | 0.287 | 0.479 | 0.718 | 0.958 | 96.24 | 96.29 | 96.11 | 96.46 | 96.34 | 95.09 | 96.27 | 95.22 | 96.38 | 96.26 | 96.55 | 96.41 | 95.56 | 96.33 | 95.93 | 96.25 | 96.33 | 96.35 | 96.15 | 95.6 | 96.18 | 2024-09-03
SPITZER ENERGY COMPANY | SPZ-M1000-S {208V} | N | Y | N | N | N | N | N | N | 0.960 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.962 | 208 | 96 | CSA Group | [4/29/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.3 |  |  | 35 | 42 | 50 | 0.096 | 0.192 | 0.289 | 0.481 | 0.722 | 0.962 | 96.41 | 96.41 | 96.4 | 96.41 | 96.31 | 95.83 | 96.33 | 95.7 | 95.5 | 96.54 | 96.46 | 96.15 | 96.4 | 96.22 | 95.05 | 94.63 | 96.38 | 96.34 | 96.26 | 96.6 | 96.18 | 2024-09-03
SPITZER ENERGY COMPANY | SPZ-M1000-W {208V} | N | Y | N | N | N | N | N | N | 0.960 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.962 | 208 | 96 | CSA Group | [4/29/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.3 |  |  | 35 | 42 | 50 | 0.096 | 0.192 | 0.289 | 0.481 | 0.722 | 0.962 | 96.41 | 96.41 | 96.4 | 96.41 | 96.31 | 95.83 | 96.33 | 95.7 | 95.5 | 96.54 | 96.46 | 96.15 | 96.4 | 96.22 | 95.05 | 94.63 | 96.38 | 96.34 | 96.26 | 96.6 | 96.18 | 2024-09-03
SPITZER ENERGY COMPANY | SPZ 7.5KW-LV {208V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter | 5.02 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 92.68 | 95.27 | 95.93 | 96.35 | 96.16 | 95.99 | 95.98 | 93.57 | 95.86 | 96.53 | 97.03 | 97.08 | 96.97 | 96.8 | 93.73 | 95.93 | 96.5 | 96.81 | 96.9 | 96.81 | 96.65 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 7.5KW-LV {240V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 5.04 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.504 | 1.008 | 1.512 | 2.52 | 3.78 | 5.04 | 92.99 | 95.51 | 96.13 | 96.56 | 96.34 | 96.22 | 96.18 | 93.67 | 95.99 | 96.75 | 97.31 | 97.43 | 97.38 | 97.1 | 93.79 | 96.14 | 96.61 | 96.98 | 97.24 | 97.24 | 96.92 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 9KW-LV {208V} | Y | Y | N | N | N | N | Y* | Y | 6 kW, 208, Grid Support Utility Interactive PV and Battery Inverter | 6.124 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.612 | 1.225 | 1.837 | 3.062 | 4.593 | 6.124 | 91.51 | 94.38 | 95.44 | 96.15 | 96.2 | 96.02 | 95.81 | 93.61 | 95.95 | 96.7 | 97.16 | 97.14 | 97.02 | 96.88 | 93.01 | 95.45 | 96.32 | 96.9 | 96.93 | 96.76 | 96.61 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 9KW-LV {240V} | Y | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 6.149 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.615 | 1.23 | 1.845 | 3.075 | 4.612 | 6.149 | 91.6 | 94.45 | 95.46 | 96.26 | 96.41 | 96.35 | 95.97 | 93.87 | 96.14 | 96.88 | 97.38 | 97.49 | 97.42 | 97.18 | 92.69 | 95.45 | 96.41 | 97.1 | 97.3 | 97.27 | 96.87 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 12KW-LV-A {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 7.647 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.529 | 2.294 | 3.824 | 5.735 | 7.647 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 89.75 | 96.08 | 96.79 | 97.16 | 96.97 | 96.77 | 96.65 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 12KW-LV-A {208V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter | 7.648 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.53 | 2.294 | 3.824 | 5.736 | 7.648 | 92.95 | 95.54 | 96.21 | 96.65 | 96.45 | 96.19 | 96.26 | 93.74 | 96.07 | 96.79 | 97.16 | 96.97 | 96.77 | 96.8 | 94.06 | 96.23 | 96.77 | 97.12 | 96.91 | 96.7 | 96.78 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 12KW-LV-B {240V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 8.047 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.805 | 1.609 | 2.414 | 4.024 | 6.035 | 8.047 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 93.75 | 96.08 | 96.8 | 97.17 | 96.97 | 96.77 | 96.81 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 12KW-LV-B {208V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter | 8.06 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 17.78 |  |  | 200 | 360 | 480 | 0.806 | 1.612 | 2.418 | 4.03 | 6.045 | 8.06 | 92.85 | 95.45 | 96.11 | 96.55 | 96.35 | 96.09 | 96.17 | 93.65 | 95.98 | 96.69 | 97.06 | 96.87 | 96.67 | 96.71 | 93.97 | 96.14 | 96.67 | 97.02 | 96.81 | 96.55 | 96.68 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 15KW-LV-B {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 10.14 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.028 | 3.042 | 5.07 | 7.605 | 10.14 | 93.05 | 95.58 | 96.24 | 96.66 | 96.45 | 96.2 | 96.28 | 93.72 | 96.07 | 96.82 | 97.15 | 96.96 | 96.78 | 96.8 | 94.05 | 96.25 | 96.79 | 97.12 | 96.92 | 96.66 | 96.79 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 15KW-LV {240V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 10.147 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.015 | 2.029 | 3.044 | 5.074 | 7.61 | 10.147 | 93 | 95.58 | 96.22 | 96.66 | 96.46 | 96.2 | 96.28 | 93.79 | 96.1 | 96.81 | 97.16 | 96.97 | 96.77 | 96.81 | 94.11 | 96.27 | 96.78 | 97.13 | 96.92 | 96.66 | 96.79 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 15KW-LV {208V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter | 10.186 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.89 | 95.48 | 96.13 | 96.56 | 96.36 | 96.1 | 96.18 | 93.7 | 96.01 | 96.71 | 97.07 | 96.88 | 96.67 | 96.72 | 94.02 | 96.16 | 96.68 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 15KW-LV-B {208V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter | 10.186 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.91 | 95.48 | 96.12 | 96.56 | 96.36 | 96.1 | 96.18 | 93.66 | 96.02 | 96.72 | 97.07 | 96.88 | 96.68 | 96.72 | 94.07 | 96.17 | 96.67 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-08-01 | 2025-01-13
SRNE Solar Co.,Ltd | HEBP4880U240-Pro {208V} | Y | Y | N | N | N | N | N | N | 8.8 kW, 208 Vac, Grid Support Utility Interactive Inverter | 8.8085 | 208 | 96 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.88085 | 1.7617 | 2.6426 | 4.4043 | 6.6064 | 8.8085 | 94.444 | 95.624 | 96.816 | 96.49 | 97.126 | 95.666 | 96.6999 | 94.382 | 95.75 | 96.022 | 96.526 | 97.2 | 95.958 | 96.6698 | 93.96 | 94.784 | 96.388 | 96.654 | 96.84 | 95.102 | 96.4418 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-8K-UPRO {208V} | Y | Y | N | N | N | N | N | N | 8.8 kW, 208 Vac, Grid Support Utility Interactive Inverter | 8.8085 | 208 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.88085 | 1.7617 | 2.6426 | 4.4043 | 6.6064 | 8.8085 | 94.444 | 95.624 | 96.816 | 96.49 | 97.126 | 95.666 | 96.6999 | 94.382 | 95.75 | 96.022 | 96.526 | 97.2 | 95.958 | 96.6698 | 93.96 | 94.784 | 96.388 | 96.654 | 96.84 | 95.102 | 96.4418 | 2025-06-23
SRNE Solar Co.,Ltd | HESP4880U200-H {208V} | Y | Y | N | N | N | N | N | N | 8 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 8.809 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.881 | 1.762 | 2.643 | 4.404 | 6.606 | 8.809 | 94.44 | 95.62 | 96.82 | 96.49 | 97.13 | 95.67 | 96.7 | 94.38 | 95.75 | 96.02 | 96.53 | 97.2 | 95.96 | 96.67 | 93.96 | 94.78 | 96.39 | 96.65 | 96.84 | 95.1 | 96.44 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-8K-UP {208V} | Y | Y | N | N | N | N | N | N | 8 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 8.809 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.881 | 1.762 | 2.643 | 4.404 | 6.606 | 8.809 | 94.44 | 95.62 | 96.82 | 96.49 | 97.13 | 95.67 | 96.7 | 94.38 | 95.75 | 96.02 | 96.53 | 97.2 | 95.96 | 96.67 | 93.96 | 94.78 | 96.39 | 96.65 | 96.84 | 95.1 | 96.44 | 2024-03-11
SRNE Solar Co.,Ltd | HEBP4880U240-Pro {240V} | Y | Y | N | N | N | N | N | N | 8.8 kW, 240 Vac, Grid Support Utility Interactive Inverter | 8.8096 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.88096 | 1.7619 | 2.6429 | 4.4048 | 6.6072 | 8.8096 | 94.272 | 95.424 | 96.778 | 96.326 | 97.096 | 95.646 | 96.6271 | 93.65 | 95.692 | 96.638 | 96.466 | 97.23 | 96.198 | 96.7268 | 94.002 | 95.676 | 96.698 | 96.354 | 96.548 | 95.556 | 96.3302 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-8K-UPRO {240V} | Y | Y | N | N | N | N | N | N | 8.8 kW, 240 Vac, Grid Support Utility Interactive Inverter | 8.8096 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.88096 | 1.7619 | 2.6429 | 4.4048 | 6.6072 | 8.8096 | 94.272 | 95.424 | 96.778 | 96.326 | 97.096 | 95.646 | 96.6271 | 93.65 | 95.692 | 96.638 | 96.466 | 97.23 | 96.198 | 96.7268 | 94.002 | 95.676 | 96.698 | 96.354 | 96.548 | 95.556 | 96.3302 | 2025-06-23
SRNE Solar Co.,Ltd | HESP4880U200-H {240V} | Y | Y | N | N | N | N | N | N | 8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 8.81 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.881 | 1.762 | 2.643 | 4.405 | 6.607 | 8.81 | 94.27 | 95.42 | 96.78 | 96.33 | 97.1 | 95.65 | 96.63 | 93.65 | 95.69 | 96.64 | 96.47 | 97.23 | 96.2 | 96.73 | 94 | 95.68 | 96.7 | 96.35 | 96.55 | 95.56 | 96.33 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-8K-UP {240V} | Y | Y | N | N | N | N | N | N | 8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 8.81 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.881 | 1.762 | 2.643 | 4.405 | 6.607 | 8.81 | 94.27 | 95.42 | 96.78 | 96.33 | 97.1 | 95.65 | 96.63 | 93.65 | 95.69 | 96.64 | 96.47 | 97.23 | 96.2 | 96.73 | 94 | 95.68 | 96.7 | 96.35 | 96.55 | 95.56 | 96.33 | 2024-03-11
SRNE Solar Co.,Ltd | HEBP48100U240-Pro {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac, Grid Support Utility Interactive Inverter | 10.0057 | 208 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.5 |  |  | 275 | 362.5 | 450 | 1.0006 | 2.0011 | 3.0017 | 5.0028 | 7.5043 | 10.0057 | 93.636 | 96.268 | 96.57 | 96.558 | 97.164 | 94.944 | 96.6685 | 94.79 | 96.362 | 96.58 | 96.79 | 97.524 | 95.16 | 96.9709 | 93.936 | 96.22 | 96.374 | 96.486 | 96.948 | 95.296 | 96.5426 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-10K-UPRO {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac, Grid Support Utility Interactive Inverter | 10.0057 | 208 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.5 |  |  | 275 | 362.5 | 450 | 1.0006 | 2.0011 | 3.0017 | 5.0028 | 7.5043 | 10.0057 | 93.636 | 96.268 | 96.57 | 96.558 | 97.164 | 94.944 | 96.6685 | 94.79 | 96.362 | 96.58 | 96.79 | 97.524 | 95.16 | 96.9709 | 93.936 | 96.22 | 96.374 | 96.486 | 96.948 | 95.296 | 96.5426 | 2025-06-23
SRNE Solar Co.,Ltd | HESP48100U200-H {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.006 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.5 |  |  | 275 | 362.5 | 450 | 1.001 | 2.001 | 3.002 | 5.003 | 7.504 | 10.006 | 93.64 | 96.27 | 96.57 | 96.56 | 97.16 | 94.94 | 96.67 | 94.79 | 96.36 | 96.58 | 96.79 | 97.52 | 95.16 | 96.97 | 93.94 | 96.22 | 96.37 | 96.49 | 96.95 | 95.3 | 96.54 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-10K-UP {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.006 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.5 |  |  | 275 | 362.5 | 450 | 1.001 | 2.001 | 3.002 | 5.003 | 7.504 | 10.006 | 93.64 | 96.27 | 96.57 | 96.56 | 97.16 | 94.94 | 96.67 | 94.79 | 96.36 | 96.58 | 96.79 | 97.52 | 95.16 | 96.97 | 93.94 | 96.22 | 96.37 | 96.49 | 96.95 | 95.3 | 96.54 | 2024-03-11
SRNE Solar Co.,Ltd | HESP48100U200-H {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 10.008 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.6 |  |  | 275 | 362.5 | 450 | 1.001 | 2.002 | 3.002 | 5.004 | 7.506 | 10.008 | 92.88 | 96.19 | 96.28 | 96.51 | 97.09 | 94.83 | 96.55 | 93.18 | 96.37 | 96.91 | 96.71 | 97.52 | 95.05 | 96.92 | 93.25 | 96.29 | 96.9 | 97.02 | 96.94 | 95.28 | 96.69 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-10K-UP {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 10.008 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.6 |  |  | 275 | 362.5 | 450 | 1.001 | 2.002 | 3.002 | 5.004 | 7.506 | 10.008 | 92.88 | 96.19 | 96.28 | 96.51 | 97.09 | 94.83 | 96.55 | 93.18 | 96.37 | 96.91 | 96.71 | 97.52 | 95.05 | 96.92 | 93.25 | 96.29 | 96.9 | 97.02 | 96.94 | 95.28 | 96.69 | 2024-03-11
SRNE Solar Co.,Ltd | HEBP48100U240-Pro {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac, Grid Support Utility Interactive Inverter | 10.0082 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.6 |  |  | 275 | 362.5 | 450 | 1.0008 | 2.0016 | 3.0025 | 5.0041 | 7.5061 | 10.0082 | 92.884 | 96.19 | 96.28 | 96.506 | 97.094 | 94.834 | 96.5462 | 93.182 | 96.368 | 96.912 | 96.706 | 97.522 | 95.052 | 96.9226 | 93.246 | 96.288 | 96.896 | 97.016 | 96.938 | 95.276 | 96.6861 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-10K-UPRO {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac, Grid Support Utility Interactive Inverter | 10.0082 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.6 |  |  | 275 | 362.5 | 450 | 1.0008 | 2.0016 | 3.0025 | 5.0041 | 7.5061 | 10.0082 | 92.884 | 96.19 | 96.28 | 96.506 | 97.094 | 94.834 | 96.5462 | 93.182 | 96.368 | 96.912 | 96.706 | 97.522 | 95.052 | 96.9226 | 93.246 | 96.288 | 96.896 | 97.016 | 96.938 | 95.276 | 96.6861 | 2025-06-23
SRNE Solar Co.,Ltd | HEBP48114U240-Pro {240V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 240 Vac, Grid Support Utility Interactive Inverter | 10.0082 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.7 |  |  | 275 | 362.5 | 450 | 1.0008 | 2.0016 | 3.0025 | 5.0041 | 7.5062 | 10.0082 | 94.646 | 95.758 | 95.334 | 96.51 | 97.434 | 95.878 | 96.7148 | 94.21 | 94.914 | 95.268 | 96.412 | 97.364 | 95.408 | 96.5661 | 94.976 | 94.772 | 95.296 | 96.478 | 97.2 | 95.4 | 96.5195 | 2025-06-23
SRNE Solar Co.,Ltd | HEBP48114U240-Pro {208V} | Y | Y | N | N | N | N | N | N | 10.4 kW, 208 Vac, Grid Support Utility Interactive Inverter | 10.009 | 208 | 97 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73 |  |  | 275 | 362.5 | 450 | 1.0009 | 2.0018 | 3.0027 | 5.0045 | 7.5067 | 10.009 | 94.448 | 95.466 | 96.09 | 96.296 | 97.494 | 95.424 | 96.7472 | 94.858 | 96.006 | 96.29 | 96.748 | 97.216 | 95.398 | 96.7609 | 95.01 | 96.252 | 96.378 | 96.514 | 97.308 | 95.266 | 96.7828 | 2025-06-23
SRNE Solar Co.,Ltd | HESP48120U200-H {208V} | Y | Y | N | N | N | N | N | N | 12 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.397 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.04 | 2.079 | 3.119 | 5.199 | 7.798 | 10.397 | 95.11 | 95.71 | 96.53 | 96.55 | 96.71 | 95.27 | 96.47 | 95.33 | 96.1 | 96.62 | 96.92 | 97.48 | 95.26 | 96.99 | 95.04 | 95.77 | 96.6 | 96.55 | 96.67 | 95.19 | 96.45 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-12K-UP {208V} | Y | Y | N | N | N | N | N | N | 12 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.397 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.04 | 2.079 | 3.119 | 5.199 | 7.798 | 10.397 | 95.11 | 95.71 | 96.53 | 96.55 | 96.71 | 95.27 | 96.47 | 95.33 | 96.1 | 96.62 | 96.92 | 97.48 | 95.26 | 96.99 | 95.04 | 95.77 | 96.6 | 96.55 | 96.67 | 95.19 | 96.45 | 2024-03-11
SRNE Solar Co.,Ltd | HEBP48120U240-Pro {208V} | Y | Y | N | N | N | N | N | N | 10.4 kW, 208 Vac, Grid Support Utility Interactive Inverter | 10.3972 | 208 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.0397 | 2.0794 | 3.1192 | 5.1986 | 7.7979 | 10.3972 | 95.11 | 95.714 | 96.534 | 96.55 | 96.714 | 95.27 | 96.4716 | 95.33 | 96.102 | 96.616 | 96.924 | 97.478 | 95.264 | 96.9928 | 95.036 | 95.774 | 96.604 | 96.55 | 96.668 | 95.186 | 96.4515 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-12K-UPRO {208V} | Y | Y | N | N | N | N | N | N | 10.4 kW, 208 Vac, Grid Support Utility Interactive Inverter | 10.3972 | 208 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.0397 | 2.0794 | 3.1192 | 5.1986 | 7.7979 | 10.3972 | 95.11 | 95.714 | 96.534 | 96.55 | 96.714 | 95.27 | 96.4716 | 95.33 | 96.102 | 96.616 | 96.924 | 97.478 | 95.264 | 96.9928 | 95.036 | 95.774 | 96.604 | 96.55 | 96.668 | 95.186 | 96.4515 | 2025-06-23
SRNE Solar Co.,Ltd | HEBP48120U240-Pro {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac, Grid Support Utility Interactive Inverter | 11.9957 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.1996 | 2.3991 | 3.5987 | 5.9979 | 8.9968 | 11.9957 | 95.452 | 95.688 | 96.376 | 96.392 | 96.504 | 95.226 | 96.3183 | 95.568 | 96.168 | 96.69 | 96.874 | 97.428 | 95.228 | 96.9757 | 95.526 | 95.868 | 96.596 | 96.456 | 96.536 | 95.324 | 96.392 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-12K-UPRO {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac, Grid Support Utility Interactive Inverter | 11.9957 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.1996 | 2.3991 | 3.5987 | 5.9979 | 8.9968 | 11.9957 | 95.452 | 95.688 | 96.376 | 96.392 | 96.504 | 95.226 | 96.3183 | 95.568 | 96.168 | 96.69 | 96.874 | 97.428 | 95.228 | 96.9757 | 95.526 | 95.868 | 96.596 | 96.456 | 96.536 | 95.324 | 96.392 | 2025-06-23
SRNE Solar Co.,Ltd | HESP48120U200-H {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 11.996 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.2 | 2.399 | 3.599 | 5.998 | 8.997 | 11.996 | 95.45 | 95.69 | 96.38 | 96.39 | 96.5 | 95.23 | 96.32 | 95.57 | 96.17 | 96.69 | 96.87 | 97.43 | 95.23 | 96.98 | 95.53 | 95.87 | 96.6 | 96.46 | 96.54 | 95.32 | 96.39 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-12K-UP {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 11.996 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.2 | 2.399 | 3.599 | 5.998 | 8.997 | 11.996 | 95.45 | 95.69 | 96.38 | 96.39 | 96.5 | 95.23 | 96.32 | 95.57 | 96.17 | 96.69 | 96.87 | 97.43 | 95.23 | 96.98 | 95.53 | 95.87 | 96.6 | 96.46 | 96.54 | 95.32 | 96.39 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-14K-U3P {208V} | Y | Y | N | N | N | N | N |  | 14 kW, 208 Vac Grid Support Utility Interactive Inverter | 14.0494 | 208 | 96.5 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.17 |  |  | 135 | 330 | 500 | 1.4049 | 2.8099 | 4.2148 | 7.0247 | 10.5371 | 14.0494 | 90.7592 | 94.8305 | 96.3293 | 96.9509 | 96.4563 | 94.4185 | 96.1338 | 91.2047 | 95.1283 | 96.8233 | 97.229 | 97.5506 | 97.0686 | 96.9967 | 93.7014 | 96.4506 | 96.8803 | 97.3064 | 97.0258 | 96.7317 | 96.8909 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HESP48140UH3 {208V} | Y | Y | N | N | N | N | N |  | 14 kW, 208 Vac Grid Support Utility Interactive Inverter | 14.0776 | 208 | 96.5 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.25 |  |  | 135 | 330 | 500 | 1.4078 | 2.8155 | 4.2233 | 7.0388 | 10.5582 | 14.0776 | 90.7593 | 94.8303 | 96.3294 | 96.9509 | 96.4563 | 94.4184 | 96.1338 | 91.2045 | 95.1283 | 96.8233 | 97.229 | 97.5506 | 97.0686 | 96.9967 | 93.2023 | 96.184 | 96.8767 | 97.2949 | 97.1327 | 96.7992 | 96.9147 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48150U320-H {208V} | Y | Y | N | N | N | N | N |  | 15 kW, 208 Vac Grid Support Utility Interactive Inverter | 14.3465 | 208 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.2 |  |  | 135 | 330 | 500 | 1.4347 | 2.8693 | 4.304 | 7.1733 | 10.7599 | 14.3465 | 92.8428 | 95.1741 | 95.8783 | 95.9649 | 96.6641 | 96.1379 | 96.1693 | 94.6874 | 96.3353 | 96.7393 | 96.8266 | 96.585 | 95.2127 | 96.4973 | 95.0317 | 96.4069 | 96.6815 | 96.6871 | 96.3717 | 95.8276 | 96.3961 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-15K-UBP {208V} | Y | Y | N | N | N | N | N |  | 15 kW, 208 Vac Grid Support Utility Interactive Inverter | 14.3489 | 208 | 97 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.4 |  |  | 135 | 330 | 500 | 1.4349 | 2.8698 | 4.3047 | 7.1744 | 10.7617 | 14.3489 | 92.75 | 95.0789 | 95.7825 | 95.8689 | 96.5675 | 96.0418 | 96.0731 | 94.7822 | 96.4317 | 96.8362 | 96.9235 | 96.6817 | 95.1175 | 96.5843 | 96.6056 | 97.9388 | 98.2142 | 98.0917 | 97.7736 | 95.7317 | 97.7527 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48150U320-H {240V} | Y | Y | N | N | N | N | N |  | 15 kW, 240 Vac Grid Support Utility Interactive Inverter | 14.72 | 240 | 96 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 30.7 |  |  | 135 | 330 | 500 | 1.472 | 2.944 | 4.416 | 7.36 | 11.04 | 14.72 | 92.7794 | 94.9734 | 95.6173 | 95.7338 | 96.3459 | 96.0725 | 95.9049 | 93.2574 | 94.7699 | 95.3153 | 95.5413 | 95.5009 | 95.2129 | 95.3464 | 94.8106 | 95.9755 | 96.2892 | 96.3862 | 96.0842 | 95.8115 | 96.1022 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-15K-UBP {240V} | Y | Y | N | N | N | N | N |  | 15 kW, 240 Vac Grid Support Utility Interactive Inverter | 14.72 | 240 | 96 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 30.7 |  |  | 135 | 330 | 500 | 1.472 | 2.944 | 4.416 | 7.36 | 11.04 | 14.72 | 92.7794 | 94.9734 | 95.6173 | 95.7338 | 96.3459 | 96.0725 | 95.9049 | 93.2574 | 94.7699 | 95.3153 | 95.5413 | 95.5009 | 95.2129 | 95.3464 | 94.8106 | 95.9755 | 96.2892 | 96.3862 | 96.0842 | 95.8115 | 96.1022 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48160U340-H {208V} | Y | Y | N | N | N | N | N |  | 16 kW, 208 Vac Grid Support Utility Interactive Inverter | 15.2514 | 208 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.3 |  |  | 150 | 330 | 500 | 1.5251 | 3.0503 | 4.5754 | 7.6257 | 11.4385 | 15.2514 | 92.9262 | 95.2756 | 95.9085 | 95.9546 | 96.3526 | 96.1306 | 96.0137 | 94.1462 | 95.758 | 96.2135 | 96.5445 | 96.5139 | 96.2114 | 96.3366 | 95.6495 | 96.9287 | 97.3307 | 97.243 | 97.0512 | 96.7694 | 97.0487 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-16K-UBP {208V} | Y | Y | N | N | N | N | N |  | 16 kW, 208 Vac Grid Support Utility Interactive Inverter | 15.2564 | 208 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.2 |  |  | 150 | 330 | 500 | 1.5256 | 3.0513 | 4.5769 | 7.6282 | 11.4423 | 15.2564 | 92.8333 | 95.1803 | 95.8126 | 95.8587 | 96.2562 | 96.0345 | 95.9177 | 94.0521 | 95.6623 | 96.1173 | 96.4479 | 96.4174 | 96.1152 | 96.2403 | 95.5539 | 96.8317 | 97.2334 | 97.1457 | 96.9541 | 96.6726 | 96.9517 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48160U340-H {240V} | Y | Y | N | N | N | N | N |  | 16 kW, 240 Vac Grid Support Utility Interactive Inverter | 16.0066 | 240 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 30.7 |  |  | 150 | 330 | 500 | 1.6007 | 3.2013 | 4.802 | 8.0033 | 12.005 | 16.0066 | 92.7875 | 95.0323 | 95.7511 | 95.7573 | 96.1756 | 95.9166 | 95.8312 | 94.1692 | 95.7223 | 96.2244 | 96.5323 | 96.4723 | 96.2198 | 96.3129 | 95.7303 | 96.9006 | 97.338 | 97.2328 | 97.0333 | 96.8243 | 97.0426 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-16K-UBP {240V} | Y | Y | N | N | N | N | N |  | 16 kW, 240 Vac Grid Support Utility Interactive Inverter | 16.0066 | 240 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 30.7 |  |  | 150 | 330 | 500 | 1.6007 | 3.2013 | 4.802 | 8.0033 | 12.005 | 16.0066 | 92.7875 | 95.0323 | 95.7511 | 95.7573 | 96.1756 | 95.9166 | 95.8312 | 94.1692 | 95.7223 | 96.2244 | 96.5323 | 96.4723 | 96.2198 | 96.3129 | 95.7303 | 96.9006 | 97.338 | 97.2328 | 97.0333 | 96.8243 | 97.0426 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-16K-U3P {208V} | Y | Y | N | N | N | N | N |  | 16 kW, 208 Vac Grid Support Utility Interactive Inverter | 16.0641 | 208 | 97 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.19 |  |  | 150 | 330 | 500 | 1.6064 | 3.2128 | 4.8192 | 8.0321 | 12.0481 | 16.0641 | 92.6948 | 95.5918 | 96.6001 | 97.0214 | 97.164 | 96.6119 | 96.7814 | 91.4358 | 94.6242 | 96.7517 | 97.4231 | 97.2836 | 96.827 | 96.8593 | 94.6103 | 96.5373 | 97.1228 | 97.4928 | 97.1187 | 96.8162 | 97.0532 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HESP48160UH3 {208V} | Y | Y | N | N | N | N | N |  | 16 kW, 208 Vac Grid Support Utility Interactive Inverter | 16.0963 | 208 | 97 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.26 |  |  | 150 | 330 | 500 | 1.6096 | 3.2193 | 4.8289 | 8.0481 | 12.0722 | 16.0963 | 92.6949 | 95.5917 | 96.6001 | 97.0216 | 97.164 | 96.6114 | 96.7814 | 91.4358 | 94.6242 | 96.7517 | 97.4232 | 97.2835 | 96.827 | 96.8593 | 94.6086 | 96.537 | 97.1227 | 97.4928 | 97.1187 | 96.8162 | 97.0531 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48180U380-H {208V} | Y | Y | N | N | N | N | N |  | 18 kW, 208 Vac Grid Support Utility Interactive Inverter | 17.0533 | 208 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.3 |  |  | 160 | 330 | 500 | 1.7053 | 3.4107 | 5.116 | 8.5267 | 12.79 | 17.0533 | 93.161 | 95.3666 | 96.0198 | 96.1669 | 95.8692 | 95.3463 | 95.7902 | 94.9542 | 96.6859 | 97.0572 | 97.2953 | 97.0991 | 96.7228 | 97.01 | 95.6412 | 96.9487 | 97.2956 | 97.2485 | 96.718 | 96.692 | 96.8659 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-18K-UBP {208V} | Y | Y | N | N | N | N | N |  | 18 kW, 208 Vac Grid Support Utility Interactive Inverter | 17.0558 | 208 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.4 |  |  | 160 | 330 | 500 | 1.7056 | 3.4112 | 5.1167 | 8.5279 | 12.7918 | 17.0558 | 93.0907 | 95.2806 | 95.9282 | 96.2794 | 95.7305 | 95.2509 | 95.7174 | 94.7822 | 96.4317 | 96.8362 | 96.9235 | 96.6817 | 96.6261 | 96.6598 | 96.6056 | 97.9388 | 98.2142 | 98.0917 | 97.7736 | 96.5954 | 97.7959 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48180U380-H {240V} | Y | Y | N | N | N | N | N |  | 18 kW, 240 Vac Grid Support Utility Interactive Inverter | 17.944 | 240 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 35.6 |  |  | 160 | 330 | 500 | 1.7944 | 3.5888 | 5.3832 | 8.972 | 13.458 | 17.944 | 93.1331 | 95.349 | 96.0269 | 96.2345 | 95.9259 | 95.4615 | 95.8391 | 94.8594 | 96.478 | 96.848 | 97.1595 | 97.1259 | 96.8312 | 96.9618 | 95.7636 | 96.9224 | 97.2501 | 97.2045 | 97.0659 | 96.6714 | 97.0381 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-18K-UBP {240V} | Y | Y | N | N | N | N | N |  | 18 kW, 240 Vac Grid Support Utility Interactive Inverter | 17.944 | 240 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 30.7 |  |  | 160 | 330 | 500 | 1.7944 | 3.5888 | 5.3832 | 8.972 | 13.458 | 17.944 | 93.1331 | 95.349 | 96.0269 | 96.2345 | 95.9259 | 95.4615 | 95.8391 | 94.8594 | 96.478 | 96.848 | 97.1595 | 97.1259 | 96.8312 | 96.9618 | 95.7636 | 96.9224 | 97.2501 | 97.2045 | 97.0659 | 96.6714 | 97.0381 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-18K-U3P {208V} | Y | Y | N | N | N | N | N |  | 18 kW, 208 Vac Grid Support Utility Interactive Inverter | 18.1348 | 208 | 97 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.19 |  |  | 160 | 330 | 500 | 1.8135 | 3.627 | 5.4405 | 9.0674 | 13.6011 | 18.1348 | 91.7859 | 95.455 | 96.451 | 96.7238 | 97.2908 | 96.939 | 96.7414 | 92.6187 | 95.4457 | 96.4775 | 97.2559 | 97.4663 | 97.102 | 96.9903 | 94.4793 | 96.7393 | 97.3627 | 97.561 | 97.4288 | 96.9581 | 97.2726 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HESP48180UH3 {208V} | Y | Y | N | N | N | N | N |  | 18 kW, 208 Vac Grid Support Utility Interactive Inverter | 18.1711 | 208 | 97 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.27 |  |  | 160 | 330 | 500 | 1.8171 | 3.6342 | 5.4513 | 9.0856 | 13.6284 | 18.1711 | 91.7861 | 95.4552 | 96.451 | 96.7238 | 97.2908 | 96.8162 | 96.7353 | 92.6187 | 95.4457 | 96.4776 | 97.2558 | 97.4663 | 97.102 | 96.9903 | 94.4812 | 96.7399 | 97.3627 | 97.561 | 97.4287 | 96.9581 | 97.2727 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Star Charge Americas Corp. | SI403LULA00 {208V} | Y | Y | N | N | N | N | Y* | Y | 3.3 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 3.315 | 208 | 97 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 19.05 |  |  | 180 | 360 | 480 | 0.332 | 0.663 | 0.995 | 1.658 | 2.487 | 3.315 | 93.55 | 95.65 | 96.44 | 96.92 | 97.03 | 96.92 | 96.72 | 93.35 | 96.57 | 97.23 | 97.73 | 97.75 | 97.67 | 97.45 | 91.22 | 95.28 | 96.58 | 97.5 | 97.69 | 97.64 | 97.13 | 2025-02-21 | 2025-05-21
Star Charge Americas Corp. | SI403LULA00 {240V} | Y | Y | N | N | N | N | Y* | Y | 3.8 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 3.811 | 240 | 96 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 6.32 |  |  | 180 | 360 | 480 | 0.381 | 0.762 | 1.143 | 1.906 | 2.858 | 3.811 | 89.26 | 93.78 | 94.99 | 96.03 | 96.47 | 96.5 | 95.78 | 88.92 | 94.16 | 95.63 | 96.76 | 97.18 | 97.31 | 96.43 | 86.74 | 92.94 | 94.96 | 96.5 | 97.09 | 97.27 | 96.1 | 2025-02-21 | 2025-05-21
Star Charge Americas Corp. | SI803LULA00 {208V} | Y | Y | N | N | N | N | Y* | Y | 6.6 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 6.635 | 208 | 97.5 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 6.635 |  |  | 260 | 360 | 480 | 0.664 | 1.327 | 1.991 | 3.318 | 4.976 | 6.635 | 96.26 | 97.26 | 97.33 | 97.31 | 97 | 96.55 | 97.07 | 96.46 | 97.57 | 97.76 | 97.65 | 97.36 | 96.97 | 97.42 | 95.17 | 97.16 | 97.6 | 97.62 | 97.36 | 96.98 | 97.33 | 2025-02-21 | 2025-05-21
Star Charge Americas Corp. | SI803LULA00 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 7.641 | 240 | 97 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 6.25 |  |  | 260 | 360 | 480 | 0.764 | 1.528 | 2.292 | 3.82 | 5.73 | 7.641 | 94.03 | 96.04 | 96.62 | 96.96 | 96.8 | 96.5 | 96.65 | 94.02 | 96.36 | 97 | 97.3 | 97.17 | 96.96 | 97 | 92.82 | 95.95 | 96.82 | 97.26 | 97.18 | 97 | 96.91 | 2025-02-21 | 2025-05-21
Star Charge Americas Corp. | SI104LULA00 {208V} | Y | Y | N | N | N | N | Y* | Y | 8.3 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 8.304 | 208 | 97 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 19 |  |  | 320 | 360 | 480 | 0.83 | 1.661 | 2.491 | 4.152 | 6.228 | 8.304 | 96.98 | 97.55 | 97.62 | 97.4 | 96.91 | 96.43 | 97.11 | 96.72 | 97.65 | 97.7 | 97.48 | 97.01 | 96.55 | 97.19 | 95.87 | 97.41 | 97.62 | 97.47 | 97.02 | 96.57 | 97.14 | 2025-02-21 | 2025-05-21
Star Charge Americas Corp. | SI104LULA00 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.5 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 9.582 | 240 | 97 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 6.26 |  |  | 320 | 360 | 480 | 0.958 | 1.916 | 2.875 | 4.791 | 7.187 | 9.582 | 94.99 | 96.65 | 97.09 | 97.18 | 96.9 | 96.54 | 96.87 | 94.88 | 96.75 | 97.17 | 97.26 | 97 | 96.67 | 96.96 | 94.07 | 96.48 | 97.07 | 97.26 | 97.04 | 96.72 | 96.93 | 2025-02-21 | 2025-05-21
Sun Gold Power Inc | SGN7.6K1HB-48 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 7.6472 | 240 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.76472 | 1.5294 | 2.2942 | 3.8236 | 5.7354 | 7.6472 | 92.9526 | 95.5516 | 96.215 | 96.6536 | 96.4528 | 96.189 | 96.2682 | 89.7494 | 96.0782 | 96.7932 | 97.1622 | 96.9742 | 96.771 | 96.648 | 94.069 | 96.2392 | 96.7722 | 97.1198 | 96.913 | 96.6498 | 96.7789 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGN7.6K1HB-48 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 7.648 | 208 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.736 | 7.648 | 92.946 | 95.544 | 96.21 | 96.648 | 96.448 | 96.186 | 96.2631 | 93.74 | 96.074 | 96.788 | 97.158 | 96.97 | 96.766 | 96.8034 | 94.064 | 96.234 | 96.766 | 97.116 | 96.906 | 96.704 | 96.7759 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGS-8K12MAX {208V} | Y | Y | N | N | N | N | N |  | 8.8 kW, 208 Vac Grid Support Utility Interactive Inverter | 8.81 | 208 | 96.5 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.88085 | 1.7617 | 2.6426 | 4.4043 | 6.6064 | 8.8085 | 94.444 | 95.624 | 96.816 | 96.49 | 97.126 | 95.666 | 96.6999 | 94.382 | 95.75 | 96.022 | 96.526 | 97.2 | 95.958 | 96.6698 | 93.96 | 94.784 | 96.388 | 96.654 | 96.84 | 95.102 | 96.4418 | 2025-09-22
Sun Gold Power Inc | SGS-8K12MAX {240V} | Y | Y | N | N | N | N | N |  | 8.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 8.81 | 240 | 96.5 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.881 | 1.762 | 2.643 | 4.405 | 6.607 | 8.81 | 94.27 | 95.42 | 96.78 | 96.33 | 97.1 | 95.65 | 96.63 | 93.65 | 95.69 | 96.64 | 96.47 | 97.23 | 96.2 | 96.73 | 94 | 95.68 | 96.7 | 96.35 | 96.55 | 95.56 | 96.33 | 2025-09-22
Sun Gold Power Inc | SGS-10K15MAX {208V} | Y | Y | N | N | N | N | N |  | 10 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.01 | 208 | 97 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 73 |  |  | 275 | 362.5 | 450 | 1.0009 | 2.0018 | 3.0027 | 5.0045 | 7.5067 | 10.009 | 94.448 | 95.466 | 96.09 | 96.296 | 97.494 | 95.424 | 96.7472 | 94.858 | 96.006 | 96.29 | 96.748 | 97.216 | 95.398 | 96.7609 | 95.01 | 96.252 | 96.378 | 96.514 | 97.308 | 95.266 | 96.7828 | 2025-09-22
Sun Gold Power Inc | SGS-10K15MAX {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.01 | 240 | 96.5 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 73.7 |  |  | 275 | 362.5 | 450 | 1.0008 | 2.0016 | 3.0025 | 5.0041 | 7.5062 | 10.0082 | 94.646 | 95.758 | 95.334 | 96.51 | 97.434 | 95.878 | 96.7148 | 94.21 | 94.914 | 95.268 | 96.412 | 97.364 | 95.408 | 96.5661 | 94.976 | 94.772 | 95.296 | 96.478 | 97.2 | 95.4 | 96.5195 | 2025-09-22
Sun Gold Power Inc | SGN11.4KHB-48 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 10.1396 | 240 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.0279 | 3.0419 | 5.0698 | 7.6047 | 10.1396 | 93.0477 | 95.5809 | 96.2415 | 96.6629 | 96.4516 | 96.2021 | 96.2786 | 93.7158 | 96.0665 | 96.8163 | 97.1487 | 96.9642 | 96.7822 | 96.8013 | 94.0472 | 96.2511 | 96.7916 | 97.1155 | 96.9244 | 96.6588 | 96.7866 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGN10KHB-48 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 10.1472 | 240 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.0147 | 2.0294 | 3.0442 | 5.0736 | 7.6104 | 10.1472 | 92.9963 | 95.5759 | 96.2237 | 96.6613 | 96.4562 | 96.1983 | 96.2761 | 93.7907 | 96.1027 | 96.8102 | 97.1618 | 96.9743 | 96.7739 | 96.8131 | 94.1119 | 96.2672 | 96.7835 | 97.1258 | 96.9159 | 96.6586 | 96.7866 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGN10KHB-48 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 10.1858 | 208 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.0186 | 2.0372 | 3.0557 | 5.0929 | 7.6393 | 10.1858 | 92.8933 | 95.4787 | 96.1281 | 96.5592 | 96.3579 | 96.0975 | 96.177 | 93.6955 | 96.0051 | 96.7063 | 97.0717 | 96.8789 | 96.675 | 96.7174 | 94.0173 | 96.1625 | 96.6817 | 96.9927 | 96.8158 | 96.5601 | 96.6795 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGN11.4KHB-48 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 10.1858 | 208 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.0186 | 2.0372 | 3.0557 | 5.0929 | 7.6393 | 10.1858 | 92.9095 | 95.4795 | 96.1203 | 96.5624 | 96.3577 | 96.1012 | 96.1775 | 93.6611 | 96.0245 | 96.7245 | 97.0669 | 96.879 | 96.6799 | 96.7185 | 94.0672 | 96.1747 | 96.6706 | 96.9939 | 96.8177 | 96.5602 | 96.682 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGS-12K18MAX {208V} | Y | Y | N | N | N | N | N |  | 12 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.4 | 208 | 96.5 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.0397 | 2.0794 | 3.1192 | 5.1986 | 7.7979 | 10.3972 | 95.11 | 95.714 | 96.534 | 96.55 | 96.714 | 95.27 | 96.4716 | 95.33 | 96.102 | 96.616 | 96.924 | 97.478 | 95.264 | 96.9928 | 95.036 | 95.774 | 96.604 | 96.55 | 96.668 | 95.186 | 96.4515 | 2025-09-22
Sun Gold Power Inc | SGN-11K15PRO {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 11.5669 | 240 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2025-06-17 |  |  | N | N | 19 |  |  | 200 | 360 | 480 | 1.1567 | 2.3134 | 3.4701 | 5.7834 | 8.6752 | 11.5669 | 93.0675 | 95.5749 | 96.2997 | 96.6409 | 96.4392 | 96.2088 | 96.2752 | 93.6781 | 96.0439 | 96.7972 | 97.1353 | 96.9536 | 96.7793 | 96.7878 | 94.0465 | 96.3229 | 96.8228 | 97.1182 | 96.9286 | 96.6545 | 96.7965 | 2025-09-02
Sun Gold Power Inc | SGN-11K15PRO {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 11.6088 | 208 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2025-06-17 |  |  | N | N | 19 |  |  | 200 | 360 | 480 | 1.1609 | 2.3218 | 3.4827 | 5.8044 | 8.7066 | 11.6088 | 92.8881 | 95.4935 | 96.1138 | 96.5693 | 96.353 | 96.1025 | 96.1756 | 93.6426 | 96.0296 | 96.7159 | 97.0645 | 96.8809 | 96.677 | 96.7174 | 94.0961 | 96.1711 | 96.6734 | 96.9968 | 96.8241 | 96.5565 | 96.6871 | 2025-09-02
Sun Gold Power Inc | SGS-12K18MAX {240V} | Y | Y | N | N | N | N | N |  | 12 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.99 | 240 | 96.5 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.1996 | 2.3991 | 3.5987 | 5.9979 | 8.9968 | 11.9957 | 95.452 | 95.688 | 96.376 | 96.392 | 96.504 | 95.226 | 96.3183 | 95.568 | 96.168 | 96.69 | 96.874 | 97.428 | 95.228 | 96.9757 | 95.526 | 95.868 | 96.596 | 96.456 | 96.536 | 95.324 | 96.392 | 2025-09-22
Sungrow | SG36CX-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 36 kVA, 480 Vac Grid Support Utility Interactive Inverter | 36.046 | 480 | 98 | CSA Group | [10/14/2022] | CSA Group | [09/30/2020] | [MDSP_AGATE-S_V11_V01_A] | 2020-12-21 | [09/30/2020] | 2020-12-21 | CSA Group | 2020-09-15 | 2020-12-21 |  | N | N | 3.7 |  |  | 550 | 710 | 850 | 3.6046 | 7.2093 | 10.8139 | 18.0232 | 27.0347 | 36.0463 | 96.1175 | 97.2055 | 97.5335 | 97.7479 | 97.742 | 97.5065 | 97.6147 | 97.1732 | 98.2799 | 98.5254 | 98.5967 | 98.521 | 98.2451 | 98.4577 | 96.4094 | 97.7387 | 98.065 | 98.2558 | 98.2296 | 98.1549 | 98.1143 | 2020-12-21 | 2024-09-23
Sungrow | SG60CX-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 60 kVA, 480 Vac Grid Support Utility Interactive Inverter | 60.182 | 480 | 98 | CSA Group | [10/14/2022] | CSA Group | [09/30/2020] | [MDSP_AGATE-S_V11_V01_A] | 2020-12-21 | [09/30/2020] | 2020-12-21 | CSA Group | 2020-09-15 | 2020-12-21 |  | N | N | 3.38 |  |  | 550 | 710 | 850 | 6.0182 | 12.0363 | 18.0545 | 30.0908 | 45.1361 | 60.1815 | 96.9202 | 97.6109 | 97.7932 | 97.9095 | 97.8059 | 97.5258 | 97.7669 | 98.1961 | 98.7137 | 98.8428 | 98.8099 | 98.6523 | 98.2665 | 98.6738 | 97.4526 | 98.1491 | 98.2803 | 98.3385 | 98.2104 | 98.0212 | 98.2029 | 2020-12-21 | 2024-09-23
Sungrow Power Supply Co., Ltd. | SG60KU-M {480V} | N | N | Y | Y | Y | N | N | N | 60 kW, 480 Vac transformerless Grid Support Utility Interactive Inverter | 60 | 480 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [07/07/2017];[05/13/2019] | [DSP_SG60KU-M_V14_A];[DSP_SG60KU-M_V14_B] | 2018-10-15 | [05/13/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 0.88 |  |  | 550 | 700 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 97.8 | 98.2 | 98.2 | 98.4 | 98.4 | 98 | 98.3 | 97.8 | 98.6 | 98.8 | 98.9 | 98.7 | 98.5 | 98.7 | 97.5 | 98.6 | 98.5 | 98.8 | 98.5 | 98.4 | 98.5 | 2017-11-15 | 2019-06-03
Sungrow Power Supply Co., Ltd. | SG125HV {600V} | N | N | Y | Y | Y | Y | Y* | Y | 125 kW, 600 Vac transformerless Grid Support Utility Interactive Inverter. | 125 | 600 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [07/07/2017];[05/13/2019] | [DSP_SG125KHV_V11_A];[DSP_SG125KHV_V11_B] | 2018-10-15 | [05/13/2019] | 2022-01-21 | CSA Group | 2021-09-26 | 2022-01-21 |  | N | N | 5.59 |  |  | 860 | 945 | 1200 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 98.5862 | 98.8265 | 98.8829 | 98.6821 | 98.4462 | 98.2555 | 98.5632 | 98.2896 | 98.5839 | 98.589 | 98.4937 | 98.3596 | 98.1057 | 98.411 | 98.0848 | 98.4261 | 98.4778 | 98.3839 | 98.0971 | 97.6269 | 98.1955 | 2017-11-01 | 2022-01-21
Sungrow Power Supply Co., Ltd. | SG200HX-US {600V} | N | Y | N | N | N | N | Y* | Y | 200 kW, 600 Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 200.444 | 600 | 98.5 | CSA Group | [6/21/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-06-28 | 2024-01-02 |  | N | N | 4.54 |  |  | 850 | 1000 | 1300 | 20.044 | 40.089 | 60.133 | 100.222 | 150.333 | 200.444 | 97.42 | 98.23 | 98.45 | 98.5 | 98.35 | 98.16 | 98.34 | 98.06 | 98.53 | 98.61 | 98.65 | 98.52 | 98.33 | 98.53 | 97.56 | 98.31 | 98.49 | 98.52 | 98.42 | 98.19 | 98.4 | 2024-01-22
Sungrow Power Supply Co., Ltd. | SG250HX-US {800V} | Y | N | Y | Y | Y | Y | Y* | Y | 250 kW, 800 Vac, 3-phase, Transformerless Grid Support Utility Interactive Battery and Solar Inverter | 226.997 | 800 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [08/04/2020] | [MDSP_DIAMOND-S_V11_V01_A] | 2020-09-21 | [08/04/2020] | 2021-02-22 | CSA Group | 2020-12-07 | 2021-02-22 |  | N | N | 5.21 |  |  | 860 | 1080 | 1300 | 22.6997 | 45.3994 | 68.0992 | 113.4986 | 170.2479 | 226.9972 | 97.0577 | 98.2506 | 98.469 | 98.5708 | 98.4621 | 98.262 | 98.409 | 98.195 | 98.7627 | 98.9461 | 99.0101 | 98.869 | 98.6779 | 98.8661 | 97.9983 | 98.6612 | 98.8997 | 98.9478 | 98.8178 | 98.632 | 98.805 | 2020-09-21 | 2021-02-22
Sungrow Power Supply Co., Ltd. | SG350HX-US {800V} | N | Y | N | N | N | N | Y* | Y | 350 kW, 800 Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 320.865 | 800 | 98.5 | CSA Group | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-05-08 | 2023-11-21 |  | N | N | 4.83 |  |  | 860 | 1180 | 1330 | 32.086 | 64.173 | 96.259 | 160.432 | 240.649 | 320.865 | 97.31 | 98.17 | 98.3 | 98.33 | 98.22 | 97.97 | 98.2 | 98.36 | 98.84 | 98.88 | 98.82 | 98.62 | 98.4 | 98.68 | 98.06 | 98.67 | 98.75 | 98.71 | 98.53 | 98.33 | 98.57 | 2023-11-21 | 2024-01-02
Sungrow Power Supply Co., Ltd. | SC1000KU {540V} | Y | N | Y | Y | N | N | N | N | 1000 kW, 540 Vac Grid Support Utility Interactive Storage Inverter, bi-directional for use with battery management system, intended to be used in conjunction with a 1000 KVA (min) rated isolation transformer | 1001.306 | 540 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [09/19/2019] | [DSP_SC1000KU_V1_B_M] | 2019-02-01 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 1 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216. | N | N | 83.7646 |  |  | 810 | 1005 | 1200 | 100.1306 | 200.2612 | 300.3918 | 500.653 | 750.9795 | 1001.306 | 94.9956 | 96.8144 | 97.2437 | 97.3155 | 97.0286 | 96.6633 | 97.0044 | 94.2811 | 96.3444 | 96.9047 | 97.0479 | 96.8017 | 96.439 | 96.7239 | 93.6894 | 95.9275 | 96.5802 | 96.8324 | 96.5978 | 96.1882 | 96.4746 | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG3150UD-MV-US {600V} | Y | Y | N | N | N | N | Y* | Y | 3150 kW, 600 Vac Hybrid Grid Support Utility Interactive Inverter connects to the grid via a 3150 kVA medium voltage transformer. (Made up of three SG1050UD-US installed together, each rated max output power = 1053). | 1053 | 600 | 97.5 | SGS | [6/15/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-05-17 | 2024-04-02 | Submitted performance data is the same as SG1050UD-US. Efficiency data inclusive of transformer effect based on Medium-Voltage Transformers DOE Table. | N | N | 124.76 |  |  | 875 | 1100 | 1438 | 105.344 | 210.687 | 316.031 | 526.718 | 790.078 | 1053.437 | 96.97 | 97.92 | 98.13 | 97.99 | 97.64 | 97.04 | 97.73 | 96.68 | 97.88 | 98 | 97.89 | 97.6 | 97 | 97.65 | 96.14 | 97.57 | 97.82 | 97.74 | 97.47 | 96.9 | 97.49 | 2024-04-02 | 2024-04-11
Sungrow Power Supply Co., Ltd. | SG4400UD-MV-US {645V} | Y | Y | N | N | N | N | Y* | Y | 4400 kW, 645 Vac Hybrid Grid Support Utility Interactive Inverter connects to the grid via a 4400 kVA medium voltage transformer. (Made up of four SG1100UD-US installed together, each rated max output power = 1103). | 1103 | 645 | 97.5 | SGS | [6/15/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-05-17 | 2024-04-02 | Submitted performance data is the same as SG1100UD-US. Efficiency data inclusive of transformer effect based on Medium-Voltage Transformers DOE Table. | N | N | 128.74 |  |  | 915 | 1100 | 1449 | 110.306 | 220.612 | 330.918 | 551.529 | 827.294 | 1103.059 | 97 | 97.92 | 98.2 | 98.07 | 97.75 | 97.17 | 97.82 | 96.83 | 97.89 | 98.13 | 97.99 | 97.68 | 97.11 | 97.75 | 96.5 | 97.57 | 97.81 | 97.82 | 97.53 | 96.98 | 97.56 | 2024-04-02 | 2024-04-11
Sungrow Power Supply Co., Ltd. | SG2500U {550V} | N | N | Y | Y | N | N | N | N | 2500kW, 550Vac Grid Support Utility Interactive Inverter connect to grid via a 2500kVA medium voltage transformer. | 2500 | 550 | 98 | No Information Submitted | No Information Submitted | CSA Group | [5/16/2017] | [DSP_SG2500U_V11_V1_A, LCD_SG2500U_V1_A_M] | 2018-10-15 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of ABB ZGSB-H-25/35. | N | N | 651.36 |  |  | 800 | 900 | 1200 | 250 | 500 | 750 | 1250 | 1875 | 2500 | 98 | 98.6 | 98.8 | 98.8 | 98.6 | 98.4 | 97.9 | 97.8 | 98.5 | 98.6 | 98.6 | 98.5 | 98.3 | 97.7 | 97.4 | 98.2 | 98.4 | 98.5 | 98.3 | 98.2 | 97.7 | 2018-02-01 | 2018-10-15
Sungrow Power Supply Co., Ltd. | SG3150U {630V} | N | N | Y | Y | Y | N | N | N | 3150 kW, 630 Vac Grid Support Utility Interactive Storage Inverter, intended to be used in conjunction with a 3150 KVA (min) rated medium voltage transformer | 3154.3 | 630 | 98 | No Information Submitted | No Information Submitted | CSA Group | [12/23/2019] | [DSP_AGATE-C_V1_B_Release20190522.02] | 2022-06-13 | [12/23/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 3150 kVA Medium-Voltage Dry-Type Distribution Transformers Table in DOE 216. | N | N | 270.2 |  |  | 915 | 1120 | 1300 | 315.43 | 630.86 | 946.29 | 1577.15 | 2365.725 | 3154.3 | 96.1785 | 97.5352 | 97.9133 | 97.999 | 97.8284 | 97.5643 | 97.7805 | 96.1278 | 97.5299 | 97.8921 | 97.9807 | 97.8081 | 97.5282 | 97.7593 | 95.7076 | 97.3019 | 97.7366 | 97.8261 | 97.6743 | 97.39 | 97.6021 | 2022-06-13
Sungrow Power Supply Co., Ltd. | SG3425UD {600V} | N | Y | Y | Y | Y | Y | N | N | 3425 kW, 600 Vac Grid Support Utility Interactive Inverter connect to grid via a 3425 kVA medium voltage transformer. | 3434.56 | 600 | 97.5 | SGS | [5/18/2022] | SGS | [02/05/2021] | [DSP_SG3425UD_V1_A, LCD_SG3425UD_V1_A] | 2022-01-21 | [02/05/2021] | 2022-01-21 | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of EagleRise 3425kVA Pad-Mount Medium Voltage Transformer. | N | N | 256.66 |  |  | 875 | 1100 | 1300 | 343.456 | 686.912 | 1030.368 | 1717.28 | 2575.92 | 3434.56 | 97.141 | 98.0424 | 98.2345 | 97.9826 | 97.7341 | 97.3307 | 97.8179 | 96.9657 | 97.9064 | 98.1324 | 97.8448 | 97.6246 | 97.2733 | 97.7019 | 96.8392 | 97.8406 | 98.0283 | 97.8177 | 97.5502 | 97.1864 | 97.6316 | 2022-01-21 | 2023-03-21
Sungrow Power Supply Co., Ltd. | SG3600UD {630V} | N | Y | Y | Y | Y | Y | N | N | 3600 kW, 630 Vac Grid Support Utility Interactive Inverter connect to grid via a 3600 kVA medium voltage transformer. | 3606.98 | 630 | 97.5 | SGS | [5/18/2022] | SGS | [02/05/2021] | [DSP_SG3600UD_V1_A, LCD_SG3600UD_V1_A] | 2022-01-21 | [02/05/2021] | 2022-01-21 | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of EagleRise 3600kVA Pad-Mount Medium Voltage Transformer. | N | N | 264.05 |  |  | 915 | 1100 | 1300 | 360.698 | 721.396 | 1082.094 | 1803.49 | 2705.235 | 3606.98 | 97.0283 | 97.9801 | 98.2175 | 97.9577 | 97.7225 | 97.3276 | 97.7966 | 96.8627 | 97.8875 | 98.1286 | 97.8907 | 97.6441 | 97.2582 | 97.7156 | 96.7288 | 97.7782 | 98.0431 | 97.8134 | 97.5748 | 97.2171 | 97.6396 | 2022-01-21 | 2023-03-21
SunPluto Energy Inc | SP-SHD-7.6kW {240V} | Y | Y | N | N | N | N | N |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.5716 | 240 | 97 | Intertek | [4/27/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.938 |  |  | 144 | 410 | 550 | 0.75716 | 1.5143 | 2.2715 | 3.7858 | 5.6787 | 7.5716 | 92.671 | 93.9896 | 96.2481 | 96.7433 | 97.2278 | 97.292 | 96.6675 | 93.4521 | 95.8866 | 96.6336 | 97.1282 | 97.4397 | 97.1679 | 97.0268 | 92.8839 | 93.7396 | 95.8119 | 96.6727 | 97.5145 | 97.4143 | 96.7545 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y | No Information Submitted | No Information Submitted
SunPluto Energy Inc | SP-SHD-9.6kW {240V} | Y | Y | N | N | N | N | N |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.6605 | 240 | 97 | Intertek | [4/27/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 11.042 |  |  | 180 | 410 | 550 | 0.96605 | 1.9321 | 2.8981 | 4.8302 | 7.2454 | 9.6605 | 95.0181 | 95.7295 | 96.3315 | 97.1202 | 97.4251 | 96.8625 | 97.0206 | 94.6952 | 96.336 | 96.9007 | 97.251 | 97.4323 | 97.0366 | 97.1463 | 93.2296 | 95.1704 | 96.2911 | 97.2355 | 97.5393 | 97.148 | 97.0153 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y | No Information Submitted | No Information Submitted
SunPluto Energy Inc | SP-SHD-11.4kW {240V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.2567 | 240 | 97 | Intertek | [4/27/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.379 |  |  | 210 | 410 | 550 | 1.1257 | 2.2513 | 3.377 | 5.6283 | 8.4425 | 11.2567 | 95.4762 | 96.2795 | 96.6426 | 97.2608 | 97.4924 | 96.3559 | 97.1437 | 95.0276 | 96.6282 | 97.1093 | 97.5876 | 97.296 | 96.8654 | 97.1892 | 93.3197 | 95.8013 | 96.6312 | 97.5435 | 97.358 | 96.479 | 97.0264 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y | No Information Submitted | No Information Submitted
SunPower | SPR-12000m-3 {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 12 kW, 480 Vac 3-phase, Grid Support Utility Interactive Inverter | 12 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 300 | 675 | 800 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 96.4293 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 97.6137 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898 | 97.8803 | 2017-09-01 | 2018-10-15
SunPower | SPR-12000m-3-H {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 12 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 12 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 300 | 675 | 800 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 96.4293 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 97.6137 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898 | 97.8803 | 2017-09-01 | 2018-10-15
SunPower | SPR-15000m-3 {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 15 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 15 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 300 | 675 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 96.448 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 97.694 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572 | 98.0267 | 2017-09-01 | 2018-10-15
SunPower | SPR-15000m-3-H {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 15 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 15 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 300 | 675 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 96.448 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 97.694 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572 | 98.0267 | 2017-09-01 | 2018-10-15
SunPower | SPR-20000m-3 {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 20 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 380 | 695 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 96.9173 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 98.0588 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422 | 98.0897 | 2017-09-01 | 2018-10-15
SunPower | SPR-20000m-3-H {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 20 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 380 | 695 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 96.9173 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 98.0588 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422 | 98.0897 | 2017-09-01 | 2018-10-15
SunPower | SPR-24000m-3 {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 24 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 24.06 | 480 | 98 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 450 | 712 | 800 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.1621 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 98.4117 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823 | 98.0569 | 2017-09-01 | 2018-10-15
SunPower | SPR-24000m-3-H {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US 24 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 24.06 | 480 | 98 | No Information Submitted | No Information Submitted | UL | [7/13/2017] | [2.03.04.R] | 2018-10-15 | [7/13/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.79 |  |  | 450 | 712 | 800 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.1621 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 98.4117 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823 | 98.0569 | 2017-09-01 | 2018-10-15
SunPower | SPR-30000m-3 {480V} | N | N | Y | Y | Y | N | N | N | Sunny Tripower TL-US, 30kW, 480Vac 3-phase, Transformerless, Grid Support Utility Interactive Inverter | 30.01 | 480 | 98 | No Information Submitted | No Information Submitted | UL | [7/6/2017] | [2.03.04.R] | 2018-10-15 | [7/6/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 1.22 |  |  | 500 | 720 | 800 | 3.001 | 6.002 | 9.003 | 15.005 | 22.5075 | 30.01 | 96.588 | 97.716 | 97.926 | 97.98 | 97.838 | 97.622 | 97.8115 | 97.588 | 98.448 | 98.69 | 98.602 | 98.538 | 98.328 | 98.5167 | 97.026 | 98.06 | 98.452 | 98.386 | 98.282 | 98.08 | 98.2528 | 2017-09-01 | 2018-10-15
Suzhou Ample ESS Co., Ltd | AP-L8K-SPUS {240V} | Y | Y | N | N | N | N | N |  | 7.98 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.9814 | 240 | 96 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.39 |  |  | 108 | 380 | 480 | 0.79814 | 1.5963 | 2.3944 | 3.9907 | 5.986 | 7.9814 | 90.9385 | 94.1039 | 94.9752 | 95.083 | 95.0387 | 94.6196 | 94.8087 | 92.1593 | 95.6656 | 96.6163 | 96.6433 | 97.0374 | 96.9779 | 96.6374 | 92.4438 | 95.9014 | 96.6012 | 97.0486 | 97.2916 | 97.2167 | 96.8905 | 2026-03-23 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Suzhou Ample ESS Co., Ltd | AP-L10K-SPUS {240V} | Y | Y | N | N | N | N | N |  | 10.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.0109 | 240 | 96 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.12 |  |  | 135 | 380 | 480 | 1.0011 | 2.0022 | 3.0033 | 5.0055 | 7.5082 | 10.0109 | 92.0512 | 94.9782 | 94.9328 | 95.3714 | 95.3991 | 94.9543 | 95.1601 | 93.0994 | 96.2304 | 96.2761 | 96.8719 | 97.0247 | 96.9062 | 96.7001 | 93.6663 | 96.3246 | 96.5808 | 97.0256 | 97.1253 | 97.0288 | 96.8558 | 2026-03-23 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Suzhou Ample ESS Co., Ltd | AP-L12K-SPUS {240V} | Y | Y | N | N | N | N | N |  | 12.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.0145 | 240 | 96.5 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.39 |  |  | 161 | 380 | 480 | 1.2014 | 2.4029 | 3.6043 | 6.0072 | 9.0109 | 12.0145 | 93.1006 | 95.228 | 95.5523 | 95.8393 | 95.6025 | 95.1408 | 95.5043 | 94.3433 | 96.5994 | 96.675 | 97.0511 | 96.9701 | 96.7737 | 96.8183 | 95.2452 | 96.8669 | 96.9412 | 97.2998 | 97.1893 | 96.9458 | 97.0767 | 2026-03-23 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Suzhou Ample ESS Co., Ltd | AP-L15K-SPUS {240V} | Y | Y | N | N | N | N | N |  | 15.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 15.0148 | 240 | 96.5 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.08 |  |  | 202 | 380 | 480 | 1.5015 | 3.003 | 4.5045 | 7.5074 | 11.2611 | 15.0148 | 94.5483 | 95.5289 | 96.0138 | 96.1843 | 95.8054 | 95.25 | 95.8181 | 95.5893 | 96.5176 | 96.9793 | 97.101 | 96.8732 | 96.5137 | 96.8467 | 96.0793 | 96.8399 | 97.2558 | 97.3226 | 96.9795 | 96.6351 | 97.0245 | 2026-03-23 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Tabuchi Electric Co., Ltd. | THD-S55P3BB-US {240V} | Y | N | Y | Y | Y | N | N | N | 5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 3.3 kW Discharge Rate/20 kWh Storage Capacity | 5.5189 | 240 | 94.5 | No Information Submitted | No Information Submitted | Intertek | [9/20/2017] | [4.1] | 2018-10-15 | [9/20/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 10.1 |  |  | 240 | 380 | 520 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.3 | 93.3 | 94.3 | 94.7 | 94.1 | 94.2 | 94 | 89.7 | 93.7 | 94.7 | 95.4 | 95.5 | 95.4 | 95.1 | 88.8 | 93.1 | 94.3 | 95.1 | 95.2 | 94.9 | 94.7 | 2017-12-15 | 2018-10-15
Tabuchi Electric Co., Ltd. | THD-S55P3B-US {240V} | Y | N | Y | Y | Y | N | N | N | 5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 2 kW Discharge Rate/10 kWh Storage Capacity | 5.5189 | 240 | 94.5 | No Information Submitted | No Information Submitted | Intertek | [9/20/2017] | [4.1] | 2018-10-15 | [9/20/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 10.1 |  |  | 240 | 380 | 520 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.3 | 93.3 | 94.3 | 94.7 | 94.1 | 94.2 | 94 | 89.7 | 93.7 | 94.7 | 95.4 | 95.5 | 95.4 | 95.1 | 88.8 | 93.1 | 94.3 | 95.1 | 95.2 | 94.9 | 94.7 | 2017-12-15 | 2018-10-15
Tabuchi Electric Co., Ltd. | THE-S55P3BB-USW {240V} | Y | N | Y | Y | Y | N | N | N | 5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 4.0 kW Discharge Rate/20 kWh Storage Capacity | 5.5189 | 240 | 94.5 | No Information Submitted | No Information Submitted | Intertek | [04/26/2018] | [4.11] | 2018-10-15 | [04/26/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 10.1 |  |  | 240 | 380 | 520 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.326 | 93.286 | 94.304 | 94.656 | 94.048 | 94.174 | 93.9857 | 89.688 | 93.666 | 94.706 | 95.44 | 95.498 | 95.41 | 95.0624 | 88.78 | 93.076 | 94.276 | 95.094 | 95.166 | 94.922 | 94.6719 | 2018-06-01 | 2018-10-15
Tesla Inc. | 1534000-xx-y {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 3.336 kW, 208 Vac Grid Support Utility Interactive Inverter, where xx is two numbers and y is a letter | 3.336 | 208 | 97.5 | Intertek | [10/13/2022] | Intertek | [11/30/20] | [1217B43E9B859EAB26ECB10B5FBECC64/8A3CA3F2] | 2021-01-21 | [11/30/20] | 2021-01-21 | Intertek | 2020-08-06 | 2021-01-21 |  | N | N | 3.8925 |  |  | 270 | 375 | 480 | 0.33357 | 0.66713 | 1.0007 | 1.6678 | 2.5017 | 3.3357 | 94.5015 | 95.4052 | 96.9255 | 97.3899 | 97.339 | 97.0429 | 97.0751 | 97.5109 | 95.4805 | 97.2538 | 96.8148 | 97.9621 | 97.4384 | 97.4679 | 95.4081 | 96.0018 | 96.4123 | 97.3319 | 97.8399 | 97.5201 | 97.3567 | 2021-01-21 | 2023-01-03
Tesla Inc. | 1534000-xx-y {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter, where xx is two numbers and y is a letter | 3.8 | 240 | 97.5 | Intertek | [10/13/2022] | Intertek | [11/30/20] | [1217B43E9B859EAB26ECB10B5FBECC64/8A3CA3F2] | 2021-01-21 | [11/30/20] | 2021-01-21 | Intertek | 2020-08-06 | 2021-01-21 |  | N | N | 4.664 |  |  | 270 | 350 | 425 | 0.38004 | 0.76008 | 1.1401 | 1.9002 | 2.8503 | 3.8004 | 93.3952 | 96.6818 | 96.8269 | 97.6523 | 97.789 | 97.1339 | 97.381 | 94.0344 | 97.5046 | 97.6631 | 98.024 | 98.074 | 97.6865 | 97.8048 | 92.4631 | 96.097 | 97.7065 | 98.1107 | 98.0548 | 97.938 | 97.6973 | 2021-01-21 | 2023-01-03
Tesla Inc. | 1538000-xx-y {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 6.656 kW, 208 Vac Grid Support Utility Interactive Inverter, where xx is two numbers and y is a letter. This inverter can be a component of the Energy Storage System 1850000-XX-Y. | 6.561 | 208 | 97.5 | Intertek | [10/13/2022] | Intertek | [11/19/2020] | [1217B43E9B859EAB26ECB10B5FBECC64/D85CAB80] | 2021-01-04 | [11/19/2020] | 2021-01-04 | Intertek | 2020-08-06 | 2021-01-04 |  | N | N | 6.7176 |  |  | 270 | 375 | 480 | 0.65614 | 1.3123 | 1.9684 | 3.2807 | 4.9211 | 6.5614 | 93.438 | 98.4475 | 97.3037 | 97.8393 | 97.6255 | 96.8692 | 97.4676 | 95.0991 | 98.0957 | 98.0608 | 98.1575 | 97.8955 | 98.2213 | 97.8848 | 95.1054 | 96.6131 | 96.4097 | 97.8988 | 97.5475 | 97.0402 | 97.315 | 2021-01-04 | 2023-01-03
Tesla Inc. | 1538000-xx-y {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.68 kW, 240 Vac Grid Support Utility Interactive Inverter, where xx is two numbers and y is a letter. This inverter can be a component of the Energy Storage System 1850000-XX-Y. Inverter is capable of PCS functionality. | 7.575 | 240 | 98 | Intertek | [3/16/2023] | Intertek | [11/19/2020] | [1217B43E9B859EAB26ECB10B5FBECC64/D85CAB80] | 2021-01-04 | [11/19/2020] | 2021-01-04 | Intertek | 2020-08-06 | 2021-01-04 |  | N | N | 6.913 |  |  | 270 | 375 | 480 | 0.75749 | 1.515 | 2.2725 | 3.7875 | 5.6812 | 7.5749 | 93.5744 | 97.8119 | 98.3803 | 98.2034 | 97.8671 | 97.2554 | 97.7942 | 96.846 | 97.8731 | 98.2225 | 98.5652 | 98.2426 | 97.6983 | 98.2064 | 95.9244 | 96.8399 | 98.117 | 98.3572 | 98.0899 | 97.6444 | 97.9779 | 2021-01-04 | 2024-06-03
Tesla Inc. | 1707000-XX-Y {240V, 10kW} | Y | Y | N | N | N | N | Y | N | 10 kW, 240 Vac Grid Support Utility Interactive Powerwall 3 Integrated Energy Storage System Inverter, where XX are numbers and Y is a letter | 9.991 | 240 | 96.2 | Intertek | [4/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2020-03-20 | No Information Submitted | This component is specific to an energy storage system (1707000-xx-y) and is not available as an individual unit. | N | N | 0.11 |  |  | 270 | 375 | 480 | 0.999 | 1.998 | 2.997 | 4.995 | 7.493 | 9.991 | 94.49 | 94.53 | 95.49 | 97.6 | 97.4 | 96.78 | 96.92 | 94.48 | 94.72 | 94.73 | 96.44 | 97 | 95.25 | 96.31 | 91.41 | 92.53 | 94.39 | 95.75 | 96.1 | 94.97 | 95.4 | 2024-08-01
Tesla Inc. | 1707000-XX-Y {240V, 11.5kW} | Y | Y | N | N | N | N | Y | N | 11.5 kW, 240 Vac Grid Support Utility Interactive Powerwall 3 Integrated Energy Storage System Inverter, where XX are numbers and Y is a letter | 11.508 | 240 | 97.5 | Intertek | [3/23/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2020-03-20 | No Information Submitted | This component is specific to an energy storage system (1707000-xx-y) and is not available as an individual unit. | N | N | 0.29 |  |  | 270 | 375 | 480 | 1.1508 | 2.3016 | 3.4524 | 5.754 | 8.631 | 11.508 | 94.2008 | 96.0606 | 96.991 | 97.8448 | 97.659 | 96.72 | 97.3526 | 92.3243 | 94.3963 | 96.7175 | 97.3893 | 98.2249 | 97.2062 | 97.3901 | 92.093 | 95.365 | 96.6821 | 97.177 | 98.2476 | 97.2883 | 97.3966 | 2024-01-11
Tigo Energy, Inc | TSI-3.0K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 2.626 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 2.626 | 208 | 96.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.576 |  |  | 125 | 380 | 480 | 0.26259 | 0.52518 | 0.78777 | 1.3129 | 1.9694 | 2.6259 | 91.2934 | 93.7087 | 95.2183 | 95.8997 | 95.8355 | 95.6645 | 95.4784 | 93.5823 | 95.3477 | 96.9042 | 97.2283 | 97.3991 | 97.0876 | 97.033 | 92.5038 | 95.6858 | 96.4301 | 96.8779 | 96.8499 | 96.9624 | 96.579 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-3.0K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.095 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.095 | 240 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.593 |  |  | 125 | 380 | 480 | 0.30951 | 0.61902 | 0.92853 | 1.5475 | 2.3213 | 3.0951 | 92.5494 | 94.742 | 95.5187 | 96.466 | 96.3778 | 96.1735 | 96.0481 | 94.9531 | 96.9774 | 97.284 | 97.7821 | 97.7609 | 97.4493 | 97.5411 | 93.2489 | 95.9992 | 96.7283 | 97.2156 | 97.3487 | 97.3889 | 97.0169 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-3.8K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.324 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 3.324 | 208 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.576 |  |  | 160 | 380 | 480 | 0.33238 | 0.66477 | 0.99715 | 1.6619 | 2.4929 | 3.3238 | 91.7552 | 94.4271 | 95.625 | 96.3968 | 96.3716 | 96.2365 | 95.9987 | 92.8401 | 95.7332 | 97.3293 | 97.2908 | 97.7747 | 97.4727 | 97.3051 | 92.8717 | 95.7668 | 96.7784 | 97.4953 | 97.5884 | 97.4672 | 97.1859 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-3.8K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.888 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.888 | 240 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.593 |  |  | 160 | 380 | 480 | 0.38882 | 0.77764 | 1.1665 | 1.9441 | 2.9162 | 3.8882 | 92.9226 | 95.0495 | 95.9079 | 96.5875 | 96.7318 | 96.456 | 96.3523 | 95.8681 | 97.43 | 97.8567 | 98.062 | 98.0583 | 97.9727 | 97.9116 | 93.4977 | 96.4887 | 97.1935 | 97.6687 | 97.7381 | 97.6144 | 97.4199 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-5.0K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4.28 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 4.28 | 208 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.576 |  |  | 210 | 380 | 480 | 0.42805 | 0.85609 | 1.2841 | 2.1402 | 3.2104 | 4.2805 | 93.9969 | 95.6291 | 96.5292 | 97.277 | 96.8685 | 96.4968 | 96.7182 | 95.6415 | 97.3556 | 97.7545 | 97.9536 | 97.7989 | 97.5872 | 97.707 | 95.0137 | 96.8034 | 97.3434 | 97.6629 | 97.6924 | 97.3985 | 97.478 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-5.0K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4.943 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 4.943 | 240 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.593 |  |  | 210 | 380 | 480 | 0.49432 | 0.98864 | 1.483 | 2.4716 | 3.7074 | 4.9432 | 94.2674 | 96.0279 | 96.6177 | 96.9688 | 96.7976 | 96.4626 | 96.6555 | 95.8274 | 97.6476 | 97.9929 | 98.1977 | 98.0262 | 97.7757 | 97.9388 | 95.1548 | 97.2155 | 97.7005 | 97.9802 | 97.817 | 97.6089 | 97.6903 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-6.0K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.143 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 5.143 | 208 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.576 |  |  | 170 | 380 | 480 | 0.51426 | 1.0285 | 1.5428 | 2.5713 | 3.8569 | 5.1426 | 93.4812 | 95.1436 | 95.9216 | 96.4143 | 96.4086 | 96.2016 | 96.1607 | 95.7404 | 97.2023 | 97.6753 | 97.7276 | 97.7059 | 97.2003 | 97.5777 | 94.531 | 96.5287 | 97.1839 | 97.4841 | 97.5 | 97.1255 | 97.2727 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-6.0K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.918 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 5.918 | 240 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.593 |  |  | 170 | 380 | 480 | 0.59178 | 1.1836 | 1.7753 | 2.9589 | 4.4383 | 5.9177 | 93.4931 | 95.0713 | 96.0091 | 96.5068 | 96.5375 | 96.277 | 96.2595 | 96.2836 | 97.6235 | 97.995 | 98.0323 | 97.7405 | 97.6407 | 97.7632 | 95.2829 | 97.0935 | 97.4899 | 97.8279 | 97.6998 | 97.4333 | 97.5612 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-7.6K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.58 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 6.58 | 208 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.576 |  |  | 212 | 380 | 480 | 0.65804 | 1.3161 | 1.9741 | 3.2902 | 4.9353 | 6.5804 | 93.7826 | 95.5421 | 96.606 | 96.8324 | 96.8224 | 96.4415 | 96.5939 | 95.6144 | 97.208 | 97.6283 | 97.7129 | 97.8083 | 97.3895 | 97.628 | 94.0659 | 96.3435 | 97.3147 | 97.3793 | 97.4451 | 97.2215 | 97.2142 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-8.2K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.2 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 7.166 | 208 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.71659 | 1.4332 | 2.1498 | 3.5829 | 5.3744 | 7.1659 | 93.818 | 95.9467 | 96.5916 | 96.9394 | 96.8921 | 96.7981 | 96.691 | 95.2258 | 97.2231 | 97.7432 | 97.9238 | 97.8229 | 97.7412 | 97.6966 | 93.7147 | 96.5216 | 97.2952 | 97.7041 | 97.7221 | 97.6373 | 97.4425 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-7.6K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.524 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 7.524 | 240 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.593 |  |  | 212 | 380 | 480 | 0.75242 | 1.5048 | 2.2573 | 3.7621 | 5.6431 | 7.5242 | 94.8321 | 96.2443 | 96.9372 | 97.1359 | 97.0549 | 96.4681 | 96.899 | 96.1031 | 97.82 | 98.0103 | 98.1875 | 98.0302 | 97.4081 | 97.9421 | 95.2191 | 97.2034 | 97.6838 | 97.8749 | 97.7927 | 97.3782 | 97.6437 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-9.0K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 7.874 | 208 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.78742 | 1.5748 | 2.3623 | 3.9371 | 5.9056 | 7.8742 | 93.9829 | 96.0797 | 96.6986 | 97.0304 | 96.9127 | 96.7846 | 96.7465 | 95.5872 | 97.3526 | 97.782 | 97.9238 | 97.7705 | 97.6713 | 97.6909 | 94.5847 | 96.692 | 97.396 | 97.712 | 97.6675 | 97.5806 | 97.4678 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-8.2K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.2 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 8.251 | 240 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.82514 | 1.6503 | 2.4754 | 4.1257 | 6.1886 | 8.2514 | 93.9258 | 96.1247 | 96.8143 | 97.2666 | 97.2617 | 97.0721 | 97.0092 | 95.5722 | 97.4863 | 97.9916 | 98.2391 | 98.1842 | 98.0166 | 98.0249 | 93.7743 | 96.6734 | 97.4868 | 97.9609 | 97.966 | 97.9229 | 97.673 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-10.0K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 8.76 | 208 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.87595 | 1.7519 | 2.6278 | 4.3797 | 6.5696 | 8.7595 | 94.7147 | 96.1872 | 96.7641 | 96.9456 | 96.7226 | 96.627 | 96.6625 | 96.1898 | 97.4947 | 97.8331 | 97.8547 | 97.653 | 97.5442 | 97.6451 | 94.884 | 96.9958 | 97.5353 | 97.726 | 97.6134 | 97.5151 | 97.4827 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-9.0K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 9.063 | 240 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.90625 | 1.8125 | 2.7188 | 4.5312 | 6.7969 | 9.0625 | 94.2384 | 96.2702 | 96.908 | 97.3235 | 97.2 | 97.0403 | 97.018 | 95.9482 | 97.6026 | 98.0707 | 98.2515 | 98.1428 | 97.9914 | 98.0346 | 94.3716 | 96.8985 | 97.6347 | 98.0229 | 98.0409 | 97.9412 | 97.7795 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-11.4K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 10.04 | 208 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.004 | 2.008 | 3.0119 | 5.0199 | 7.5298 | 10.0398 | 95.0284 | 96.5616 | 97.0154 | 97.1814 | 96.9023 | 96.8567 | 96.8802 | 95.703 | 97.5294 | 97.8587 | 97.8733 | 97.7607 | 97.7179 | 97.7001 | 95.102 | 97.007 | 97.5024 | 97.6871 | 97.6273 | 97.6013 | 97.4916 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-10.0K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 10.082 | 240 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.0082 | 2.0164 | 3.0246 | 5.041 | 7.5615 | 10.082 | 95.1276 | 96.4976 | 97.0675 | 97.3296 | 97.1985 | 96.9229 | 97.0787 | 96.3253 | 97.7618 | 98.1384 | 98.2919 | 98.1462 | 97.9316 | 98.0731 | 95.0134 | 97.1984 | 97.7803 | 98.0517 | 98.0092 | 97.8719 | 97.8234 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-11.4K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 11.52 | 240 | 98 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.152 | 2.304 | 3.456 | 5.76 | 8.64 | 11.52 | 95.3626 | 96.9572 | 97.4775 | 97.685 | 97.5433 | 97.3539 | 97.4392 | 96.5819 | 98.0275 | 98.3999 | 98.5274 | 98.4351 | 98.2539 | 98.3467 | 95.457 | 97.1914 | 97.7448 | 97.9708 | 97.8318 | 97.6582 | 97.7149 | 2022-02-01 | 2023-10-11
TMEIC | PVU-L0840GR {630V} | N | N | Y | Y | Y | N | N | N | 840 kW, 630Vac, Grid Support Utility Interactive Photovoltaic Inverter | 794.693 | 630 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [10/14/2019] | [DSP: HM0041, FPGA: HF0008] | 2020-07-01 | [10/14/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 2500 kVA Low-Voltage Liquid-Immersed Distribution Transformers Table in DOE2016. | N | N | 47.17 |  |  | 915 | 1150 | 1200 | 79.469 | 158.939 | 23.8407 | 397.346 | 596.02 | 794.693 | 93.5562 | 97.2253 | 97.9043 | 98.4527 | 98.639 | 98.7216 | 98.2419 | 93.0512 | 96.7995 | 97.5749 | 98.1032 | 98.3158 | 98.2723 | 97.8937 | 92.8149 | 96.6179 | 97.4354 | 98.0106 | 98.2316 | 98.2048 | 97.791 | 2020-07-01
TMEIC Corporation | PVU-L0840URN {630V} | N | Y | N | N | N | N | N | N | 840 kW, 630 Vac Grid Support Utility Interactive Inverter | 796.4682 | 630 | 98.5 | CSA Group | [2/7/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 2500 kVA Liquid-Immersed Distribution Transformers table in DOE216. | N | N | 76.9288 |  |  | 915 | 986 | 1200 | 79.6468 | 159.2936 | 238.9405 | 398.2341 | 597.3511 | 796.4682 | 96.6005 | 97.9885 | 98.3127 | 98.5491 | 98.6038 | 98.6205 | 98.4473 | 96.3136 | 97.861 | 98.1599 | 98.4366 | 98.4755 | 98.4634 | 98.3117 | 95.9751 | 97.5663 | 97.984 | 98.2565 | 98.3226 | 98.3517 | 98.1378 | 2024-07-01
TSUNESS Co., Ltd | TSOL-M1600P {240V} | N | N | Y | Y | Y | N | N | N | 1.5 kW, 240 Vac Grid Support Utility Interactive Microinverters | 1.551 | 240 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [03/17/2020] | [V01.01.00] | 2020-06-01 | [03/17/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.03 |  |  | 36 | 42 | 48 | 0.15507 | 0.31014 | 0.46522 | 0.77536 | 1.163 | 1.5507 | 95.9528 | 96.054 | 96.306 | 96.641 | 96.7401 | 95.8974 | 96.5592 | 95.9448 | 95.6511 | 96.3554 | 96.3046 | 96.7191 | 96.4267 | 96.4894 | 95.1415 | 95.8675 | 96.4516 | 96.1667 | 96.6732 | 96.591 | 96.4346 | 2020-06-01
Univix Power Solutions | UVX5KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 5 | 240 | 97 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-14 |  |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2025-09-11
Univix Power Solutions | UVX6KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 6 | 240 | 97 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-14 |  |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2025-09-11
Univix Power Solutions | UVX7.6KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6 | 240 | 97 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-14 |  |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2025-09-11
Univix Power Solutions | UVX8KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 8.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 8 | 240 | 97.5 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-14 |  |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2025-09-11
Univix Power Solutions | UVX10KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 10 | 240 | 97 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-14 |  |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.018 | 2.035 | 3.053 | 5.088 | 7.632 | 10.177 | 94.69 | 95.94 | 96.4 | 96.8 | 97.34 | 96.75 | 96.91 | 95.39 | 96.33 | 96.85 | 97.45 | 97.97 | 97.37 | 97.51 | 94.93 | 95.96 | 96.65 | 97.01 | 97.56 | 97.03 | 97.12 | 2025-09-11
Univix Power Solutions | UVX12KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 12.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 12 | 240 | 96 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-15 |  |  | N | N | 13.202 |  |  | 200 | 360 | 430 | 1.2214 | 2.4427 | 3.6641 | 6.1068 | 9.1601 | 12.2135 | 93.588 | 95.318 | 95.52 | 95.804 | 95.494 | 95.612 | 95.4831 | 94.262 | 96.132 | 96.662 | 96.872 | 96.622 | 96.294 | 96.544 | 94.002 | 96.18 | 96.74 | 96.876 | 96.678 | 96.362 | 96.5793 | 2025-09-11
Univix Power Solutions | UVX16LNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 16.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 16 | 240 | 96 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-15 |  |  | N | N | 20.465 |  |  | 220 | 360 | 430 | 1.6199 | 3.2398 | 4.8596 | 8.0994 | 12.1491 | 16.1988 | 93.662 | 95.358 | 95.802 | 95.93 | 95.51 | 96.18 | 95.5852 | 94.188 | 96.06 | 96.548 | 96.876 | 96.636 | 96.35 | 96.5348 | 94.088 | 95.998 | 96.536 | 96.946 | 96.692 | 96.25 | 96.5657 | 2025-09-11
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 6KW {240V} | Y | Y | Y | Y | Y | N | N | N | 6 kW, 240 Vac Split Phase, Transformerless Grid Support Utility Interactive Inverter | 6 | 240 | 90.5 | Intertek | [11/18/2024] | Intertek | [11/18/2024] | [V01.14] | 2025-05-01 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 250 | 370 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 80.54 | 88.08 | 90.48 | 91.91 | 92.06 | 91.51 | 91.15 | 76.64 | 86.18 | 89.25 | 91.47 | 92.15 | 92.15 | 90.74 | 75.32 | 84.7 | 88.23 | 90.81 | 91.67 | 91.76 | 90.08 | 2025-05-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 6KW {120V} | Y | Y | Y | Y | Y | N | N | N | 6 kW, 120 Vac Split Phase, Transformerless Grid Support Utility Interactive Inverter | 6.0177 | 120 | 93.5 | Intertek | [11/18/2024] | Intertek | [11/18/2024] | [V01.14] | 2023-05-11 | [8/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 43 |  |  | 250 | 370 | 500 | 0.60177 | 1.2035 | 1.8053 | 3.0088 | 4.5132 | 6.0177 | 84.5455 | 90.3878 | 92.4318 | 93.9429 | 94.4517 | 94.3979 | 93.5003 | 83.7684 | 90.3217 | 92.4553 | 94.1133 | 94.8535 | 94.8931 | 93.7422 | 80.8311 | 88.8891 | 90.9986 | 93.3728 | 94.0658 | 94.308 | 92.7761 | 2023-05-22 | 2025-05-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP 12KW Optimum {120V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 120 Vac Grid Support Utility Interactive Inverter | 9.0186 | 120 | 95.5 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-06-03 | [3/13/2024] | 2024-06-03 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-06-03 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP 12KW Optimum {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.0186 | 240 | 95.5 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-06-11 | [3/13/2024] | 2024-06-11 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-06-11 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 12KW {120V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 120 Vac Grid Support Utility Interactive Inverter | 9.0186 | 120 | 95.5 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-06-03 | [3/13/2024] | 2024-06-03 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-06-03 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 12KW {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.0186 | 240 | 95.5 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-06-11 | [3/13/2024] | 2024-06-11 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-06-11 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP 12KW Premium {120V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 120 Vac Grid Support Utility Interactive Inverter | 10.029 | 120 | 95 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-08-12 | [5/20/2024] | 2024-08-12 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 1.0029 | 2.0058 | 3.0087 | 5.0145 | 7.5217 | 10.029 | 90.8464 | 94.1071 | 94.9509 | 95.2844 | 95.0472 | 94.9427 | 94.8652 | 91.4204 | 94.5211 | 95.4529 | 95.936 | 95.4773 | 95.0275 | 95.3381 | 88.6076 | 93.0581 | 94.426 | 95.1626 | 95.1729 | 94.8367 | 94.6959 | 2024-08-12 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP 12KW Premium {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.029 | 240 | 95 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-08-12 | [5/20/2024] | 2024-08-12 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 1.0029 | 2.0058 | 3.0087 | 5.0145 | 7.5217 | 10.029 | 90.8464 | 94.1071 | 94.9509 | 95.2844 | 95.0472 | 94.9427 | 94.8652 | 91.4204 | 94.5211 | 95.4529 | 95.936 | 95.4773 | 95.0275 | 95.3381 | 88.6076 | 93.0581 | 94.426 | 95.1626 | 95.1729 | 94.8367 | 94.6959 | 2024-08-12 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 15KW {240V} | Y | Y | Y | Y | Y | N | N |  | 15 kW, 240 Vac Grid Support Utility Interactive Inverter | 14.79 | 240 | 97 | Intertek/ETL | [5/29/2026] | Intertek/ETL | [5/29/2026] | [36-105771, 36-105772] | 2026-07-13 | [5/29/2026] | 2026-07-13 | No Information Submitted | No Information Submitted |  |  | N | N | 42 |  |  | 150 | 360 | 450 | 1.479 | 2.958 | 4.437 | 7.395 | 11.093 | 14.79 | 90.78 | 94.72 | 95.88 | 96.41 | 96.25 | 96.04 | 95.94 | 93.68 | 98.03 | 97.76 | 97.98 | 97.68 | 98.02 | 97.63 | 94.61 | 96.87 | 97.77 | 98.11 | 98.25 | 98.11 | 97.94 | 2026-07-13 |  | N | N | N | Y | N | N | N | N | N
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 15KW {120V} | Y | Y | Y | Y | Y | N | N |  | 15 kW, 120 Vac Grid Support Utility Interactive Inverter | 15.036 | 120 | 96 | Intertek/ETL | [5/29/2026] | Intertek/ETL | [5/29/2026] | [36-105771, 36-105772] | 2026-07-13 | [5/29/2026] | 2026-07-13 | No Information Submitted | No Information Submitted |  |  | N | N | 42 |  |  | 150 | 360 | 450 | 1.504 | 3.007 | 4.511 | 7.518 | 11.277 | 15.036 | 90.72 | 94.02 | 94.9 | 95.17 | 94.88 | 94.64 | 94.72 | 91.1 | 96.38 | 96.66 | 96.72 | 96.67 | 96.24 | 96.42 | 94.65 | 95.93 | 96.37 | 96.53 | 96.4 | 96.23 | 96.32 | 2026-07-13 |  | N | N | N | Y | N | N | N | N | N
Wanbang Digital Energy Co., Ltd. | SI104LULA00 {208V} | Y | Y | N | N | N | N | Y* | Y | 8.3 kW, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.323 | 208 | 97 | CSA Group | [9/7/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-14 | 2024-02-21 |  | N | N | 5.03 |  |  | 320 | 360 | 480 | 0.832 | 1.665 | 2.497 | 4.162 | 6.243 | 8.323 | 96.79 | 97.5 | 97.58 | 97.36 | 96.96 | 96.44 | 97.11 | 96.6 | 97.58 | 97.65 | 97.43 | 97.04 | 96.56 | 97.18 | 95.8 | 97.36 | 97.57 | 97.42 | 97.01 | 96.57 | 97.11 | 2024-02-21
Wanbang Digital Energy Co., Ltd. | SI104LULA00 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 9.58 | 240 | 97 | CSA Group | [9/7/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-14 | 2024-02-21 |  | N | N | 5.42 |  |  | 320 | 360 | 480 | 0.958 | 1.916 | 2.874 | 4.79 | 7.185 | 9.58 | 95.07 | 96.6 | 97.07 | 97.19 | 96.95 | 96.55 | 96.9 | 94.86 | 96.68 | 97.15 | 97.26 | 97.05 | 96.69 | 96.98 | 94.02 | 96.48 | 97.07 | 97.26 | 97.08 | 96.74 | 96.94 | 2024-02-21
WSTECH GmbH | APS800-PV-1-440-5 {440V} | N | N | Y | Y | Y | N | N | N | 800 kW, 440 Vac, Grid Support Utility Interactive Centeral PV Inverter | 814.167 | 440 | 97.5 | No Information Submitted | No Information Submitted | MET | [10/12/2020] | [APU V3130 APMC V2040] | 2020-11-12 | [10/12/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 1000 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216. | N | N | 91.4 |  |  | 648 | 1000 | 1500 | 81.4167 | 162.8334 | 244.2501 | 407.0835 | 610.6252 | 814.1669 | 96.8994 | 97.9207 | 98.1472 | 98.0855 | 97.7317 | 97.3005 | 97.8104 | 97.156 | 97.9031 | 98.0845 | 97.9812 | 97.697 | 97.2751 | 97.7708 | 96.5182 | 97.3518 | 97.6259 | 97.6679 | 97.3419 | 96.9571 | 97.3927 | 2020-11-12
WSTECH GmbH | APS870-PV-1-480-5 {480V} | N | N | Y | Y | Y | Y | N | N | 870 kW, 480 Vac, Grid Support Utility Interactive Centeral PV Inverter | 872.029 | 480 | 98 | No Information Submitted | No Information Submitted | MET | [04/08/2021] | [APU V3130 APMC V2050] | 2021-07-01 | [04/08/2021] | 2021-07-01 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 91.402 |  |  | 770 | 1000 | 1470 | 87.2029 | 174.4058 | 261.6087 | 436.0145 | 654.0218 | 872.029 | 97.0815 | 98.1883 | 98.4162 | 98.4017 | 98.1322 | 97.7562 | 98.1648 | 95.7664 | 97.2807 | 97.8339 | 98.0408 | 97.8593 | 97.5271 | 97.7651 | 96.9374 | 97.6397 | 97.8465 | 97.7946 | 97.5592 | 97.1756 | 97.6031 | 2021-07-01
WSTECH GmbH | APS1600-PV-2-440-5 {440V} | N | N | Y | Y | Y | N | N | N | 1600 kW, 440 Vac, Grid Support Utility Interactive Centeral PV Inverter | 1626.952 | 440 | 98 | No Information Submitted | No Information Submitted | MET | [10/12/2020] | [APU V3130 APMC V2040] | 2020-11-12 | [10/12/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 91.4 |  |  | 648 | 1000 | 1500 | 162.6952 | 325.3904 | 488.0856 | 813.476 | 1220.214 | 1626.952 | 98.0396 | 98.5839 | 98.6684 | 98.5329 | 98.2151 | 97.8585 | 98.3298 | 96.9836 | 97.9106 | 98.1157 | 98.1085 | 97.8527 | 97.453 | 97.8861 | 96.318 | 97.3792 | 97.6608 | 97.7017 | 97.437 | 97.0028 | 97.4501 | 2020-11-12
WSTECH GmbH | APS1740-PV-2-480-5 {480V} | N | N | Y | Y | Y | Y | N | N | 1735 kW, 480 Vac, Grid Support Utility Interactive Centeral PV Inverter | 1735.36 | 480 | 97.5 | No Information Submitted | No Information Submitted | MET | [04/08/2021] | [APU V3130 APMC V2050] | 2021-07-01 | [04/08/2021] | 2021-07-01 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 91.402 |  |  | 770 | 1000 | 1470 | 173.536 | 347.0721 | 520.6081 | 867.6802 | 1301.5204 | 1735.3605 | 96.2018 | 97.6354 | 98.0243 | 98.1239 | 97.9169 | 97.5975 | 97.8746 | 95.6963 | 97.2746 | 97.7805 | 97.9519 | 97.7577 | 97.4332 | 97.6784 | 94.3845 | 96.4707 | 97.0706 | 97.4161 | 97.3403 | 97.06 | 97.1481 | 2021-07-01
Xiamen Kehua Digital Energy Tech Co., Ltd | iStoragE2A 7600 {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.581 | 240 | 97 | Intertek | [10/18/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.7581 | 1.5162 | 2.2743 | 3.7905 | 5.6858 | 7.581 | 94.2651 | 95.2225 | 96.163 | 96.9234 | 97.1125 | 97.0636 | 96.748 | 95.2164 | 96.1836 | 96.7935 | 97.3649 | 97.6024 | 97.5348 | 97.2857 | 94.8243 | 95.8334 | 96.5515 | 97.2034 | 97.4231 | 97.3541 | 97.0855 | 2023-01-23
Xiamen Kehua Digital Energy Tech Co., Ltd | iStoragE2A 9600 {240V} | Y | Y | N | N | N | N | N | N | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.5733 | 240 | 97 | Intertek | [10/18/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.95733 | 1.9147 | 2.872 | 4.7866 | 7.1799 | 9.5733 | 94.324 | 95.4338 | 96.4736 | 97.0126 | 97.0914 | 97.0133 | 96.8032 | 95.7635 | 96.4127 | 97.0422 | 97.4839 | 97.5735 | 97.4048 | 97.352 | 94.8907 | 95.9847 | 96.8438 | 97.3145 | 97.3946 | 97.234 | 97.133 | 2023-01-23
Xiamen Kehua Digital Energy Tech Co., Ltd | iStoragE2A 10000 {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.9563 | 240 | 97 | Intertek | [10/18/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.99563 | 1.9913 | 2.9869 | 4.9782 | 7.4672 | 9.9563 | 94.3337 | 95.6136 | 96.5122 | 97.0308 | 97.0728 | 96.9826 | 96.8097 | 95.7935 | 96.475 | 97.0733 | 97.5049 | 97.543 | 97.3726 | 97.3468 | 95.184 | 96.0843 | 96.883 | 97.3434 | 97.3652 | 97.2134 | 97.1439 | 2023-01-23
Xiamen Kehua Digital Energy Tech Co., Ltd | iStoragE2A 11400 {240V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.3705 | 240 | 97 | Intertek | [10/18/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.1371 | 2.2741 | 3.4112 | 5.6853 | 8.5279 | 11.3705 | 94.3642 | 96.055 | 96.9052 | 97.1019 | 97.0437 | 96.9028 | 96.8756 | 95.8125 | 96.7944 | 97.3353 | 97.6036 | 97.4725 | 97.2634 | 97.3728 | 95.284 | 96.5532 | 97.1622 | 97.414 | 97.3038 | 97.0831 | 97.1806 | 2023-01-23
Xiamen Kehua Digital Energy Tech Co., Ltd | iStoragE2A 12000 {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.9682 | 240 | 97 | Intertek | [10/18/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.1968 | 2.3936 | 3.5905 | 5.9841 | 8.9761 | 11.9682 | 94.3841 | 96.0625 | 96.9237 | 97.1216 | 97.0131 | 96.8713 | 96.8654 | 95.8343 | 96.815 | 97.3428 | 97.6232 | 97.4548 | 97.223 | 97.3683 | 95.3154 | 96.5735 | 97.1839 | 97.4422 | 97.282 | 97.04 | 97.1777 | 2023-01-23
Xiamen Kehua Hengsheng Co., Ltd. | SPI50K-BHV {480V} | N | N | Y | Y | Y | N | N | N | 50 kW, 480 Vac Grid Support Utility Interactive Inverter | 49.825 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [11/27/2017] | [Main CPU(28335):V1] | 2018-10-15 | [11/27/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.8 |  |  | 540 | 695 | 850 | 4.983 | 9.966 | 14.949 | 24.915 | 37.3725 | 49.83 | 96.7703 | 96.973 | 97.3637 | 97.6805 | 97.7045 | 97.6785 | 97.5833 | 97.3153 | 98.4954 | 98.6189 | 98.7698 | 98.6611 | 98.2836 | 98.5979 | 96.5521 | 97.8957 | 98.1552 | 98.33 | 98.283 | 98.0881 | 98.1792 | 2018-01-02 | 2018-10-15
Xiamen Kehua Hengsheng Co., Ltd. | SPI60K-BHV {480V} | N | N | Y | Y | Y | N | N | N | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 59.668 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [11/27/2017] | [Main CPU(28335):V1] | 2018-10-15 | [11/27/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.8 |  |  | 540 | 695 | 850 | 5.967 | 11.934 | 17.901 | 29.835 | 44.7525 | 59.67 | 97.0114 | 97.6315 | 97.6409 | 97.9122 | 97.5927 | 97.3714 | 97.6332 | 98.5714 | 98.8538 | 98.8416 | 98.7205 | 98.6058 | 98.3476 | 98.6563 | 97.7579 | 98.3751 | 98.523 | 98.3758 | 98.1648 | 97.9527 | 98.2357 | 2018-01-02 | 2018-10-15
Yaskawa Solectria Solar | PVI20TL-480-R {480V} | N | N | Y | Y | Y | Y | Y* | Y | 20 kW, 480 Vac Grid Support Utility Interactive Inverter | 20 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [01/20/2020] | [00.02.00] | 2020-02-21 | [01/20/2020] | 2020-08-11 | Intertek | 2020-03-20 | 2020-08-11 |  | N | N | 3 |  |  | 560 | 735 | 850 | 2.0112 | 4.0224 | 6.0336 | 10.056 | 15.0839 | 20.1119 | 96.9815 | 97.6652 | 97.8012 | 97.8313 | 97.6023 | 97.256 | 97.6353 | 97.9016 | 98.3305 | 98.4819 | 98.4139 | 98.2956 | 98.149 | 98.3215 | 97.5397 | 98.2151 | 98.3121 | 98.2684 | 98.1987 | 97.9889 | 98.1909 | 2020-02-21 | 2021-04-12
Yaskawa Solectria Solar | PVI 25TL-208 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 25 kW, 208 Vac Grid Support Utility Interactive Inverter | 25 | 208 | 96.5 | CSA Group | [03/15/2022] | CSA Group | [09/10/2020] | [V01.01.00] | 2020-10-21 | [09/10/2020] | 2020-10-21 | Intertek | 2020-09-11 | 2020-10-21 |  | N | N | 2.9 |  |  | 480 | 575 | 850 | 2.5432 | 5.0864 | 7.6296 | 12.716 | 19.074 | 25.432 | 95.687 | 96.8055 | 97.0311 | 97.0424 | 96.7769 | 96.4735 | 96.8058 | 95.3071 | 96.2843 | 96.7871 | 96.7814 | 96.4829 | 96.1186 | 96.5069 | 93.5943 | 95.6171 | 96.1229 | 96.3357 | 96.1514 | 95.85 | 96.0426 | 2020-10-21 | 2022-09-01
Yaskawa Solectria Solar | PVI25TL-480-R {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 25 kW, 480 Vac Grid Support Utility Interactive Inverter | 25 | 480 | 98 | Intertek | [11/9/2022] | Intertek | [01/20/2020] | [00.02.00] | 2020-02-21 | [01/20/2020] | 2020-08-11 | Intertek | 2020-03-20 | 2020-08-11 |  | N | N | 3 |  |  | 560 | 735 | 850 | 2.5259 | 5.0517 | 7.5776 | 12.6294 | 18.944 | 25.2587 | 96.9119 | 97.6982 | 97.8295 | 97.8399 | 97.5971 | 97.2868 | 97.6381 | 97.8973 | 98.3256 | 98.4773 | 98.4082 | 98.2817 | 98.0946 | 98.3092 | 97.5003 | 98.1562 | 98.3137 | 98.2793 | 98.1854 | 97.9963 | 98.1822 | 2020-02-21 | 2023-05-01
Yaskawa Solectria Solar | PVI 36TL-480 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 36 kVA, 480 Vac, 1000 Vdc, 3-phase, non-isolated Grid Support Utility Interactive Inverter | 36 | 480 | 98 | No Information Submitted | No Information Submitted | CSA Group | [12/10/2020] | [V0.90] | 2018-10-15 | [12/10/2020] | 2021-02-01 | CSA Group | 2020-12-16 | 2021-02-01 | Formerly "Solectria Renewables, LLC" | N | N | 0 |  |  | 540 | 730 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 98.4 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2 | 98.3 | 2017-10-01 | 2021-02-01
Yaskawa Solectria Solar | PVI-36TL-480-V2 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 36 kW, 480 Vac, Grid Support Utility Interactive Inverter | 36 | 480 | 97.5 | CSA Group | [11/22/2022] | CSA Group | [11/22/2022] | [V01.18.00] | 2023-06-12 | [11/22/2022] | 2023-06-12 | Intertek | 2023-05-16 | 2023-06-12 |  | N | N | 2.9 |  |  | 400 | 625 | 850 | 3.6292 | 7.2583 | 10.8875 | 18.1458 | 27.2188 | 36.2917 | 93.7839 | 95.508 | 96.459 | 96.7736 | 97.1214 | 96.9894 | 96.7481 | 94.9739 | 96.4987 | 96.7245 | 97.8252 | 97.8261 | 97.7151 | 97.5077 | 95.5762 | 97.0793 | 97.3029 | 97.8896 | 98.181 | 98.0773 | 97.85 | 2023-06-12
Yaskawa Solectria Solar | PVI 50TL-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 50 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc | 50 | 480 | 98.5 | CSA Group | [03/15/2022] | CSA Group | [7/6/2017];[03/19/2019] | [V5.00];[V01.09.00] | 2018-10-15 | [03/19/2019] | 2020-08-11 | Intertek | 2020-03-20 | 2020-08-11 | Formerly "Solectria Renewables, LLC" | N | N | 0.88 |  |  | 480 | 730 | 850 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6 | 96.8 | 97.5 | 97.9 | 97.8 | 97.7 | 97.6 | 98 | 98.6 | 98.8 | 98.8 | 98.7 | 98.6 | 98.7 | 97.7 | 98.5 | 98.6 | 98.7 | 98.6 | 98.5 | 98.6 | 2017-10-01 | 2022-09-01
Yaskawa Solectria Solar | PVI-50TL-208 {208V} | N | Y | Y | Y | Y | Y | Y* |  | 50 kW, 208 Vac Grid Support Utility Interactive Inverter | 50 | 208 | 96.5 | CSA Group | [11/6/2025] | CSA Group | [11/6/2025] | [01.01.00] | 2025-12-22 | [11/6/2025] | 2025-12-22 | CSA Group | 2025-11-04 |  |  | N | N | 50.118 |  |  | 200 | 380 | 700 | 5.0118 | 10.0236 | 15.0354 | 25.059 | 37.6 | 50.1 | 95.8 | 96.5 | 96.7 | 96.6 | 96.2 | 95.6 | 96.3 | 96.7 | 97.3 | 97.3 | 97.2 | 96.8 | 96.3 | 96.9 | 95.5 | 96.4 | 96.8 | 96.7 | 96.3 | 95.9 | 96.4 | 2025-12-22
Yaskawa Solectria Solar | PVI 60TL-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 60 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc | 60 | 480 | 98.5 | CSA Group | [03/15/2022] | CSA Group | [7/6/2017];[03/19/2019] | [V5.00];[V01.09.00] | 2018-10-15 | [03/19/2019] | 2020-08-11 | Intertek | 2020-03-20 | 2020-08-11 | Formerly"Solectria Renewables, LLC" | N | N | 0.88 |  |  | 540 | 730 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5 | 97.5 | 97.9 | 98.1 | 97.9 | 97.7 | 97.9 | 98.2 | 98.7 | 98.8 | 98.8 | 98.7 | 98.5 | 98.7 | 98 | 98.6 | 98.7 | 98.7 | 98.5 | 98.4 | 98.5 | 2017-10-01 | 2022-09-01
Yaskawa Solectria Solar | PVI-100TL-480 {480V} | N | Y | Y | Y | Y | Y | Y* |  | 100 kW, 480 Vac Grid Support Utility Interactive Inverter | 100 | 480 | 98 | CSA Group | [11/6/2025] | CSA Group | [11/6/2025] | [01.01.00] | 2025-12-22 | [11/6/2025] | 2025-12-22 | CSA Group | 2025-11-04 |  |  | N | N | 21.54 |  |  | 340 | 720 | 850 | 10.016 | 20.032 | 30.048 | 50.08 | 75.1 | 100.2 | 95.7 | 97 | 97.2 | 97.4 | 97.3 | 97.1 | 97.2 | 97.4 | 98.5 | 98.6 | 98.6 | 98.5 | 98.3 | 98.4 | 97.2 | 98.2 | 98.4 | 98.4 | 98.3 | 98.2 | 98.3 | 2025-12-22
Yaskawa Solectria Solar | XGI 1500-125/125-3S {600V} | Y | Y | N | N | N | N | N | Y | 125 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 125 | 600 | 98.5 | TUV Rheinland of North America | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-06-11 |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 12.5111 | 25.0222 | 37.5333 | 62.5555 | 93.8333 | 125.111 | 97.8024 | 98.2426 | 98.5526 | 98.7074 | 98.7076 | 98.8392 | 98.6361 | 97.3452 | 97.8518 | 98.2734 | 98.4604 | 98.5148 | 98.4916 | 98.3933 | 97.1044 | 97.4718 | 98.1588 | 98.6012 | 98.396 | 98.369 | 98.3114 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500-125/125-UL {600V} | N | Y | N | N | N | N | Y* | Y | 125 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 125 | 600 | 98.5 | TUV Rheinland of North America | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-05-16 | 2023-09-01 |  | N | N | 2.75 |  |  | 860 | 1000 | 1250 | 12.5214 | 25.0427 | 37.5641 | 62.6068 | 93.9102 | 125.2136 | 97.8024 | 98.2426 | 98.5526 | 98.7074 | 98.7076 | 98.8392 | 98.6361 | 97.3452 | 97.8518 | 98.2734 | 98.4604 | 98.5148 | 98.4916 | 98.3933 | 97.1044 | 97.4718 | 98.1588 | 98.6012 | 98.396 | 98.369 | 98.3114 | 2023-09-01
Yaskawa Solectria Solar | XGI 1500-125/125-UL-A {600V} | N | Y | N | N | N | N | Y* | Y | 125 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 125 | 600 | 98.5 | TUV Rheinland | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-05-16 | 2024-06-11 |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 12.511 | 25.022 | 37.533 | 62.556 | 93.833 | 125.111 | 97.8 | 98.24 | 98.55 | 98.71 | 98.71 | 98.84 | 98.64 | 97.35 | 97.85 | 98.27 | 98.46 | 98.51 | 98.49 | 98.39 | 97.1 | 97.47 | 98.16 | 98.6 | 98.4 | 98.37 | 98.31 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500-125/150-UL {600V} | N | Y | N | N | N | N | Y* | N | 125 kW, 150 kVA, 600Vac 3-Phase Grid-Support Utility Interactive Inverter | 125 | 600 | 98.5 | TUV Rheinland of North America | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-05-16 | No Information Submitted |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 12.5214 | 25.0427 | 37.5641 | 62.6068 | 93.9102 | 125.2136 | 97.8024 | 98.2426 | 98.5526 | 98.7074 | 98.7076 | 98.8392 | 98.6361 | 97.3452 | 97.8518 | 98.2734 | 98.4604 | 98.5148 | 98.4916 | 98.3933 | 97.1044 | 97.4718 | 98.1588 | 98.6012 | 98.396 | 98.369 | 98.3114 | 2023-06-12
Yaskawa Solectria Solar | XGI 1500-125/150-UL-A {600V} | N | Y | N | N | N | N | Y* | Y | 125 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 125 | 600 | 98.5 | TUV Rheinland | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-05-16 | 2024-06-11 |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 12.511 | 25.022 | 37.533 | 62.556 | 93.833 | 125.111 | 97.8 | 98.24 | 98.55 | 98.71 | 98.71 | 98.84 | 98.64 | 97.35 | 97.85 | 98.27 | 98.46 | 98.51 | 98.49 | 98.39 | 97.1 | 97.47 | 98.16 | 98.6 | 98.4 | 98.37 | 98.31 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500-150/166-UL {600V} | N | Y | N | N | N | N | Y* | Y | 150 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 150 | 600 | 98.5 | TUV Rheinland of North America | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-05-16 | 2023-08-11 |  | N | N | 2.75 |  |  | 860 | 1000 | 1250 | 15.0388 | 30.0775 | 45.1163 | 75.1938 | 112.7907 | 150.3876 | 98.4688 | 98.9332 | 98.9862 | 98.8872 | 98.8088 | 98.718 | 98.8346 | 98.1948 | 98.2298 | 98.5054 | 98.5424 | 98.4976 | 98.38 | 98.4766 | 98.2596 | 98.2596 | 98.2786 | 98.3684 | 98.298 | 98.178 | 98.301 | 2023-08-11
Yaskawa Solectria Solar | XGI 1500-150/166-UL-A {600V} | N | Y | N | N | N | N | Y* | Y | 150 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 150 | 600 | 98.5 | TUV Rheinland | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-05-16 | 2024-06-11 |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 15.003 | 30.007 | 45.01 | 75.017 | 112.525 | 150.033 | 98.47 | 98.93 | 98.99 | 98.89 | 98.81 | 98.72 | 98.83 | 98.19 | 98.23 | 98.51 | 98.54 | 98.5 | 98.38 | 98.48 | 98.26 | 98.26 | 98.28 | 98.37 | 98.3 | 98.18 | 98.3 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500-166/166-3S {600V} | Y | Y | N | N | N | N | N | Y | 166 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 166 | 600 | 98.5 | TUV Rheinland of North America | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-06-11 |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 16.6009 | 33.2018 | 49.8028 | 83.0046 | 124.5069 | 166.0092 | 97.973 | 98.9236 | 99.2198 | 98.9218 | 98.8862 | 98.7352 | 98.8915 | 97.9882 | 98.0974 | 98.4554 | 98.6134 | 98.5788 | 98.4484 | 98.517 | 97.5094 | 97.6668 | 97.8232 | 98.1354 | 98.104 | 97.9988 | 98.026 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500-166/166-UL {600V} | N | Y | N | N | N | N | Y* | Y | 166 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 166 | 600 | 98.5 | TUV Rheinland of North America | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-05-16 | 2023-09-01 |  | N | N | 2.75 |  |  | 860 | 1000 | 1250 | 16.6068 | 33.2136 | 49.8204 | 83.034 | 124.551 | 166.068 | 97.973 | 98.9236 | 99.2198 | 98.9218 | 98.8862 | 98.7352 | 98.8915 | 97.9882 | 98.0974 | 98.4554 | 98.6134 | 98.5788 | 98.4484 | 98.517 | 97.5094 | 97.6668 | 97.8232 | 98.1354 | 98.104 | 97.9988 | 98.026 | 2023-09-01
Yaskawa Solectria Solar | XGI 1500-166/166-UL-A {600V} | N | Y | N | N | N | N | Y* | Y | 166 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 166 | 600 | 98.5 | TUV Rheinland | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-05-16 | 2024-06-11 |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 16.601 | 33.202 | 49.803 | 83.005 | 124.507 | 166.009 | 97.97 | 98.92 | 99.22 | 98.92 | 98.89 | 98.74 | 98.89 | 97.99 | 98.1 | 98.46 | 98.61 | 98.58 | 98.45 | 98.52 | 97.51 | 97.67 | 97.82 | 98.14 | 98.1 | 98 | 98.03 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500 175-480 {480V} | N | Y | N | N | N | N | Y* | Y | 175 kW 480 Vac Grid-Support Utility Interactive Inverters | 175 | 480 | 98.5 | TUV Rheinland | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2022-02-23 | 2023-04-21 |  | N | N | 0.25 |  |  | 860 | 1100 | 1250 | 17.5973 | 35.1945 | 52.7918 | 87.9863 | 131.9794 | 175.9726 | 98.6904 | 98.6564 | 98.6596 | 98.4576 | 98.1634 | 98.0654 | 98.3256 | 98.1476 | 98.5456 | 98.5186 | 98.3238 | 98.3072 | 98.1306 | 98.3328 | 98.2056 | 98.1258 | 98.2508 | 98.1602 | 98.3382 | 98.0278 | 98.2589 | 2023-04-21
Yaskawa Solectria Solar | XGI 1500-175-480-DCG {480V} | N | Y | N | N | N | N | N | Y | 175 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 175 | 480 | 98.5 | TUV Rheinland | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-06-11 |  | N | N | 0.25 |  |  | 860 | 1000 | 1250 | 17.524 | 35.049 | 52.573 | 87.622 | 131.433 | 175.244 | 98.69 | 98.66 | 98.66 | 98.46 | 98.16 | 98.07 | 98.33 | 98.15 | 98.55 | 98.52 | 98.32 | 98.31 | 98.13 | 98.33 | 98.21 | 98.13 | 98.25 | 98.16 | 98.34 | 98.03 | 98.26 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500 200/200-480 {480V} | N | Y | N | N | N | N | Y* | Y | 200 kW 480 Vac Grid-Support Utility Interactive Inverters | 200 | 480 | 98.5 | TUV Rheinland | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2022-02-23 | 2023-04-21 |  | N | N | 0.25 |  |  | 860 | 1100 | 1250 | 20.1963 | 40.3927 | 60.589 | 100.9817 | 151.4726 | 201.9634 | 98.6606 | 98.7222 | 98.6306 | 98.358 | 98.0206 | 97.693 | 98.209 | 98.4728 | 98.617 | 98.5158 | 98.2234 | 98.8578 | 98.5346 | 98.6399 | 98.481 | 98.441 | 98.439 | 98.2314 | 98.883 | 98.5274 | 98.6369 | 2023-04-21
Yaskawa Solectria Solar | XGI 1500-200/200-480-DCG {480V} | N | Y | N | N | N | N | N | Y | 200 kW, 480 Vac, Grid-Support Utility Interactive Inverter | 200 | 480 | 98.5 | TUV Rheinland | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-06-11 |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 20.28 | 40.56 | 60.839 | 101.399 | 152.099 | 202.798 | 98.66 | 98.72 | 98.63 | 98.36 | 98.02 | 97.69 | 98.21 | 98.47 | 98.62 | 98.52 | 98.22 | 98.86 | 98.53 | 98.64 | 98.48 | 98.44 | 98.44 | 98.23 | 98.88 | 98.53 | 98.64 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500 225-600 {600V} | N | Y | N | N | N | N | Y* | Y | 225 kW 600 Vac Grid-Support Utility Interactive Inverters | 225 | 600 | 98.5 | TUV Rheinland | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2022-02-23 | 2023-04-21 |  | N | N | 0.25 |  |  | 860 | 1100 | 1250 | 22.52 | 45.0401 | 67.5601 | 112.6002 | 168.9003 | 225.2004 | 98.531 | 98.9844 | 99.0338 | 98.843 | 98.69 | 98.4814 | 98.7613 | 97.9578 | 98.5964 | 98.6094 | 98.5448 | 98.3914 | 98.2254 | 98.4344 | 97.619 | 98.4006 | 98.5636 | 98.51 | 98.357 | 98.1716 | 98.3773 | 2023-04-21
Yaskawa Solectria Solar | XGI 1500-225-600-DCG {600V} | N | Y | N | N | N | N | N | Y | 225 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 225 | 600 | 98.5 | TUV Rheinland | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-06-11 |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 22.543 | 45.086 | 67.629 | 112.714 | 169.071 | 225.428 | 98.53 | 98.98 | 99.03 | 98.84 | 98.69 | 98.48 | 98.76 | 97.96 | 98.6 | 98.61 | 98.54 | 98.39 | 98.23 | 98.43 | 97.62 | 98.4 | 98.56 | 98.51 | 98.36 | 98.17 | 98.38 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500 250/250-600 {600V} | N | Y | N | N | N | N | Y* | Y | 250 kW 600 Vac Grid-Support Utility Interactive Inverters | 250 | 600 | 98.5 | TUV Rheinland | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2022-02-23 | 2023-04-21 |  | N | N | 0.33 |  |  | 860 | 1100 | 1250 | 25.0746 | 50.1491 | 75.2237 | 125.3728 | 188.0592 | 250.7456 | 98.6258 | 98.8768 | 98.925 | 98.7854 | 98.6236 | 98.3892 | 98.6948 | 98.042 | 98.6054 | 98.6498 | 98.4886 | 98.3166 | 98.1066 | 98.3857 | 97.6658 | 98.4366 | 98.4766 | 98.41 | 98.2532 | 97.9288 | 98.2824 | 2023-04-21
Yaskawa Solectria Solar | XGI 1500-250/250-600-DCG {600V} | N | Y | N | N | N | N | N | Y | 250 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 250 | 600 | 98.5 | TUV Rheinland | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-06-11 |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 25.009 | 50.017 | 75.026 | 125.043 | 187.565 | 250.086 | 98.63 | 98.88 | 98.93 | 98.79 | 98.62 | 98.39 | 98.69 | 98.04 | 98.61 | 98.65 | 98.49 | 98.32 | 98.11 | 98.39 | 97.67 | 98.44 | 98.48 | 98.41 | 98.25 | 97.93 | 98.28 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500-0.50MW-600 {600V} | Y | Y | N | N | N | N | N | Y | 500 kW, 600Vac Grid Support Utility Interactive Inverter | 500 | 600 | 98.5 | TUV Rheinland of North America | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-05-12 |  | N | N | 36.85 |  |  | 860 | 1100 | 1250 | 50.496 | 100.992 | 151.488 | 252.48 | 378.72 | 504.96 | 97 | 98.58 | 98.9 | 99.07 | 99.2 | 99.11 | 99.01 | 92.95 | 96.46 | 97.78 | 98.29 | 98.55 | 98.5 | 98.07 | 91.08 | 95.9 | 96.98 | 98.06 | 98.4 | 98.52 | 97.74 | 2025-05-12
Yaskawa Solectria Solar | SGI 500XTM {380V} | N | N | Y | N | N | N | N | N | 500 kW, 1000 Vdc, 380 Vac, 3-Phase Grid Support Utility Interactive Inverter | 507 | 380 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [01/09/2018] | [D003 Checksum- D9E00BD0] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data is inclusive of three Phase transformer from the CSA C82.2 table with transformer efficiency of 98.8%. | N | N | 88.78 |  |  | 545 | 615 | 820 | 50.7 | 101.4 | 152.1 | 253.5 | 380.25 | 507 | 93.6 | 96.1 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 93.2 | 95.8 | 96.5 | 96.9 | 97 | 97 | 96.7 | 92.1 | 95.3 | 96.1 | 96.6 | 96.8 | 96.8 | 96.4 | 2018-02-15
Yaskawa Solectria Solar | XGI 1500-0.75MW-600 {600V} | Y | Y | N | N | N | N | N | Y | 750 kW, 600Vac Grid Support Utility Interactive Inverter | 750 | 600 | 98.5 | TUV Rheinland of North America | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-05-12 |  | N | N | 36.85 |  |  | 860 | 1100 | 1250 | 75.341 | 150.683 | 226.024 | 376.707 | 565.061 | 753.414 | 96.15 | 97.89 | 98.54 | 98.98 | 99.09 | 99.05 | 98.82 | 92.88 | 96.93 | 97.71 | 98.27 | 98.54 | 98.59 | 98.08 | 91.68 | 96.58 | 97.56 | 98.03 | 98.45 | 98.56 | 97.89 | 2025-05-12
Yaskawa Solectria Solar | SGI 750XTM {380V} | N | N | Y | N | N | N | N | N | 750 kW, 1000 Vdc, 380Vac, 3-Phase Grid Support Utility Interactive Inverter | 753.2 | 380 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [01/09/2018] | [D003 Checksum- D9E00BD0] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data is inclusive of three Phase transformer from the CSA C82.2 table with transformer efficiency of 98.8%. | N | N | 122.55 |  |  | 545 | 615 | 820 | 75.32 | 150.64 | 225.96 | 376.6 | 564.9 | 753.2 | 94 | 96.2 | 96.7 | 97 | 97 | 96.9 | 96.8 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 97 | 96.9 | 91.9 | 95.3 | 96.2 | 96.7 | 96.7 | 96.8 | 96.4 | 2018-02-15
Yaskawa Solectria Solar | XGI 1500-0.85MW-600 {600V} | Y | Y | N | N | N | N | N | Y | 850 kW, 600Vac Grid Support Utility Interactive Inverter | 850 | 600 | 98.5 | TUV Rheinland of North America | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-05-12 |  | N | N | 36.85 |  |  | 860 | 1100 | 1250 | 85.335 | 170.67 | 256.004 | 426.674 | 640.011 | 853.348 | 96.54 | 98.26 | 98.81 | 99.09 | 99.14 | 99.07 | 98.94 | 93.23 | 97 | 97.98 | 98.42 | 98.62 | 98.58 | 98.2 | 90.95 | 95.79 | 97.4 | 97.98 | 98.3 | 98.35 | 97.71 | 2025-05-12
Yaskawa Solectria Solar | XGI 1500-0.99MW-600 {600V} | Y | Y | N | N | N | N | N | Y | 999 kW, 600Vac Grid Support Utility Interactive Inverter | 999 | 600 | 98.5 | TUV Rheinland of North America | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-05-12 |  | N | N | 36.85 |  |  | 860 | 1100 | 1250 | 99.969 | 199.938 | 299.906 | 499.844 | 749.766 | 999.688 | 96.96 | 98.22 | 98.75 | 99.07 | 99.09 | 98.96 | 98.91 | 94.3 | 97.15 | 98.02 | 98.51 | 98.58 | 98.47 | 98.25 | 92.65 | 96.26 | 97.33 | 98.04 | 98.21 | 98.17 | 97.74 | 2025-05-12
Yaskawa Solectria Solar | XGI 1500-1MW-600 {600V} | Y | Y | N | N | N | N | N | Y | 1000 kW, 600Vac Grid Support Utility Interactive Inverter | 1000 | 600 | 98.5 | TUV Rheinland of North America | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-05-12 |  | N | N | 36.85 |  |  | 860 | 1100 | 1250 | 100.21 | 200.42 | 300.629 | 501.049 | 751.574 | 1002.098 | 96.96 | 98.22 | 98.75 | 99.07 | 99.09 | 98.96 | 98.91 | 94.3 | 97.15 | 98.02 | 98.51 | 98.58 | 98.47 | 98.25 | 92.65 | 96.26 | 97.33 | 98.04 | 98.21 | 98.17 | 97.74 | 2025-05-12
Yotta Energy, Inc. | DPI-208 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 1728 VA, 208 Vac Grid Support Utility Interactive Inverter | 1.733 | 208 | 96 | CSA Group | [4/6/2023] | CSA Group | [9/22/2022];[4/6/2023] | [V3] | 2022-11-01 | [9/22/2022];[4/6/2023] | 2022-11-01 | CSA Group | 2022-09-23 | 2022-11-01 | This microinverter can be utilized in Energy Storage System applications, paired only with Yotta SL-1000 battery system. | N | Y | 0.087 |  |  | 34 | 38 | 42 | 0.17335 | 0.34669 | 0.52004 | 0.86673 | 1.3001 | 1.7335 | 91.7047 | 94.9566 | 95.8278 | 96.4736 | 96.2718 | 95.6544 | 95.9816 | 91.1033 | 94.6328 | 95.5262 | 96.2977 | 96.0945 | 95.5277 | 95.7679 | 90.7908 | 94.3068 | 95.2091 | 96.1291 | 96.0151 | 95.4601 | 95.6202 | 2022-11-01 | 2023-07-21
Yotta Energy, Inc. | DPI-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 1800 VA, 480 Vac Grid Support Utility Interactive Inverter | 1.821 | 480 | 95.5 | CSA Group | [4/6/2023] | CSA Group | [9/22/2022];[4/6/2023] | [V3] | 2022-11-01 | [9/22/2022];[4/6/2023] | 2022-11-01 | CSA Group | 2022-09-23 | 2022-11-01 | This microinverter can be utilized in Energy Storage System applications, paired only with Yotta SL-1000 battery system. | N | Y | 0.2248 |  |  | 34 | 38 | 42 | 0.18209 | 0.36418 | 0.54628 | 0.91046 | 1.3657 | 1.8209 | 91.7619 | 95.0301 | 95.8934 | 95.8613 | 96.5617 | 96.4818 | 96.0618 | 91.0471 | 94.4013 | 95.2407 | 94.6659 | 95.9417 | 95.9714 | 95.3184 | 90.5428 | 93.7744 | 94.5888 | 95.1333 | 95.1599 | 95.6227 | 94.855 | 2022-11-01 | 2023-07-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M400-S-NA {208V} | N | Y | N | N | N | N | Y* | Y | 0.360 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.366 | 208 | 95.5 | CSA Group | [4/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.014 |  |  | 35 | 42 | 50 | 0.037 | 0.073 | 0.11 | 0.183 | 0.274 | 0.366 | 95.1 | 95.33 | 95.51 | 95.11 | 95.97 | 95.21 | 95.63 | 93.99 | 95.33 | 95.29 | 95.89 | 95.93 | 95.53 | 95.72 | 94.31 | 94.52 | 95.48 | 96.09 | 95.72 | 95.49 | 95.64 | 2024-07-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M400-SW-NA {208V} | N | Y | N | N | N | N | Y* | Y | 0.360 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.366 | 208 | 95.5 | CSA Group | [4/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.014 |  |  | 35 | 42 | 50 | 0.037 | 0.073 | 0.11 | 0.183 | 0.274 | 0.366 | 95.1 | 95.33 | 95.51 | 95.11 | 95.97 | 95.21 | 95.63 | 93.99 | 95.33 | 95.29 | 95.89 | 95.93 | 95.53 | 95.72 | 94.31 | 94.52 | 95.48 | 96.09 | 95.72 | 95.49 | 95.64 | 2024-07-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M400-S-NA {240V} | N | Y | N | N | N | N | Y* | Y | 0.360 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.367 | 240 | 95.5 | CSA Group | [4/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.02 |  |  | 35 | 42 | 50 | 0.037 | 0.073 | 0.11 | 0.183 | 0.275 | 0.367 | 95.24 | 95.42 | 94.34 | 94.92 | 94.97 | 95.05 | 94.92 | 94.54 | 95.21 | 95.53 | 95.53 | 96.21 | 95.04 | 95.81 | 92.98 | 95.11 | 95.42 | 95.35 | 95.78 | 95.94 | 95.51 | 2024-07-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M400-SW-NA {240V} | N | Y | N | N | N | N | Y* | Y | 0.360 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.367 | 240 | 95.5 | CSA Group | [4/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.02 |  |  | 35 | 42 | 50 | 0.037 | 0.073 | 0.11 | 0.183 | 0.275 | 0.367 | 95.24 | 95.42 | 94.34 | 94.92 | 94.97 | 95.05 | 94.92 | 94.54 | 95.21 | 95.53 | 95.53 | 96.21 | 95.04 | 95.81 | 92.98 | 95.11 | 95.42 | 95.35 | 95.78 | 95.94 | 95.51 | 2024-07-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M500-S-NA {208V} | N | Y | N | N | N | N | Y* | Y | 0.475 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.478 | 208 | 95.5 | CSA Group | [4/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.008 |  |  | 35 | 42 | 50 | 0.048 | 0.096 | 0.143 | 0.239 | 0.359 | 0.478 | 95.24 | 94.96 | 95.47 | 95.99 | 95.52 | 95.15 | 95.55 | 94.74 | 95.42 | 95.71 | 95.5 | 95.03 | 95.69 | 95.25 | 94.45 | 95.02 | 95.43 | 95.96 | 95.49 | 95.02 | 95.49 | 2024-07-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M500-SW-NA {208V} | N | Y | N | N | N | N | Y* | Y | 0.475 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.478 | 208 | 95.5 | CSA Group | [4/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.008 |  |  | 35 | 42 | 50 | 0.048 | 0.096 | 0.143 | 0.239 | 0.359 | 0.478 | 95.24 | 94.96 | 95.47 | 95.99 | 95.52 | 95.15 | 95.55 | 94.74 | 95.42 | 95.71 | 95.5 | 95.03 | 95.69 | 95.25 | 94.45 | 95.02 | 95.43 | 95.96 | 95.49 | 95.02 | 95.49 | 2024-07-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M500-S-NA {240V} | N | Y | N | N | N | N | Y* | Y | 0.475 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.479 | 240 | 96 | CSA Group | [4/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.03 |  |  | 35 | 42 | 50 | 0.048 | 0.096 | 0.144 | 0.24 | 0.36 | 0.479 | 95.49 | 95.52 | 95.66 | 95.36 | 95.7 | 95.93 | 95.62 | 94.68 | 95.81 | 95.74 | 96.47 | 96.21 | 95.45 | 96.09 | 95.26 | 95.24 | 95.99 | 96.44 | 95.88 | 95.74 | 95.95 | 2024-07-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M500-SW-NA {240V} | N | Y | N | N | N | N | Y* | Y | 0.475 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.479 | 240 | 96 | CSA Group | [4/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.03 |  |  | 35 | 42 | 50 | 0.048 | 0.096 | 0.144 | 0.24 | 0.36 | 0.479 | 95.49 | 95.52 | 95.66 | 95.36 | 95.7 | 95.93 | 95.62 | 94.68 | 95.81 | 95.74 | 96.47 | 96.21 | 95.45 | 96.09 | 95.26 | 95.24 | 95.99 | 96.44 | 95.88 | 95.74 | 95.95 | 2024-07-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M600-S-NA {208V} | N | Y | N | N | N | N | Y* | Y | 0.548 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.548 | 208 | 96 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.2 |  |  | 35 | 42 | 50 | 0.055 | 0.11 | 0.165 | 0.274 | 0.411 | 0.548 | 96.26 | 96.22 | 96.28 | 96.3 | 96.2 | 95.93 | 96.22 | 96.06 | 96.37 | 96.24 | 96.6 | 96.16 | 96.04 | 96.26 | 96.17 | 96.17 | 96.22 | 96.35 | 96.09 | 96.03 | 96.16 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M600-SW-NA {208V} | N | Y | N | N | N | N | Y* | Y | 0.548 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.548 | 208 | 96 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.2 |  |  | 35 | 42 | 50 | 0.054838 | 0.10968 | 0.16451 | 0.27419 | 0.41129 | 0.54838 | 96.2555 | 96.222 | 96.2822 | 96.304 | 96.199 | 95.9345 | 96.2212 | 96.0573 | 96.3722 | 96.242 | 96.5991 | 96.1558 | 96.0355 | 96.2601 | 96.1652 | 96.1734 | 96.2168 | 96.35 | 96.0904 | 96.0274 | 96.1641 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M600-S-NA {240V} | N | Y | N | N | N | N | Y* | Y | 0.548 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.549 | 240 | 96 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.2 |  |  | 35 | 42 | 50 | 0.055 | 0.11 | 0.165 | 0.274 | 0.412 | 0.549 | 96.2 | 96.15 | 96.27 | 96.32 | 96.2 | 95.99 | 96.22 | 96.15 | 96.21 | 96.24 | 96.32 | 96.28 | 95.65 | 96.24 | 96.11 | 96.2 | 96.24 | 96.26 | 96.24 | 95.93 | 96.22 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M600-SW-NA {240V} | N | Y | N | N | N | N | Y* | Y | 0.548 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.549 | 240 | 96 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.2 |  |  | 35 | 42 | 50 | 0.055 | 0.11 | 0.165 | 0.274 | 0.412 | 0.549 | 96.2 | 96.15 | 96.27 | 96.32 | 96.2 | 95.99 | 96.22 | 96.15 | 96.21 | 96.24 | 96.32 | 96.28 | 95.65 | 96.24 | 96.11 | 96.2 | 96.24 | 96.26 | 96.24 | 95.93 | 96.22 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M600-S {240V} | N | Y | N | N | N | N | N | N | 0.6 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.60412 | 240 | 96.5 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.7 |  |  | 35 | 42 | 50 | 0.060412 | 0.12082 | 0.18124 | 0.30206 | 0.45309 | 0.60412 | 96.8037 | 96.0663 | 95.6242 | 96.8963 | 97.9767 | 95.9794 | 97.2252 | 95.9534 | 96.0087 | 95.5371 | 96.3311 | 97.4044 | 96.0642 | 96.7601 | 95.0711 | 96.1103 | 95.9092 | 95.784 | 96.155 | 95.7088 | 95.9797 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M600-SW {240V} | N | Y | N | N | N | N | N | N | 0.6 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.60412 | 240 | 96.5 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.7 |  |  | 35 | 42 | 50 | 0.060412 | 0.12082 | 0.18124 | 0.30206 | 0.45309 | 0.60412 | 96.8037 | 96.0663 | 95.6242 | 96.8963 | 97.9767 | 95.9794 | 97.2252 | 95.9534 | 96.0087 | 95.5371 | 96.3311 | 97.4044 | 96.0642 | 96.7601 | 95.0711 | 96.1103 | 95.9092 | 95.784 | 96.155 | 95.7088 | 95.9797 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M600-S {208V} | N | Y | N | N | N | N | N | N | 0.6 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.60836 | 208 | 96.5 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.2 |  |  | 35 | 42 | 50 | 0.060836 | 0.12167 | 0.18251 | 0.30418 | 0.45627 | 0.60836 | 94.802 | 95.9074 | 95.8721 | 96.8963 | 96.6872 | 96.5717 | 96.5132 | 96.3571 | 96.477 | 95.7722 | 95.9097 | 96.4804 | 96.6999 | 96.2814 | 96.6819 | 95.5282 | 96.4058 | 96.8878 | 96.3044 | 96.1516 | 96.4077 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M600-SW {208V} | N | Y | N | N | N | N | N | N | 0.6 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.60836 | 208 | 96.5 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.2 |  |  | 35 | 42 | 50 | 0.060836 | 0.12167 | 0.18251 | 0.30418 | 0.45627 | 0.60836 | 94.802 | 95.9074 | 95.8721 | 96.8963 | 96.6872 | 96.5717 | 96.5132 | 96.3571 | 96.477 | 95.7722 | 95.9097 | 96.4804 | 96.6999 | 96.2814 | 96.6819 | 95.5282 | 96.4058 | 96.8878 | 96.3044 | 96.1516 | 96.4077 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M800-S-NA {208V} | N | Y | N | N | N | N | Y* | Y | 0.720 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.721 | 208 | 96 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.3 |  |  | 35 | 42 | 50 | 0.072 | 0.144 | 0.216 | 0.361 | 0.541 | 0.721 | 96.19 | 96.15 | 96.38 | 96.43 | 96.21 | 96.24 | 96.27 | 96.3 | 96.28 | 96.22 | 96.54 | 96.12 | 95.87 | 96.22 | 95.33 | 96.13 | 96.04 | 96.35 | 96.15 | 95.8 | 96.13 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M800-SW-NA {208V} | N | Y | N | N | N | N | Y* | Y | 0.720 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.721 | 208 | 96 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.3 |  |  | 35 | 42 | 50 | 0.072 | 0.144 | 0.216 | 0.361 | 0.541 | 0.721 | 96.19 | 96.15 | 96.38 | 96.43 | 96.21 | 96.24 | 96.27 | 96.3 | 96.28 | 96.22 | 96.54 | 96.12 | 95.87 | 96.22 | 95.33 | 96.13 | 96.04 | 96.35 | 96.15 | 95.8 | 96.13 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M800-S-NA {240V} | N | Y | N | N | N | N | Y* | Y | 0.720 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.723 | 240 | 96 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.4 |  |  | 35 | 42 | 50 | 0.072 | 0.145 | 0.217 | 0.362 | 0.542 | 0.723 | 96.26 | 96.22 | 96.15 | 96.42 | 96.37 | 96.1 | 96.33 | 94.72 | 96.24 | 96.23 | 96.44 | 96.22 | 95.86 | 96.19 | 96.1 | 95.95 | 96.26 | 96.12 | 96.16 | 95.84 | 96.13 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M800-SW-NA {240V} | N | Y | N | N | N | N | Y* | Y | 0.720 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.723 | 240 | 96 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.4 |  |  | 35 | 42 | 50 | 0.072 | 0.145 | 0.217 | 0.362 | 0.542 | 0.723 | 96.26 | 96.22 | 96.15 | 96.42 | 96.37 | 96.1 | 96.33 | 94.72 | 96.24 | 96.23 | 96.44 | 96.22 | 95.86 | 96.19 | 96.1 | 95.95 | 96.26 | 96.12 | 96.16 | 95.84 | 96.13 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M800-S {240V} | N | Y | N | N | N | N | N | N | 0.8 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.80012 | 240 | 96.5 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.23 |  |  | 35 | 42 | 50 | 0.080012 | 0.16002 | 0.24004 | 0.40006 | 0.60009 | 0.80012 | 96.3717 | 97.0774 | 96.1956 | 96.8963 | 96.0392 | 93.7512 | 96.1888 | 95.9053 | 96.6536 | 97.0635 | 98.058 | 96.3628 | 94.0804 | 96.685 | 95.4745 | 95.5748 | 97.1111 | 97.2619 | 97.066 | 95.6257 | 96.9023 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M800-SW {240V} | N | Y | N | N | N | N | N | N | 0.8 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.80012 | 240 | 96.5 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.23 |  |  | 35 | 42 | 50 | 0.080012 | 0.16002 | 0.24004 | 0.40006 | 0.60009 | 0.80012 | 96.3717 | 97.0774 | 96.1956 | 96.8963 | 96.0392 | 93.7512 | 96.1888 | 95.9053 | 96.6536 | 97.0635 | 98.058 | 96.3628 | 94.0804 | 96.685 | 95.4745 | 95.5748 | 97.1111 | 97.2619 | 97.066 | 95.6257 | 96.9023 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M800-S {208V} | N | Y | N | N | N | N | N | N | 0.8 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.80039 | 208 | 96 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.23 |  |  | 35 | 42 | 50 | 0.080039 | 0.16008 | 0.24012 | 0.40019 | 0.60029 | 0.80039 | 95.3515 | 96.0277 | 95.7675 | 96.8963 | 95.9563 | 95.5367 | 96.0895 | 96.1239 | 95.4933 | 95.5283 | 95.617 | 96.0796 | 95.8535 | 95.8775 | 94.4585 | 95.1759 | 95.8249 | 95.9753 | 96.4027 | 96.0689 | 96.0878 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M800-SW {208V} | N | Y | N | N | N | N | N | N | 0.8 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.80039 | 208 | 96 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.23 |  |  | 35 | 42 | 50 | 0.080039 | 0.16008 | 0.24012 | 0.40019 | 0.60029 | 0.80039 | 95.3515 | 96.0277 | 95.7675 | 96.8963 | 95.9563 | 95.5367 | 96.0895 | 96.1239 | 95.4933 | 95.5283 | 95.617 | 96.0796 | 95.8535 | 95.8775 | 94.4585 | 95.1759 | 95.8249 | 95.9753 | 96.4027 | 96.0689 | 96.0878 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M1000-S-NA {240V} | N | Y | N | N | N | N | Y* | Y | 0.960 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.958 | 240 | 96.5 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.5 |  |  | 35 | 42 | 50 | 0.096 | 0.192 | 0.287 | 0.479 | 0.718 | 0.958 | 96.24 | 96.29 | 96.11 | 96.46 | 96.34 | 95.09 | 96.27 | 95.22 | 96.38 | 96.26 | 96.55 | 96.41 | 95.56 | 96.33 | 95.93 | 96.25 | 96.33 | 96.35 | 96.15 | 95.6 | 96.18 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M1000-SW-NA {240V} | N | Y | N | N | N | N | Y* | Y | 0.960 kW, 240 Vac Grid Support Utility Interactive Microinverter | 0.958 | 240 | 96.5 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.5 |  |  | 35 | 42 | 50 | 0.096 | 0.192 | 0.287 | 0.479 | 0.718 | 0.958 | 96.24 | 96.29 | 96.11 | 96.46 | 96.34 | 95.09 | 96.27 | 95.22 | 96.38 | 96.26 | 96.55 | 96.41 | 95.56 | 96.33 | 95.93 | 96.25 | 96.33 | 96.35 | 96.15 | 95.6 | 96.18 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M1000-S-NA {208V} | N | Y | N | N | N | N | Y* | Y | 0.960 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.962 | 208 | 96 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.3 |  |  | 35 | 42 | 50 | 0.096 | 0.192 | 0.289 | 0.481 | 0.722 | 0.962 | 96.41 | 96.41 | 96.4 | 96.41 | 96.31 | 95.83 | 96.33 | 95.7 | 95.5 | 96.54 | 96.46 | 96.15 | 96.4 | 96.22 | 95.05 | 94.63 | 96.38 | 96.34 | 96.26 | 96.6 | 96.18 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M1000-SW-NA {208V} | N | Y | N | N | N | N | Y* | Y | 0.960 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.962 | 208 | 96 | CSA Group | [1/31/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-24 | 2024-11-01 |  | N | Y | 0.3 |  |  | 35 | 42 | 50 | 0.096 | 0.192 | 0.289 | 0.481 | 0.722 | 0.962 | 96.41 | 96.41 | 96.4 | 96.41 | 96.31 | 95.83 | 96.33 | 95.7 | 95.5 | 96.54 | 96.46 | 96.15 | 96.4 | 96.22 | 95.05 | 94.63 | 96.38 | 96.34 | 96.26 | 96.6 | 96.18 | 2024-05-13 | 2024-11-01
Zhejiang Hyxi Technology Co., Ltd | HYX-M1000-S {208V} | N | Y | N | N | N | N | N | N | 1 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.9938 | 208 | 96.5 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.11 |  |  | 35 | 42 | 50 | 0.09938 | 0.19876 | 0.29814 | 0.4969 | 0.74535 | 0.9938 | 94.8389 | 95.1632 | 96.3585 | 96.8963 | 96.2311 | 96.3252 | 96.2817 | 95.4059 | 96.3941 | 96.615 | 96.911 | 97.2046 | 95.6185 | 96.8804 | 95.8743 | 95.0963 | 96.5121 | 96.6598 | 96.5588 | 97.1322 | 96.5026 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M1000-SW {208V} | N | Y | N | N | N | N | N | N | 1 kW, 208 Vac Grid Support Utility Interactive Microinverter | 0.9938 | 208 | 96.5 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.11 |  |  | 35 | 42 | 50 | 0.09938 | 0.19876 | 0.29814 | 0.4969 | 0.74535 | 0.9938 | 94.8389 | 95.1632 | 96.3585 | 96.8963 | 96.2311 | 96.3252 | 96.2817 | 95.4059 | 96.3941 | 96.615 | 96.911 | 97.2046 | 95.6185 | 96.8804 | 95.8743 | 95.0963 | 96.5121 | 96.6598 | 96.5588 | 97.1322 | 96.5026 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M1000-S {240V} | N | Y | N | N | N | N | N | N | 1 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.0622 | 240 | 96.5 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.13 |  |  | 35 | 42 | 50 | 0.10622 | 0.21243 | 0.31865 | 0.53108 | 0.79662 | 1.0622 | 96.2013 | 96.4271 | 96.2333 | 95.9093 | 96.9055 | 96.2318 | 96.5299 | 95.7771 | 96.6314 | 96.6278 | 96.3144 | 96.5852 | 96.2115 | 96.4847 | 95.0948 | 96.5864 | 96.6371 | 96.0928 | 97.2478 | 96.2319 | 96.762 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M1000-SW {240V} | N | Y | N | N | N | N | N | N | 1 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.0622 | 240 | 96.5 | CSA Group | [11/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | Y | 0.13 |  |  | 35 | 42 | 50 | 0.10622 | 0.21243 | 0.31865 | 0.53108 | 0.79662 | 1.0622 | 96.2013 | 96.4271 | 96.2333 | 95.9093 | 96.9055 | 96.2318 | 96.5299 | 95.7771 | 96.6314 | 96.6278 | 96.3144 | 96.5852 | 96.2115 | 96.4847 | 95.0948 | 96.5864 | 96.6371 | 96.0928 | 97.2478 | 96.2319 | 96.762 | 2024-02-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M1800-S-NA {208V} | N | Y | N | N | N | N | Y* | Y | 1.66 kW, 208 Vac Grid Support Utility Interactive Microinverter | 1.655 | 208 | 96 | CSA Group | [2/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-30 | 2025-03-21 |  | N | Y | 0.1 |  |  | 35 | 42 | 50 | 0.16553 | 0.33106 | 0.4966 | 0.82766 | 1.2415 | 1.6553 | 94.3316 | 95.1957 | 95.5913 | 95.8156 | 96.2774 | 95.6232 | 95.9335 | 93.6969 | 94.9393 | 95.4203 | 95.9799 | 96.4267 | 95.8476 | 95.9996 | 92.9028 | 94.9295 | 95.2148 | 95.7578 | 96.4247 | 95.8513 | 95.8952 | 2024-06-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M1800-SW-NA {208V} | N | Y | N | N | N | N | Y* | Y | 1.66 kW, 208 Vac Grid Support Utility Interactive Microinverter | 1.655 | 208 | 96 | CSA Group | [2/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-30 | 2025-03-21 |  | N | Y | 0.1 |  |  | 35 | 42 | 50 | 0.16553 | 0.33106 | 0.4966 | 0.82766 | 1.2415 | 1.6553 | 94.3316 | 95.1957 | 95.5913 | 95.8156 | 96.2774 | 95.6232 | 95.9335 | 93.6969 | 94.9393 | 95.4203 | 95.9799 | 96.4267 | 95.8476 | 95.9996 | 92.9028 | 94.9295 | 95.2148 | 95.7578 | 96.4247 | 95.8513 | 95.8952 | 2024-06-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M1800-S-NA {240V} | N | Y | N | N | N | N | Y* | Y | 1.66 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.656 | 240 | 94.5 | CSA Group | [2/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-30 | 2025-03-21 |  | N | Y | 0.034 |  |  | 35 | 42 | 50 | 0.16555 | 0.33111 | 0.49666 | 0.82777 | 1.2417 | 1.6555 | 92.4076 | 95.9834 | 94.62 | 94.7966 | 94.8713 | 93.833 | 94.7306 | 94.058 | 95.8686 | 96.008 | 92.4746 | 94.82 | 94.7991 | 94.4909 | 94.2755 | 95.6438 | 95.1127 | 95.3602 | 94.8049 | 94.8914 | 94.9835 | 2024-06-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M1800-SW-NA {240V} | N | Y | N | N | N | N | Y* | Y | 1.66 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.656 | 240 | 94.5 | CSA Group | [2/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-30 | 2025-03-21 |  | N | Y | 0.034 |  |  | 35 | 42 | 50 | 0.16555 | 0.33111 | 0.49666 | 0.82777 | 1.2417 | 1.6555 | 92.4076 | 95.9834 | 94.62 | 94.7966 | 94.8713 | 93.833 | 94.7306 | 94.058 | 95.8686 | 96.008 | 92.4746 | 94.82 | 94.7991 | 94.4909 | 94.2755 | 95.6438 | 95.1127 | 95.3602 | 94.8049 | 94.8914 | 94.9835 | 2024-06-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M2000-S-NA {240V} | N | Y | N | N | N | N | Y* | Y | 1.92 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.91 | 240 | 96 | CSA Group | [2/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-30 | 2025-03-21 |  | N | Y | 0.034 |  |  | 35 | 42 | 50 | 0.19103 | 0.38205 | 0.57308 | 0.95513 | 1.4327 | 1.9103 | 95.8001 | 95.874 | 95.6189 | 95.4989 | 96.26 | 95.7317 | 95.9591 | 95.1908 | 95.649 | 95.2122 | 95.853 | 96.2477 | 95.8462 | 95.9483 | 96.1328 | 95.1143 | 95.7101 | 96.0079 | 95.8571 | 95.7082 | 95.8376 | 2024-06-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M2000-SW-NA {240V} | N | Y | N | N | N | N | Y* | Y | 1.92 kW, 240 Vac Grid Support Utility Interactive Microinverter | 1.91 | 240 | 96 | CSA Group | [2/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-30 | 2025-03-21 |  | N | Y | 0.034 |  |  | 35 | 42 | 50 | 0.19103 | 0.38205 | 0.57308 | 0.95513 | 1.4327 | 1.9103 | 95.8001 | 95.874 | 95.6189 | 95.4989 | 96.26 | 95.7317 | 95.9591 | 95.1908 | 95.649 | 95.2122 | 95.853 | 96.2477 | 95.8462 | 95.9483 | 96.1328 | 95.1143 | 95.7101 | 96.0079 | 95.8571 | 95.7082 | 95.8376 | 2024-06-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M2000-S-NA {208V} | N | Y | N | N | N | N | Y* | Y | 1.92 kW, 208 Vac Grid Support Utility Interactive Microinverter | 1.914 | 208 | 97 | CSA Group | [2/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-30 | 2025-03-21 |  | N | Y | 0.026 |  |  | 35 | 42 | 50 | 0.19142 | 0.38285 | 0.57427 | 0.95712 | 1.4357 | 1.9142 | 95.6159 | 96.8323 | 97.5282 | 97.2084 | 96.5136 | 94.823 | 96.6768 | 94.9546 | 96.5035 | 97.0596 | 97.4252 | 96.7889 | 95.5139 | 96.8036 | 93.9465 | 96.088 | 96.77 | 97.4788 | 96.9105 | 96.8075 | 96.8482 | 2024-06-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-M2000-SW-NA {208V} | N | Y | N | N | N | N | Y* | Y | 1.92 kW, 208 Vac Grid Support Utility Interactive Microinverter | 1.914 | 208 | 97 | CSA Group | [2/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-30 | 2025-03-21 |  | N | Y | 0.026 |  |  | 35 | 42 | 50 | 0.19142 | 0.38285 | 0.57427 | 0.95712 | 1.4357 | 1.9142 | 95.6159 | 96.8323 | 97.5282 | 97.2084 | 96.5136 | 94.823 | 96.6768 | 94.9546 | 96.5035 | 97.0596 | 97.4252 | 96.7889 | 95.5139 | 96.8036 | 93.9465 | 96.088 | 96.77 | 97.4788 | 96.9105 | 96.8075 | 96.8482 | 2024-06-11 | 2025-03-21
Zhejiang Hyxi Technology Co., Ltd | HYX-H-HSPA {240V} | Y | Y | N | N | N | N | N | N | 11.5kW, 240Vac Grid Support Utility Interactive Inverter | 11.147 | 240 | 96 | TUV Rheinland of North America | [1/5/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.05 |  |  | 200 | 350 | 500 | 1.115 | 2.229 | 3.344 | 5.573 | 8.36 | 11.147 | 93.87 | 95.67 | 96.07 | 96.19 | 95.74 | 97.45 | 95.88 | 93.82 | 95.7 | 96.17 | 96.23 | 95.9 | 95.57 | 95.89 | 93.86 | 95.69 | 96.17 | 96.23 | 95.92 | 95.49 | 95.9 | 2025-03-21
Zhuhai Ruixu Electronic Technology Co., Ltd | RX-12K {208V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.8807 | 208 | 96.5 | Intertek | [10/18/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 24.1 |  |  | 190 | 380 | 510 | 0.98807 | 1.9761 | 2.9642 | 4.9403 | 7.4105 | 9.8807 | 91.2599 | 94.3745 | 95.5505 | 96.3072 | 96.3427 | 95.9977 | 95.9212 | 92.7067 | 95.4866 | 96.9869 | 97.2662 | 97.3087 | 97.1489 | 96.978 | 90.94 | 94.226 | 96.3799 | 97.1281 | 97.2907 | 97.2045 | 96.7357 | 2025-09-02
Zhuhai Ruixu Electronic Technology Co., Ltd | RX-12K {240V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.2981 | 240 | 96.5 | Intertek | [10/18/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 24 |  |  | 190 | 380 | 510 | 1.1298 | 2.2596 | 3.3894 | 5.649 | 8.4736 | 11.2981 | 92.0154 | 94.7699 | 95.7195 | 96.3851 | 96.3008 | 96.1752 | 95.9945 | 93.0107 | 95.727 | 96.7399 | 97.4337 | 97.3657 | 97.355 | 97.0482 | 91.9487 | 95.0137 | 96.5928 | 97.2894 | 97.1867 | 97.2073 | 96.8199 | 2025-09-02

## Battery_Inverters
Grid Support Battery Inverter List (Full Data)
Data has not changed since October 12, 2026
This list contains an extensive amount of equipment information. If you require any assistance, please reach out to us at SolarEquipment@energy.ca.gov or 916-654-4120.
Inverter List Notes
This row is intentionally left blank.
(1) Any text in curly brackets at the end of the Model Number is not part of the Manufacturer's Model Number. Part of the text in curly brackets indicates the specified voltage option for that model number, if provided; models with multiple voltage options will have multiple row entries, with one for each eligible option.
(2) Hybrid inverters are capable of taking DC power input from both a solar system and an energy storage system. These models are listed on both the solar and battery inverter lists to reflect the dual functionality. Refer to the manufacturer's documentation for more information on the exact functionality and limitations.
(3) RPP: UL 1741 SA13 tested with reactive power priority enabled (when operating at apparent power capacity, inverter will reduce active power as needed to ensure curve-required reactive power is provided)
(4) A Y* notes the inverter has not been certified according to CSIP, but instead NRTL reported inverter was connected to a gateway during compatibility testing.
(5) The listed Firmware Version is the version used during the inverter's UL 1741 Supplement SA (SA8-SA13) testing and certified on the listed Certificate Date; multiple firmware versions may be listed for a single certificate date if all are required to comply with Supplement SA. Multiple certificate dates with different firmware versions may be listed if new firmware versions were certified under Supplement SA and reported by the manufacturer. Additional firmware versions may be certified but not reported. Check with NRTL for the most current information.
(6) Inverter CSIP conformance information refers to the entity responsible for the documentation provided to the manufacturer. If the inverter is certified to CSIP, then the information refers to the certifying entity and the certificate date. Otherwise, the information refers to the NRTL that issued the compatibility report and the date of the report.
(7) The 'Monitor Key Data Scheduling Attestation' is no longer required by California Investor Owned Utilities and the CEC no longer collects this information.
(8) The anti-island detection method information is from a manufacturer self-attestation.
Blue colored text indicates that the model number occurs multiple times on the list under different manufacturer names.
Manufacturer Name | Model Number1 | Hybrid Inverter2 | UL 1741 Supplement SB Certification | UL 1741 Supplement SA Testing | UL 1741 SA13 Volt-Var | UL 1741 SA Freq-Watt Volt-Watt | UL 1741 SA Disable Permit Service Limit Active Power | Common Smart Inverter Profile Conformance | Monitor Key Data Scheduling | Description | Maximum Continuous Output Power at Unity Power Factor | Nominal Voltage | Weighted Efficiency | UL 1741 (3rd Ed.) Supplement SB Certification |  | UL 1741 Supplement SA Certification (SA8-SA13)5 |  |  | UL 1741 SA13 Volt-Var | UL 1741 SA Freq-Watt Volt-Watt | UL 1741 SA Disable Permit Service Limit Active Power | Inverter CSIP Conformance6 |  | Monitor Key Data Scheduling Attestation7 | Notes | Built-In Meter | Microinverter | Night Tare Loss | Power Rating, Continuous, 40 deg C | Night Tare Loss, 40 deg C | Voltage Minimum | Voltage Nominal | Voltage Maximum | Power Level | Power Level | Power Level | Power Level | Power Level | Power Level | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Grid Support Listing Date | Last Update | Group 1 Anti-Island8 | Group 2a Anti-Island8 | Group 2b Anti-Island8 | Group 2c Anti-Island8 | Group 3 Anti-Island8 | Group 4 Anti-Island8 | Group 5 Anti-Island8 | Group 6 Anti-Island8 | Others8
|  | PV and Battery | 3rd Edition | SA8-SA13 | RPP3 | SA14-SA15 | SA17-SA18 | CSIP4 | Attestation7 |  | (kW) | (Vac) | (%) | Certifying Entity | Certificate Date [mo/day/yr] | Certifying Entity | Certificate Date [mo/day/yr] | Firmware Version(s) Tested | Listing Date (mo/day/yr) | Certificate Date [mo/day/yr] | Listing Date (mo/day/yr) | Issuing Entity | Document Date (mo/day/yr) | Listing Date |  |  |  | (W) | (kW) | (W) | (Vdc) | (Vdc) | (Vdc) | 10% (kW) | 20% (kW) | 30% (kW) | 50% (kW) | 75% (kW) | 100% (kW) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%) |  |  | G1AI | G2aAI | G2bAI | G2cAI | G3AI | G4AI | G5AI | G6AI | OAI
Afore New Energy Technology (Shanghai) Co., Ltd. | AF4.6K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 4.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.55 |  |  | 170 | 360 | 480 | 0.46004 | 0.92008 | 1.3801 | 2.3002 | 3.4503 | 4.6004 | 90.0323 | 93.5475 | 95.1945 | 96.1078 | 97.0873 | 97.6576 | 96.2238 | 92.0536 | 95.4444 | 96.6155 | 97.193 | 97.6015 | 97.9183 | 97.0835 | 91.3957 | 94.457 | 95.607 | 96.4039 | 97.3965 | 97.7534 | 96.6042 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF5K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 5 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.998 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.54 |  |  | 185 | 360 | 480 | 0.49977 | 0.99954 | 1.4993 | 2.4988 | 3.7483 | 4.9977 | 90.4784 | 93.2137 | 95.14 | 96.0694 | 96.9926 | 97.6424 | 96.1594 | 92.4052 | 95.3595 | 96.3498 | 97.3339 | 97.7012 | 97.8953 | 97.1427 | 92.1092 | 94.4574 | 96.025 | 96.9389 | 97.2818 | 97.7372 | 96.7336 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF6K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.995 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.55 |  |  | 220 | 360 | 480 | 0.59949 | 1.199 | 1.7985 | 2.9974 | 4.4962 | 5.9949 | 89.6111 | 93.1275 | 95.0844 | 95.9139 | 96.7975 | 97.5628 | 95.9737 | 91.5635 | 95.2459 | 96.3148 | 97.026 | 97.4503 | 97.6847 | 96.891 | 90.447 | 94.2504 | 95.2582 | 96.0739 | 97.3601 | 97.5238 | 96.4139 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF7K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 7 kW, 240 Vac Grid Support Utility Interactive Inverter | 6.996 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.55 |  |  | 170 | 360 | 480 | 0.69965 | 1.3993 | 2.0989 | 3.4982 | 5.2474 | 6.9965 | 90.3929 | 93.17 | 95.0405 | 95.8786 | 97.0631 | 97.8025 | 96.1472 | 91.7958 | 94.7364 | 95.9576 | 97.3508 | 97.62 | 98.0209 | 97.0069 | 90.9421 | 94.2244 | 95.3311 | 97.2654 | 97.577 | 97.9083 | 96.8256 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF7.6K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.599 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.55 |  |  | 185 | 360 | 480 | 0.75993 | 1.5199 | 2.2798 | 3.7996 | 5.6995 | 7.5993 | 90.5816 | 93.924 | 95.0812 | 95.9376 | 96.8505 | 97.3432 | 96.074 | 92.2385 | 94.5571 | 95.506 | 96.3515 | 97.2995 | 97.7191 | 96.5666 | 91.2608 | 94.6559 | 95.4007 | 96.3723 | 97.146 | 97.5532 | 96.4345 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF8K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 8 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.999 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.64 |  |  | 195 | 360 | 480 | 0.79986 | 1.5997 | 2.3996 | 3.9993 | 5.9989 | 7.9986 | 91.8222 | 93.64 | 95.1025 | 96.117 | 97.2117 | 97.5628 | 96.3521 | 92.4234 | 95.301 | 96.372 | 97.1563 | 97.482 | 97.9602 | 96.9929 | 91.3948 | 94.4946 | 95.4063 | 96.7014 | 97.5172 | 97.7524 | 96.7083 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF8.6K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 8.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 8.596 | 240 | 97 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.58 |  |  | 210 | 360 | 480 | 0.85956 | 1.7191 | 2.5787 | 4.2978 | 6.4467 | 8.5956 | 92.3963 | 94.4909 | 95.2393 | 96.215 | 97.3575 | 97.7814 | 96.5428 | 93.4917 | 95.4239 | 96.5341 | 97.3485 | 97.6449 | 97.9515 | 97.1875 | 93.2217 | 95.1588 | 95.5559 | 96.7104 | 97.5554 | 97.9038 | 96.8622 | 2022-12-01
Afore New Energy Technology (Shanghai) Co., Ltd. | AF9.6K-DH {240V} | Y | N | Y | Y | Y | Y | Y* | N | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.592 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/2/2022] | [1.11] | 2022-12-01 | [8/2/2022] | 2022-12-01 | Intertek | 2022-07-20 | 2022-12-01 |  | N | N | 0.65 |  |  | 235 | 360 | 480 | 0.9592 | 1.9184 | 2.8776 | 4.796 | 7.194 | 9.592 | 90.0006 | 93.7166 | 95.2164 | 96.0942 | 97.1032 | 97.8688 | 96.2497 | 91.9548 | 95.489 | 96.5298 | 97.3018 | 97.623 | 97.9692 | 97.1082 | 91.4432 | 94.7028 | 95.6808 | 96.6654 | 97.5238 | 97.776 | 96.7507 | 2022-12-01
AIMS Power Inc. | PIHY4600 {240V} | Y | N | Y | Y | Y | Y | Y* | N | 4.6 kW, 240 Vac, Grid Support Utility Interactive Inverter | 4.6004 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [11/17/2022] | [1.11] | 2023-02-13 | [11/17/2022] | 2023-02-13 | Intertek | 2022-06-20 | No Information Submitted |  | N | N | 0.55 |  |  | 170 | 360 | 480 | 0.46004 | 0.92008 | 1.3801 | 2.3002 | 3.4503 | 4.6004 | 90.0323 | 93.5475 | 95.1945 | 96.1078 | 97.0873 | 97.6576 | 96.2238 | 92.0536 | 95.4444 | 96.6155 | 97.193 | 97.6015 | 97.9183 | 97.0835 | 91.3957 | 94.457 | 95.607 | 96.4039 | 97.3965 | 97.7534 | 96.6042 | 2023-02-13
AIMS Power Inc. | PIHY9600 {240V} | Y | N | Y | Y | Y | Y | Y* | N | 9.6 kW, 240 Vac, Grid Support Utility Interactive Inverter | 9.592 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [11/17/2022] | [1.11] | 2023-02-13 | [11/17/2022] | 2023-02-13 | Intertek | 2022-06-20 | No Information Submitted |  | N | N | 0.65 |  |  | 235 | 360 | 480 | 0.9592 | 1.9184 | 2.8776 | 4.796 | 7.194 | 9.592 | 90.0006 | 93.7166 | 95.2164 | 96.0942 | 97.1032 | 97.8688 | 96.2497 | 91.9548 | 95.489 | 96.5298 | 97.3018 | 97.623 | 97.9692 | 97.1082 | 91.4432 | 94.7028 | 95.6808 | 96.6654 | 97.5238 | 97.776 | 96.7507 | 2023-02-13
Alpha ESS Co., Ltd. | SMILE-SP7.6-INV {240V} | Y | Y | N | N | N | N | Y | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.644 | 240 | 97 | CSA Group | [5/5/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-07-09 | 2024-09-23 |  | N | N | 9.44 |  |  | 230 | 400 | 480 | 0.764 | 1.529 | 2.293 | 3.822 | 5.733 | 7.644 | 94.86 | 96.15 | 96.53 | 96.68 | 96.44 | 96.2 | 96.41 | 96.22 | 97.36 | 97.65 | 97.68 | 97.53 | 97.26 | 97.5 | 95.62 | 97.01 | 97.4 | 97.59 | 97.45 | 97.2 | 97.36 | 2024-05-01 | 2024-09-23
Alpha ESS Co., Ltd. | SMILE-SPB7.6-INV {240V} | N | Y | N | N | N | N | Y | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 7.648 | 240 | 96.5 | CSA Group | [5/5/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-07-09 | 2024-09-23 |  | N | N | 9.48 |  |  | 200 | 350 | 495 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.736 | 7.648 | 94.2091 | 95.7971 | 96.2502 | 96.4508 | 96.086 | 95.8884 | 96.0829 | 95.3028 | 96.2388 | 96.7456 | 96.9702 | 96.8508 | 96.6381 | 96.7601 | 93.7819 | 95.8515 | 96.4641 | 96.8137 | 96.743 | 96.552 | 96.5518 | 2024-05-01 | 2024-09-23
Alpha ESS Co., Ltd. | SMILE-SPB9.6-INV {240V} | N | Y | N | N | N | N | Y | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 9.616 | 240 | 96.5 | CSA Group | [5/5/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-07-09 | 2024-09-23 |  | N | N | 9.5 |  |  | 200 | 350 | 450 | 0.9616 | 1.9232 | 2.8848 | 4.808 | 7.212 | 9.616 | 95.0112 | 96.1034 | 96.3344 | 96.288 | 95.8601 | 95.4093 | 95.9626 | 95.7041 | 96.6346 | 96.9842 | 96.9505 | 96.7684 | 96.4098 | 96.7653 | 95.0504 | 96.1493 | 96.569 | 96.7048 | 96.6938 | 96.4008 | 96.5735 | 2024-05-01 | 2024-09-23
Alpha ESS Co., Ltd. | SMILE-SP9.6-INV {240V} | Y | Y | N | N | N | N | Y | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 9.628 | 240 | 97 | CSA Group | [5/5/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-07-09 | 2024-09-23 |  | N | N | 9.4 |  |  | 300 | 400 | 480 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7607 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 97.378 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369 | 97.2329 | 2024-05-01 | 2024-09-23
Altenergy Power System Inc. | ELS-3K {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 3.68 kVA, 240 Vac, Grid Support Utility Interactive Bi-directional Battery Inverter | 3.685 | 240 | 94 | CSA Group | [5/6/2023] | CSA Group | [5/6/2023] | [V1.0.13] | 2023-07-11 | [5/6/2023] | 2023-07-11 | CSA Group | 2022-03-17 | 2023-07-11 |  | N | N | 4.271 |  |  | 52 | 56 | 60 | 0.3685 | 0.73701 | 1.1055 | 1.8425 | 2.7638 | 3.685 | 86.2581 | 91.8918 | 93.8271 | 94.9016 | 94.8259 | 94.1987 | 94.2012 | 85.3236 | 91.2437 | 93.442 | 94.6459 | 94.8806 | 94.4286 | 94.072 | 84.4659 | 90.7334 | 92.9722 | 94.3856 | 94.7739 | 94.5661 | 93.8514 | 2023-07-11
Altenergy Power System Inc. | ELS-5K {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 5 kVA, 240 Vac, Grid Support Utility Interactive Bi-directional Battery Inverter | 5.008 | 240 | 94 | CSA Group | [5/6/2023] | CSA Group | [5/6/2023] | [V1.0.13] | 2023-07-11 | [5/6/2023] | 2023-07-11 | CSA Group | 2022-03-17 | 2023-07-11 |  | N | N | 4.006 |  |  | 52 | 56 | 60 | 0.5008 | 1.0016 | 1.5024 | 2.504 | 3.756 | 5.008 | 88.2799 | 93.203 | 94.5115 | 94.8867 | 94.1207 | 92.8027 | 93.983 | 87.4006 | 92.5454 | 94.115 | 94.8191 | 94.3474 | 93.2334 | 93.9949 | 86.4327 | 91.9796 | 93.8105 | 94.6317 | 94.491 | 93.5582 | 93.9444 | 2023-07-11
Altenergy Power System Inc. | ELS-7.6 {208V} | N | Y | N | N | N | N | Y* | Y | ELS-7.6:7.6kVA,240 Vac Grid Support Utility Interactive Bi-directional Battery Inverter with PCS functionality. ELS-7.6:6.6kVA,208 Vac Grid Support Utility Interactive Bi-directional Battery Inverte | 6.606 | 208 | 93 | CSA Group | [7/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-28 | 2024-12-02 |  | N | N | 10.55 |  |  | 51 | 56 | 60 | 0.661 | 1.321 | 1.982 | 3.303 | 4.955 | 6.606 | 85.14 | 91.17 | 93.3 | 94.12 | 94.34 | 94.03 | 93.63 | 83.2 | 90.02 | 92.52 | 93.72 | 94.15 | 94 | 93.21 | 81.79 | 89.18 | 91.94 | 93.37 | 93.93 | 93.9 | 92.85 | 2024-12-02 | 2025-01-13
Altenergy Power System Inc. | ELS-7.6 {240V} | N | Y | N | N | N | N | Y* | Y | ELS-7.6:7.6kVA,240 Vac Grid Support Utility Interactive Bi-directional Battery Inverter with PCS functionality. ELS-7.6:6.6kVA,208 Vac Grid Support Utility Interactive Bi-directional Battery Inverte | 7.609 | 240 | 94 | CSA Group | [7/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-28 | 2024-12-02 |  | N | N | 11.06 |  |  | 51 | 56 | 60 | 0.761 | 1.522 | 2.283 | 3.804 | 5.706 | 7.609 | 86.96 | 92.21 | 93.95 | 94.63 | 94.67 | 94.24 | 94.12 | 85.19 | 91.23 | 93.28 | 94.32 | 94.59 | 94.36 | 93.82 | 83.88 | 90.5 | 92.78 | 94.05 | 94.47 | 94.35 | 93.55 | 2024-12-02 | 2025-01-13
Altenergy Power System Inc. | ELS-9.6 {208V} | N | Y | N | N | N | N | Y* | Y | ELS-9.6:9.6kVA,240 Vac Grid Support Utility Interactive Bi-directional Battery Inverter with PCS functionality. ELS-9.6:8.3kVA,208 Vac Grid Support Utility Interactive Bi-directional Battery Inverter | 8.308 | 208 | 93.5 | CSA Group | [7/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-28 | 2024-12-02 |  | N | N | 10.55 |  |  | 51 | 56 | 60 | 0.831 | 1.662 | 2.492 | 4.154 | 6.231 | 8.308 | 87.18 | 92.28 | 93.93 | 94.28 | 94.12 | 93.41 | 93.73 | 85.48 | 91.35 | 93.29 | 93.97 | 94.06 | 93.55 | 93.44 | 84.27 | 90.67 | 92.85 | 93.68 | 93.93 | 93.53 | 93.18 | 2024-12-02 | 2025-01-13
Altenergy Power System Inc. | ELS-9.6 {240V} | N | Y | N | N | N | N | Y* | Y | ELS-9.6:9.6kVA,240 Vac Grid Support Utility Interactive Bi-directional Battery Inverter with PCS functionality. ELS-9.6:8.3kVA,208 Vac Grid Support Utility Interactive Bi-directional Battery Inverter | 9.606 | 240 | 94 | CSA Group | [7/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-28 | 2024-12-02 |  | N | N | 11.04 |  |  | 51 | 56 | 60 | 0.961 | 1.921 | 2.882 | 4.803 | 7.205 | 9.606 | 89.04 | 93.38 | 94.45 | 94.73 | 94.37 | 93.53 | 94.15 | 87.56 | 92.56 | 93.96 | 94.55 | 94.43 | 93.8 | 94 | 86.43 | 91.96 | 93.54 | 94.35 | 94.39 | 93.9 | 93.82 | 2024-12-02 | 2025-01-13
Altenergy Power System Inc. | ELS-11.4 {208V} | N | Y | N | N | N | N | Y* | Y | ELS-11.4:11.4kVA,240 Vac Grid Support Utility Interactive Bi-directional Battery Inverter with PCS functionality. ELS-11.4:10kVA,208 Vac Grid Support Utility Interactive Bi-directional Battery Inverte | 10.011 | 208 | 93.5 | CSA Group | [7/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-28 | 2024-12-02 |  | N | N | 10.59 |  |  | 51 | 56 | 60 | 1.001 | 2.002 | 3.003 | 5.005 | 7.508 | 10.011 | 88.94 | 93.29 | 93.9 | 94.31 | 93.72 | 92.58 | 93.6 | 87.46 | 92.52 | 93.43 | 94.1 | 93.78 | 92.88 | 93.45 | 86.42 | 91.97 | 93.06 | 93.89 | 93.73 | 92.95 | 93.26 | 2024-12-02 | 2025-01-13
Altenergy Power System Inc. | ELS-11.4 {240V} | N | Y | N | N | N | N | Y* | Y | ELS-11.4:11.4kVA,240 Vac Grid Support Utility Interactive Bi-directional Battery Inverter with PCS functionality. ELS-11.4:10kVA,208 Vac Grid Support Utility Interactive Bi-directional Battery Inverte | 11.415 | 240 | 94 | CSA Group | [7/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-28 | 2024-12-02 |  | N | N | 11.03 |  |  | 51 | 56 | 60 | 1.141 | 2.283 | 3.424 | 5.707 | 8.561 | 11.415 | 90.61 | 94.04 | 94.55 | 94.71 | 93.93 | 92.71 | 93.98 | 89.33 | 93.4 | 94.2 | 94.64 | 94.12 | 93.12 | 93.96 | 88.39 | 92.91 | 93.89 | 94.53 | 94.22 | 93.3 | 93.9 | 2024-12-02 | 2025-01-13
Amensolar Ess Co., Ltd | N3H-X5.0-US {240V} | Y | Y | N | N | N | N | N | N | 5 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 5.09 | 240 | 97 | SGS | [2/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2023-06-12
Amensolar Ess Co., Ltd | N3H-X5US {240V} | Y | Y | N | N | N | N | N | N | 5.0 kW, 240Vac Grid Support Utility Interactive Hybrid Inverter | 5.09 | 240 | 97 | SGS | [10/12/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.509 | 1.018 | 1.527 | 2.545 | 3.817 | 5.09 | 94.57 | 95.73 | 96.2 | 96.92 | 97.19 | 96.59 | 96.81 | 95.31 | 96.27 | 96.69 | 97.41 | 97.78 | 97.08 | 97.36 | 95.11 | 95.97 | 96.72 | 97.19 | 97.64 | 96.85 | 97.21 | 2025-04-01
Amensolar Ess Co., Ltd | N3H-X6.0-US {240V} | Y | Y | N | N | N | N | N | N | 6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 6.117 | 240 | 97 | SGS | [2/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2023-06-12
Amensolar Ess Co., Ltd | N3H-X7.6-US {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 7.765 | 240 | 97 | SGS | [2/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2023-06-12
Amensolar Ess Co., Ltd | N3H-X8.0-US {240V} | Y | Y | N | N | N | N | N | N | 8 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 8.084 | 240 | 97 | SGS | [2/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.808 | 1.617 | 2.425 | 4.042 | 6.063 | 8.084 | 93.98 | 95.42 | 96.35 | 97.36 | 97.92 | 96.85 | 97.27 | 93.95 | 95.64 | 96.59 | 97.27 | 97.93 | 97.01 | 97.31 | 94.07 | 95.49 | 96.43 | 97.32 | 97.69 | 96.99 | 97.17 | 2023-06-12
Amensolar Ess Co., Ltd | N3H-X8US {240V} | Y | Y | N | N | N | N | N | N | 8.0 kW, 240Vac Grid Support Utility Interactive Hybrid Inverter | 8.084 | 240 | 97.5 | SGS | [10/12/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.808 | 1.617 | 2.425 | 4.042 | 6.063 | 8.084 | 93.98 | 95.42 | 96.35 | 97.36 | 97.92 | 96.85 | 97.27 | 93.95 | 95.64 | 96.59 | 97.27 | 97.93 | 97.01 | 97.31 | 94.07 | 95.49 | 96.43 | 97.32 | 97.69 | 96.99 | 97.17 | 2025-04-01
Amensolar Ess Co., Ltd | N3H-X10.0-US {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 10.177 | 240 | 97 | SGS | [2/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2023-06-12
Amensolar Ess Co., Ltd | N3H-X10US {240V} | Y | Y | N | N | N | N | N | N | 10.0 kW, 240Vac Grid Support Utility Interactive Hybrid Inverter | 10.177 | 240 | 97 | SGS | [10/12/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.018 | 2.035 | 3.053 | 5.088 | 7.632 | 10.177 | 94.69 | 95.94 | 96.4 | 96.8 | 97.34 | 96.75 | 96.91 | 95.39 | 96.33 | 96.85 | 97.45 | 97.97 | 97.37 | 97.51 | 94.93 | 95.96 | 96.65 | 97.01 | 97.56 | 97.03 | 97.12 | 2025-04-01
Amensolar Ess Co., Ltd | N3H-X12US {240V} | Y | Y | N | N | N | N | N | N | 12.0 kW, 240Vac Grid Support Utility Interactive Hybrid Inverter | 12.214 | 240 | 96 | SGS | [11/11/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 13.202 |  |  | 200 | 360 | 430 | 1.221 | 2.443 | 3.664 | 6.107 | 9.16 | 12.214 | 93.59 | 95.32 | 95.52 | 95.8 | 95.49 | 95.61 | 95.48 | 94.26 | 96.13 | 96.66 | 96.87 | 96.62 | 96.29 | 96.54 | 94 | 96.18 | 96.74 | 96.88 | 96.68 | 96.36 | 96.58 | 2025-04-01
Amensolar Ess Co., Ltd | N3H-X16US {240V} | Y | Y | N | N | N | N | N | N | 16.0 kW, 240Vac Grid Support Utility Interactive Hybrid Inverter | 16.199 | 240 | 96 | SGS | [11/11/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 16.199 |  |  | 220 | 360 | 430 | 1.62 | 3.24 | 4.86 | 8.099 | 12.149 | 16.199 | 93.66 | 95.36 | 95.8 | 95.93 | 95.51 | 96.18 | 95.59 | 94.19 | 96.06 | 96.55 | 96.88 | 96.64 | 96.35 | 96.53 | 94.09 | 96 | 96.54 | 96.95 | 96.69 | 96.25 | 96.57 | 2025-04-01
Anker Innovations Limited | X1-P6K-US {240V} | N | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 6.04 | 240 | 97.5 | CSA Group | [1/11/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-01-11 | 2024-03-21 |  | N | N | 7.5 |  |  | 365 | 400 | 450 | 0.604 | 1.208 | 1.812 | 3.02 | 4.53 | 6.04 | 95.75 | 97.37 | 97.66 | 97.75 | 97.71 | 97.52 | 97.61 | 95.44 | 97.19 | 97.44 | 97.63 | 97.58 | 97.48 | 97.46 | 95.14 | 96.86 | 97.3 | 97.5 | 97.42 | 97.27 | 97.29 | 2024-03-21
Anker Innovations Limited | A17E1 {240V} | Y | Y | N | N | N | N | Y* |  | 7.68 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.687 | 240 | 96 | SGS | [9/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-09-23 |  |  | N | N | 8.23 |  |  | 350 | 400 | 450 | 0.769 | 1.537 | 2.306 | 3.844 | 5.765 | 7.687 | 91.34 | 94.38 | 95.35 | 95.94 | 96.03 | 95.48 | 95.63 | 94.04 | 96.12 | 96.69 | 96.97 | 96.93 | 96.28 | 96.72 | 93.21 | 95.57 | 96.28 | 96.63 | 96.58 | 96.02 | 96.34 | 2025-12-01
Base Power, Inc | MIN 3000TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 3.095 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.095 | 240 | 97 | Intertek | [7/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 1.593 |  |  | 125 | 380 | 480 | 0.30951 | 0.61902 | 0.92853 | 1.5475 | 2.3213 | 3.0951 | 92.5494 | 94.742 | 95.5187 | 96.466 | 96.3778 | 96.1735 | 96.0481 | 94.9531 | 96.9774 | 97.284 | 97.7821 | 97.7609 | 97.4493 | 97.5411 | 93.2489 | 95.9992 | 96.7283 | 97.2156 | 97.3487 | 97.3889 | 97.0169 | 2025-09-22
Base Power, Inc | MIN 3800TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 3.888 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.888 | 240 | 97 | Intertek | [7/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 1.593 |  |  | 160 | 380 | 480 | 0.38882 | 0.77764 | 1.1665 | 1.9441 | 2.9162 | 3.8882 | 92.9226 | 95.0495 | 95.9079 | 96.5875 | 96.7318 | 96.456 | 96.3523 | 95.8681 | 97.43 | 97.8567 | 98.062 | 98.0583 | 97.9727 | 97.9116 | 93.4977 | 96.4887 | 97.1935 | 97.6687 | 97.7381 | 97.6144 | 97.4199 | 2025-09-22
Base Power, Inc | MIN 5000TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 4.943 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 4.943 | 240 | 97.5 | Intertek | [7/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 1.593 |  |  | 210 | 380 | 480 | 0.49432 | 0.98864 | 1.483 | 2.4716 | 3.7074 | 4.9432 | 94.2674 | 96.0279 | 96.6177 | 96.9688 | 96.7976 | 96.4626 | 96.6555 | 95.8274 | 97.6476 | 97.9929 | 98.1977 | 98.0262 | 97.7757 | 97.9388 | 95.1548 | 97.2155 | 97.7005 | 97.9802 | 97.817 | 97.6089 | 97.6903 | 2025-09-22
Base Power, Inc | MIN 6000TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 5.918 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 5.918 | 240 | 97 | Intertek | [7/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 1.593 |  |  | 170 | 380 | 480 | 0.59178 | 1.1836 | 1.7753 | 2.9589 | 4.4383 | 5.9177 | 93.4931 | 95.0713 | 96.0091 | 96.5068 | 96.5375 | 96.277 | 96.2595 | 96.2836 | 97.6235 | 97.995 | 98.0323 | 97.7405 | 97.6407 | 97.7632 | 95.2829 | 97.0935 | 97.4899 | 97.8279 | 97.6998 | 97.4333 | 97.5612 | 2025-09-22
Base Power, Inc | MIN 7600TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 7.524 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 7.524 | 240 | 97.5 | Intertek | [7/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 1.593 |  |  | 212 | 380 | 480 | 0.75242 | 1.5048 | 2.2573 | 3.7621 | 5.6431 | 7.5242 | 94.8321 | 96.2443 | 96.9372 | 97.1359 | 97.0549 | 96.4681 | 96.899 | 96.1031 | 97.82 | 98.0103 | 98.1875 | 98.0302 | 97.4081 | 97.9421 | 95.2191 | 97.2034 | 97.6838 | 97.8749 | 97.7927 | 97.3782 | 97.6437 | 2025-09-22
Base Power, Inc | MIN 8200TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 8.2 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 8.251 | 240 | 97.5 | Intertek | [6/25/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.82514 | 1.6503 | 2.4754 | 4.1257 | 6.1886 | 8.2514 | 93.9258 | 96.1247 | 96.8143 | 97.2666 | 97.2617 | 97.0721 | 97.0092 | 95.5722 | 97.4863 | 97.9916 | 98.2391 | 98.1842 | 98.0166 | 98.0249 | 93.7743 | 96.6734 | 97.4868 | 97.9609 | 97.966 | 97.9229 | 97.673 | 2025-09-22
Base Power, Inc | MIN 9000TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 9 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 9.063 | 240 | 97.5 | Intertek | [6/25/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.90625 | 1.8125 | 2.7188 | 4.5312 | 6.7969 | 9.0625 | 94.2384 | 96.2702 | 96.908 | 97.3235 | 97.2 | 97.0403 | 97.018 | 95.9482 | 97.6026 | 98.0707 | 98.2515 | 98.1428 | 97.9914 | 98.0346 | 94.3716 | 96.8985 | 97.6347 | 98.0229 | 98.0409 | 97.9412 | 97.7795 | 2025-09-22
Base Power, Inc | MIN 10000TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 10.082 | 240 | 97.5 | Intertek | [6/25/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.0082 | 2.0164 | 3.0246 | 5.041 | 7.5615 | 10.082 | 95.1276 | 96.4976 | 97.0675 | 97.3296 | 97.1985 | 96.9229 | 97.0787 | 96.3253 | 97.7618 | 98.1384 | 98.2919 | 98.1462 | 97.9316 | 98.0731 | 95.0134 | 97.1984 | 97.7803 | 98.0517 | 98.0092 | 97.8719 | 97.8234 | 2025-09-22
Base Power, Inc | MIN 11400TL-XH-US {240V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 11.52 | 240 | 98 | Intertek | [6/25/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.152 | 2.304 | 3.456 | 5.76 | 8.64 | 11.52 | 95.3626 | 96.9572 | 97.4775 | 97.685 | 97.5433 | 97.3539 | 97.4392 | 96.5819 | 98.0275 | 98.3999 | 98.5274 | 98.4351 | 98.2539 | 98.3467 | 95.457 | 97.1914 | 97.7448 | 97.9708 | 97.8318 | 97.6582 | 97.7149 | 2025-09-22
BYD Auto Industry Company Limited | BEG60KTL-U-R1 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 60 kVA, 480 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 60.276 | 480 | 95.5 | CSA Group | [12/16/2022] | CSA Group | [10/30/2021] | [4.0] | 2019-12-11 | [06/17/2019] | 2021-12-13 | CSA Group | 2021-10-26 | 2021-12-13 | Efficiency data inclusive of transformer effect based on 6 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216. | N | N | 98 |  |  | 750 | 850 | 950 | 6.0276 | 12.0552 | 18.0828 | 30.138 | 45.207 | 60.276 | 92.2639 | 95.0925 | 95.9421 | 96.3742 | 96.2199 | 95.9526 | 95.991 | 91.6435 | 94.6529 | 95.5526 | 96.0407 | 95.9491 | 95.6573 | 95.6691 | 91.2179 | 94.3735 | 95.3175 | 95.8259 | 95.7582 | 95.4622 | 95.4539 | 2019-12-11 | 2023-02-01
BYD Auto Industry Company Limited | BEG500KTL-U {480V} | N | N | Y | Y | Y | N | N | N | 500 kVA, 480 Vac, Grid Support Utility Interactive Battery Inverter, permanently connected, bi-directional for use with battery management system | 501.756 | 480 | 96 | No Information Submitted | No Information Submitted | CSA Group | [01/31/2019] | [V002.18] | 2019-06-17 | [01/31/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 5 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216. | N | N | 2 |  |  | 780 | 890 | 1000 | 50.1756 | 100.3512 | 150.5268 | 250.878 | 376.317 | 501.756 | 90.958 | 94.5322 | 95.7353 | 96.3971 | 96.4923 | 96.3587 | 96.0554 | 90.5506 | 94.2426 | 95.3835 | 96.1757 | 96.2707 | 96.1176 | 95.8064 | 89.9146 | 93.8477 | 95.0786 | 95.9497 | 96.0727 | 95.9028 | 95.5615 | 2019-06-17
BYD Auto Industry Company Limited | BEG500KTL-U/01 {480V} | N | N | Y | Y | Y | N | N | N | 500 kVA, 480 Vac, Grid Support Utility Interactive Battery Inverter, permanently connected, bi-directional for use with battery management system. This model does not have protective cover for cooling fans. | 501.756 | 480 | 96 | No Information Submitted | No Information Submitted | CSA Group | [01/31/2019] | [V002.18] | 2019-06-17 | [01/31/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 5 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216. | N | N | 2 |  |  | 780 | 890 | 1000 | 50.1756 | 100.3512 | 150.5268 | 250.878 | 376.317 | 501.756 | 90.958 | 94.5322 | 95.7353 | 96.3971 | 96.4923 | 96.3587 | 96.0554 | 90.5506 | 94.2426 | 95.3835 | 96.1757 | 96.2707 | 96.1176 | 95.8064 | 89.9146 | 93.8477 | 95.0786 | 95.9497 | 96.0727 | 95.9028 | 95.5615 | 2019-06-17
CE+T America Inc. | 30C {480V} | Y | N | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac Grid Support Utility Interactive Battery Charge controller | 29.99 | 480 | 95 | No Information Submitted | No Information Submitted | UL | [10/31/2018];[10/31/2018];[10/31/2018];[10/31/2018];[03/22/2019] | [3.2.42];[3.2.60];[3.2.90];[3.2.91];[3.2.106] | 2018-10-15 | [03/22/2019] | 2022-01-03 | Intertek | 2021-10-27 | 2022-01-03 | Formerly Ideal Power Inc. 30C {480V}, or CE+T Energy Solution Inc. 30C {480V}. | N | N | 56.8 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.7 | 94.3 | 94.8 | 95.2 | 95.1 | 94.8 | 94.9 | 92.2 | 94.2 | 94.6 | 95.3 | 95.4 | 95.5 | 95.1 | 89.6 | 92.8 | 93.3 | 94.8 | 95.2 | 95.4 | 94.6 | 2018-02-01 | 2022-01-03
CE+T America Inc. | 30C3 {480V} | Y | N | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac Grid Support Utility Interactive Battery Charge controller with additional Photovoltaic input | 29.99 | 480 | 95 | No Information Submitted | No Information Submitted | UL | [10/31/2018];[10/31/2018];[10/31/2018];[10/31/2018];[03/22/2019] | [3.2.42];[3.2.60];[3.2.90];[3.2.91];[3.2.106] | 2018-10-15 | [03/22/2019] | 2022-01-03 | Intertek | 2021-10-27 | 2022-01-03 | Formerly Ideal Power Inc. 30C3 {480V}, or CE+T Energy Solution Inc. 30C3 {480V}. | N | N | 56.8 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.7 | 94.3 | 94.8 | 95.2 | 95.1 | 94.8 | 94.9 | 92.2 | 94.2 | 94.6 | 95.3 | 95.4 | 95.5 | 95.1 | 89.6 | 92.8 | 93.3 | 94.8 | 95.2 | 95.4 | 94.6 | 2018-02-01 | 2022-01-03
CESC New Energy Technology Co., Ltd. | Mars 9600 HVSP {240V} | Y | N | Y | Y | Y | Y | Y* |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.592 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [6/19/2024] | [1.11] | 2025-11-03 | [6/19/2024] | 2025-11-03 | Intertek | 2024-07-08 |  |  | N | N | 0.65 |  |  | 235 | 360 | 480 | 0.9592 | 1.9184 | 2.8776 | 4.796 | 7.194 | 9.592 | 90.0006 | 93.7166 | 95.2164 | 96.0942 | 97.1032 | 97.8688 | 96.2497 | 91.9548 | 95.489 | 96.5298 | 97.3018 | 97.623 | 97.9692 | 97.1082 | 91.4432 | 94.7028 | 95.6808 | 96.6654 | 97.5238 | 97.776 | 96.7507 | 2025-10-28
Chint Power Systems America | CPS ECH7.6KTL/US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 208Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 7.57 | 208 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 50 |  |  | 200 | 370 | 480 | 0.757 | 1.514 | 2.271 | 3.785 | 5.678 | 7.57 | 94.56 | 94.85 | 96.24 | 96.53 | 96.92 | 96.17 | 96.52 | 92.85 | 95.08 | 95.82 | 96.68 | 96.91 | 96.86 | 96.48 | 93.76 | 94.98 | 96.55 | 96.49 | 96.81 | 96.51 | 96.48 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH7.6KTL/US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 7.57 | 240 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 60 |  |  | 200 | 370 | 480 | 0.757 | 1.514 | 2.271 | 3.785 | 5.678 | 7.57 | 93.67 | 94.44 | 96.1 | 96.58 | 96.58 | 96.81 | 96.31 | 93.37 | 94.93 | 95.94 | 95.94 | 96.8 | 96.8 | 96.28 | 93.76 | 94.98 | 96.55 | 96.49 | 96.81 | 96.51 | 96.48 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH9.6KTL/US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 208Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 9.54 | 240 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 50 |  |  | 200 | 370 | 480 | 0.954 | 1.908 | 2.862 | 4.77 | 7.155 | 9.54 | 93.67 | 95.3 | 96.29 | 96.41 | 96.85 | 96.66 | 96.48 | 93.34 | 95.58 | 96.24 | 96.71 | 96.82 | 96.74 | 96.52 | 92.37 | 95.32 | 96.76 | 96.57 | 96.78 | 96.43 | 96.46 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH9.6KTL/US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 9.55 | 208 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 60 |  |  | 200 | 370 | 480 | 0.955 | 1.91 | 2.865 | 4.775 | 7.163 | 9.55 | 93.14 | 95.32 | 96.26 | 96.52 | 96.97 | 96.69 | 96.54 | 93.15 | 95.37 | 96.33 | 96.71 | 96.8 | 96.81 | 96.51 | 92.61 | 95.52 | 96.23 | 96.73 | 96.82 | 96.68 | 96.49 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH11.4KTL/US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 11.35 | 208 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 80 |  |  | 200 | 370 | 480 | 1.135 | 2.27 | 3.405 | 5.675 | 8.513 | 11.35 | 93.09 | 95.58 | 96.61 | 96.68 | 96.67 | 96.62 | 96.47 | 93.52 | 95.77 | 96.55 | 96.75 | 96.78 | 96.71 | 96.56 | 92.98 | 95.7 | 96.48 | 96.74 | 96.74 | 96.62 | 96.5 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH11.4KTL/US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 11.36 | 240 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 30 |  |  | 200 | 370 | 480 | 1.136 | 2.272 | 3.408 | 5.68 | 8.52 | 11.36 | 93.84 | 95.64 | 96.4 | 96.47 | 96.77 | 96.49 | 96.48 | 93.84 | 95.83 | 96.45 | 96.76 | 96.77 | 96.64 | 96.56 | 93.44 | 95.75 | 96.44 | 96.69 | 96.67 | 96.45 | 96.46 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH12KTL/US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12 kW, 208Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 11.99 | 240 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 60 |  |  | 200 | 370 | 480 | 1.199 | 2.398 | 3.597 | 5.995 | 8.993 | 11.99 | 93.6 | 95.71 | 96.47 | 96.56 | 96.65 | 96.59 | 96.44 | 93.91 | 95.96 | 96.56 | 96.86 | 96.73 | 96.56 | 96.58 | 93.45 | 95.87 | 96.45 | 96.67 | 96.61 | 96.65 | 96.44 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECH12KTL/US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12 kW, 240Vac, Bi-directional, Transformerless, Hybrid Grid Support Utility Interactive Inverter with PCS functionality. | 12 | 208 | 96.5 | CSA Group | [1/14/2025] | CSA Group | [1/14/2025] | [V01.02.00] | 2024-07-11 | [1/14/2025] | 2024-07-11 | CSA Group | 2024-05-22 | 2024-07-11 |  | N | N | 80 |  |  | 200 | 370 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.26 | 95.84 | 96.34 | 96.57 | 96.65 | 96.51 | 96.45 | 94.27 | 95.87 | 96.58 | 96.86 | 96.86 | 96.73 | 96.67 | 93.7 | 95.9 | 96.43 | 96.75 | 96.81 | 96.61 | 96.57 | 2024-04-22 | 2025-04-21
Chint Power Systems America | CPS ECB30KTL-O/US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac, Bi-directional Grid Support Utility Interactive Battery Inverter | 30.26 | 480 | 97 | No Information Submitted | No Information Submitted | CSA Group | [01/29/2019] | [1.01.00] | 2019-05-01 | [01/29/2019] | 2020-09-01 | CSA Group | 2020-07-21 | 2020-09-01 |  | N | N | 20 |  |  | 450 | 660 | 800 | 3.026 | 6.052 | 9.078 | 15.13 | 22.695 | 30.26 | 94.6505 | 96.0141 | 96.0641 | 96.6384 | 96.7254 | 96.6107 | 96.5035 | 94.9588 | 96.6395 | 97.0651 | 97.2663 | 97.3067 | 97.205 | 97.1369 | 96.0461 | 97.4821 | 97.7088 | 98.0111 | 97.9517 | 97.7971 | 97.8276 | 2019-05-01 | 2020-09-01
Chint Power Systems America | CPS ECB62.5KTL-M/US-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 62.5 kVA, 1000 Vdc, 480 Vac, 3-phase, Bi-directional Transformerless Grid Support Utility Interactive Battery Inverter with PCS functionality. | 62.5 | 480 | 97.5 | CSA Group | [4/16/2025] | CSA Group | [4/16/2025] | [1.06.00] | 2020-11-12 | [4/16/2025] | 2020-11-12 | CSA Group | 2020-09-30 | 2020-11-12 |  | N | N | 6.1 |  |  | 750 | 925 | 1100 | 6.2552 | 12.5104 | 18.7656 | 31.276 | 46.914 | 62.552 | 97.3465 | 97.9921 | 98.095 | 98.1165 | 97.9762 | 97.7541 | 97.9844 | 95.9685 | 97.3161 | 97.572 | 97.7175 | 97.6025 | 97.3576 | 97.531 | 94.5644 | 96.473 | 97.091 | 97.2707 | 97.195 | 96.9647 | 97.0456 | 2020-11-12 | 2025-06-23
Chint Power Systems America | CPS ECB125KTL-M/US-480 {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 125 kVA, 1000 Vdc, 480 Vac, 3-phase, Bi-directional Transformerless Grid Support Utility Interactive Battery Inverter with PCS functionality. | 125 | 480 | 97.5 | CSA Group | [4/16/2025] | CSA Group | [4/16/2025] | [1.06.00] | 2020-11-12 | [4/16/2025] | 2020-11-12 | CSA Group | 2020-09-30 | 2020-11-12 |  | N | N | 5.8 |  |  | 750 | 925 | 1100 | 12.5188 | 25.0376 | 37.5564 | 62.594 | 93.891 | 125.188 | 97.3827 | 97.8322 | 98.0844 | 98.0479 | 97.8368 | 97.5419 | 97.8777 | 96.6968 | 97.3947 | 97.5562 | 97.6474 | 97.4809 | 97.1852 | 97.4745 | 95.9715 | 96.9549 | 97.0383 | 97.264 | 97.1269 | 96.8405 | 97.0759 | 2020-11-12 | 2025-06-23
Chint Power Systems America | CPS ECB200KTL/US-800 {800V} | N | Y | Y | Y | Y | Y | Y* | Y | 200 kVA, 1500 Vdc, 800 Vac, 3 Phase, Grid Support Utility Interactive Inverter | 200 | 800 | 97.5 | CSA Group | [1/10/2025] | CSA Group | [1/10/2025] | [1.05.00, 1.00, 2.00, 5.0] | 2025-03-03 | [1/10/2025] | 2025-03-03 | CSA Group | 2024-08-08 | 2025-03-03 |  | N | N | 5 |  |  | 950 | 1225 | 1500 | 20.0744 | 40.1488 | 60.2232 | 100.372 | 150.558 | 200.744 | 93.6271 | 96.1857 | 96.94 | 97.3857 | 97.3243 | 97.0986 | 97.075 | 96.0214 | 97.1629 | 97.5271 | 97.7957 | 97.7986 | 97.6286 | 97.654 | 95.6457 | 97.3929 | 97.7914 | 98.0771 | 98.0486 | 97.9214 | 97.8885 | 2022-09-12 | 2025-03-03
CSI Solar Co., Ltd. | CSEC-200K-T6901A-U {690V} | N | Y | N | N | N | N | N | N | 200 kW, 690 Vac Grid Support Utility Interactive Inverter | 200.7056 | 690 | 98.5 | CSA Group | [4/22/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 11 |  |  | 1000 | 1325 | 1500 | 20.0706 | 40.1411 | 60.2117 | 100.3528 | 150.5292 | 200.7056 | 98.7823 | 99.0522 | 99.1239 | 99.0374 | 98.9432 | 98.7456 | 98.9738 | 97.9083 | 98.5066 | 98.6801 | 98.6798 | 98.5333 | 98.3949 | 98.5484 | 97.4215 | 98.2805 | 98.4748 | 98.5422 | 98.3953 | 98.2687 | 98.3847 | 2025-06-23
CSI Solar Co., Ltd. | CSEC-215K-T6901A-U {690V} | N | Y | N | N | N | N | N | N | 215kW, 690 Vac Grid Support Utility Interactive Inverter | 215.9366 | 690 | 98.5 | CSA Group | [4/22/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 11 |  |  | 1000 | 1325 | 1500 | 21.5937 | 43.1873 | 64.781 | 107.9683 | 161.9524 | 215.9366 | 98.814 | 99.0695 | 99.1133 | 99.0081 | 98.8196 | 98.7099 | 98.9012 | 97.983 | 98.5491 | 98.694 | 98.6679 | 98.511 | 98.3687 | 98.5396 | 97.6407 | 98.3234 | 98.4761 | 98.5483 | 98.3726 | 98.2235 | 98.3827 | 2025-06-23
Darfon Electronics Corp. | HB51xxxxxx {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5000 W, 240 Vac, Grid Support Utility Interactive Battery Inverter, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer). Inverter is capable of PCS functionality. | 4.665 | 240 | 90 | No Information Submitted | No Information Submitted | Intertek | [06/16/2019] | [DSP1: PV_Inverter Ver 5.2, DSP2: Charger Ver33.8] | 2019-08-01 | [06/16/2019] | 2020-09-11 | Intertek | 2020-09-02 | 2020-09-11 |  | N | N | 0.6021 |  |  | 48 | 53 | 56.5 | 0.46648 | 0.93296 | 1.3994 | 2.3324 | 3.4986 | 4.6648 | 82.1179 | 89.1571 | 90.2158 | 90.0063 | 88.7866 | 86.8904 | 88.8712 | 82.0054 | 89.6871 | 91.1703 | 91.3826 | 90.5543 | 89.4695 | 90.3626 | 80.8864 | 89.1741 | 90.9925 | 91.4401 | 91.1444 | 90.1807 | 90.6312 | 2019-08-01 | 2020-12-21
Darfon Electronics Corp. | H5001xxxxxx {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 5000 W, 240 Vac, Hybrid PV and Battery Grid Support Utility Interactive Inverter, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer). Inverter is capable of PCS functionality. | 4.844 | 240 | 94.5 | No Information Submitted | No Information Submitted | Intertek | [07/28/2020] | [82,372] | 2020-11-02 | [07/28/2020] | 2020-11-02 | Intertek | 2020-08-12 | 2020-11-02 |  | N | N | 28.48 |  |  | 300 | 360 | 380 | 0.48442 | 0.96883 | 1.4533 | 2.4221 | 3.6331 | 4.8442 | 86.6736 | 92.8161 | 94.3502 | 95.2023 | 95.0579 | 94.4449 | 94.5252 | 87.1365 | 93.1676 | 94.6479 | 95.4859 | 95.3797 | 94.8013 | 94.845 | 87.1729 | 93.1946 | 94.6523 | 95.4841 | 95.3494 | 94.7714 | 94.8304 | 2020-11-02 | 2021-01-11
Darfon Electronics Corp. | H5000xxxxxx {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 5000 W, 240 Vac, Hybrid PV and Battery Grid support Utility Interactive Inverter with PCS functionality, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer). Inverter is capable of PCS functionality. | 5.074 | 240 | 95.5 | No Information Submitted | No Information Submitted | Intertek | [07/28/2020] | [82,372] | 2018-10-15 | [07/28/2020] | 2020-09-11 | Intertek | 2020-09-02 | 2020-09-11 |  | N | N | 0.43 |  |  | 300 | 360 | 380 | 0.508 | 1.016 | 1.524 | 2.54 | 3.81 | 5.076 | 89.2283 | 93.7363 | 94.9074 | 95.7518 | 95.8863 | 95.613 | 95.3531 | 89.4891 | 93.9486 | 95.2566 | 95.9139 | 96.0338 | 95.8858 | 95.5419 | 89.3177 | 94.0048 | 95.2025 | 95.9477 | 96.0161 | 95.9196 | 95.5308 | 2018-03-15 | 2021-01-11
Darfon Electronics Corp. | H7xxxxxx {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 9600 W, 240 Vac, Grid Support Utility Interactive Inverter, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer) | 9.604 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [8/5/2022] | [DSP1 V5.1, DSP2 V6.2] | 2022-10-01 | [8/5/2022] | 2022-10-01 | Intertek | 2022-07-26 | 2022-10-01 |  | N | N | 26.9 |  |  | 230 | 360 | 410 | 0.9604 | 1.9208 | 2.8812 | 4.802 | 7.203 | 9.604 | 91.3976 | 94.7078 | 95.7095 | 96.1271 | 96.2157 | 96.023 | 95.8586 | 92.0634 | 95.5511 | 96.3626 | 96.8436 | 96.8099 | 96.5703 | 96.4985 | 92.3296 | 95.6888 | 96.5581 | 97.0053 | 96.9658 | 96.7095 | 96.6631 | 2022-11-01
dcbel Inc. | Dcbel Ara (DBHS-ARxx-xx) {240V} | Y | Y | N | N | N | N | N |  | 7.62 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.624 | 240 | 92 | TUV SUD America | [5/7/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Home Energy Appliance including grid support solar inverter | N | N | 32.5 |  |  | 450 | 460 | 470 | 0.762 | 1.525 | 2.287 | 3.812 | 5.718 | 7.624 | 84.3 | 90.7 | 92.42 | 93.07 | 92.35 | 92.02 | 92.09 | 82.61 | 90.67 | 92.41 | 93.11 | 92.35 | 92.04 | 92.03 | 84.62 | 90.66 | 92.4 | 93.08 | 92.34 | 92.07 | 92.1 | 2026-04-01
Delta Electronics | E4_BDI {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3328 W, 208 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 3.3413 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.24 |  |  | 280 | 380 | 480 | 0.33413 | 0.66827 | 1.0024 | 1.6707 | 2.506 | 3.3413 | 92.6852 | 95.2806 | 96.3508 | 97.0447 | 97.0686 | 97.336 | 96.7261 | 92.1027 | 95.4066 | 96.5531 | 97.315 | 97.5791 | 97.6175 | 97.0747 | 89.0319 | 94.0125 | 95.5747 | 96.8148 | 97.2577 | 97.3776 | 96.4774 | 2022-06-01 | 2024-04-02
Delta Electronics | E4-TL-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3328 W, 208 Vac, transformerless, Bi-directional, Multi-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 3.36 | 208 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2020-08-11 | [6/2/2022] | 2020-08-11 | CSA Group | 2022-11-25 | 2020-08-11 |  | Y | N | 1.21 |  |  | 200 | 380 | 480 | 0.33599 | 0.67197 | 1.008 | 1.6799 | 2.5199 | 3.3599 | 92.7058 | 95.316 | 96.0794 | 96.9375 | 97.261 | 97.2579 | 96.7716 | 94.6716 | 96.7433 | 97.431 | 97.8832 | 97.9342 | 97.8306 | 97.6679 | 93.5334 | 96.0786 | 96.9192 | 97.5645 | 97.7603 | 97.6747 | 97.3608 | 2020-08-11 | 2024-04-02
Delta Electronics | E4-TL-US(AC) {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 3328 W, 208 Vac Transformerless Grid Support Utility Interactive Energy Storagy Inverter with PCS functionality. | 3.364 | 208 | 98 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2020-08-11 | [6/2/2022] | 2020-08-11 | CSA Group | 2022-11-25 | 2020-08-11 |  | Y | N | 1.23 |  |  | 350 | 400 | 480 | 0.33644 | 0.67288 | 1.0093 | 1.6822 | 2.5233 | 3.3644 | 95.4286 | 97.272 | 97.8821 | 98.254 | 98.3148 | 98.1972 | 98.0767 | 94.8143 | 96.9329 | 97.6159 | 98.0971 | 98.1976 | 98.1162 | 97.9041 | 93.9184 | 96.3871 | 97.1728 | 97.7982 | 97.993 | 97.934 | 97.6075 | 2020-08-11 | 2024-04-02
Delta Electronics | E4-TL-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3840 W, 240 Vac, transformerless, Bi-directional, Multi-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 3.87 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2020-08-11 | [6/2/2022] | 2020-08-11 | CSA Group | 2022-11-25 | 2020-08-11 |  | Y | N | 1.27 |  |  | 200 | 380 | 400 | 0.38696 | 0.77392 | 1.1609 | 1.9348 | 2.9022 | 3.8696 | 92.8573 | 95.3032 | 96.0816 | 97.008 | 97.3433 | 97.3609 | 96.8409 | 95.3025 | 97.1049 | 97.7261 | 98.0933 | 98.1429 | 98.1114 | 97.9154 | 94.285 | 96.4536 | 97.2773 | 97.8608 | 98.0038 | 97.9448 | 97.6574 | 2020-08-11 | 2024-04-02
Delta Electronics | E4-TL-US(AC) {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 3840 W, 240 Vac Transformerless Grid Support Utility Interactive Energy Storage Inverter with PCS functionality. | 3.888 | 240 | 98.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2020-08-11 | [6/2/2022] | 2020-08-11 | CSA Group | 2022-11-25 | 2020-08-11 |  | Y | N | 1.28 |  |  | 350 | 400 | 480 | 0.38876 | 0.77751 | 1.1663 | 1.9438 | 2.9157 | 3.8876 | 95.9481 | 97.6144 | 98.153 | 98.4067 | 98.6146 | 98.3924 | 98.3478 | 95.4757 | 97.3498 | 97.9766 | 98.3716 | 98.712 | 98.5177 | 98.345 | 94.657 | 96.7993 | 97.543 | 98.1036 | 98.616 | 98.4252 | 98.1209 | 2020-08-11 | 2024-04-02
Delta Electronics | E4_BDI {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3480 W, 240 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 3.8982 | 240 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.3 |  |  | 280 | 380 | 480 | 0.38982 | 0.77964 | 1.1695 | 1.9491 | 2.9236 | 3.8982 | 92.7724 | 95.442 | 96.4856 | 97.125 | 97.3647 | 97.4288 | 96.9323 | 93.2521 | 96.152 | 97.0569 | 97.6876 | 97.8589 | 97.9251 | 97.4604 | 90.5052 | 94.6892 | 96.1085 | 97.2209 | 97.5572 | 97.6718 | 96.893 | 2022-06-01 | 2024-04-02
Delta Electronics | E6-TL-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4992 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 4.992 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.86 |  |  | 200 | 380 | 480 | 0.4992 | 0.9984 | 1.4976 | 2.496 | 3.744 | 4.992 | 94.0016 | 95.6485 | 96.4705 | 97.0318 | 96.9884 | 96.6789 | 96.7334 | 95.696 | 97.2204 | 97.6522 | 97.8362 | 97.6671 | 97.3491 | 97.5837 | 94.6317 | 96.517 | 97.1735 | 97.5416 | 97.4711 | 97.1739 | 97.274 | 2018-08-01 | 2024-04-02
Delta Electronics | E6-TL-US(AC) {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 5000 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter with PCS functionality. | 5 | 208 | 98 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.85 |  |  | 350 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.3576 | 97.7104 | 98.1201 | 98.2082 | 98.0337 | 97.6876 | 97.9802 | 95.6974 | 97.377 | 97.8682 | 98.0571 | 97.92 | 97.611 | 97.8111 | 94.7983 | 96.7769 | 97.4536 | 97.765 | 97.7211 | 97.431 | 97.5196 | 2018-08-01 | 2024-04-02
Delta Electronics | E6-TL-US(AC) {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 5000 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter with PCS functionality. | 5 | 240 | 98 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 2.05 |  |  | 350 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.4809 | 97.5846 | 98.1167 | 98.4736 | 98.3238 | 97.9351 | 98.2003 | 95.8938 | 97.5508 | 98.0084 | 98.4507 | 98.3503 | 98.1238 | 98.1808 | 94.8718 | 96.9341 | 97.5858 | 98.1949 | 98.1673 | 97.9672 | 97.8998 | 2018-08-01 | 2024-04-02
Delta Electronics | E6_BDI {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4992 W, 208 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 5.025 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 3.07 |  |  | 280 | 380 | 480 | 0.50521 | 1.0104 | 1.5156 | 2.5261 | 3.7891 | 5.0521 | 94.108 | 96.4743 | 96.8432 | 97.2485 | 97.2693 | 96.4695 | 97.0076 | 94.1138 | 96.5094 | 97.1953 | 97.5538 | 97.5799 | 97.5277 | 97.3335 | 92.1224 | 95.6496 | 96.6604 | 97.2666 | 97.3945 | 97.3385 | 96.9786 | 2022-06-01 | 2024-04-02
Delta Electronics | E6-TL-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5760 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 5.76 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 2.25 |  |  | 200 | 380 | 480 | 0.576 | 1.152 | 1.728 | 2.88 | 4.32 | 5.76 | 93.9636 | 95.7324 | 96.5328 | 97.1183 | 97.0624 | 96.7746 | 96.8057 | 96.2574 | 97.615 | 97.9819 | 98.0814 | 97.6804 | 97.6267 | 97.738 | 95.2386 | 96.9825 | 97.5357 | 97.8342 | 97.7548 | 97.4585 | 97.5911 | 2018-08-01 | 2024-04-02
Delta Electronics | E6_BDI {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5760 W, 240 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 5.823 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 3.56 |  |  | 280 | 380 | 480 | 0.58227 | 1.1645 | 1.7468 | 2.9113 | 4.367 | 5.8227 | 94.3806 | 96.5167 | 97.113 | 97.2899 | 97.4038 | 97.3849 | 97.1788 | 95.1918 | 96.9824 | 97.6172 | 97.8772 | 97.8794 | 97.8499 | 97.6936 | 93.3812 | 96.121 | 97.0916 | 97.579 | 97.6894 | 97.6744 | 97.3429 | 2022-06-01 | 2024-04-02
Delta Electronics | E8-TL-US(AC) {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 6500 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter with PCS functionality. | 6.494 | 240 | 98 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 2.1 |  |  | 350 | 400 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 96.564 | 97.9534 | 98.1731 | 98.3825 | 98.2962 | 98.0856 | 98.2026 | 95.9941 | 97.6828 | 98.1182 | 98.3712 | 98.3594 | 98.0923 | 98.1911 | 95.036 | 97.1456 | 97.7444 | 98.1155 | 98.1782 | 97.9141 | 97.9224 | 2018-08-01 | 2024-04-02
Delta Electronics | E8-TL-US(AC) {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 6500 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter with PCS functionality. | 6.5 | 208 | 98 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.91 |  |  | 350 | 400 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 96.5268 | 97.8051 | 98.1607 | 98.2713 | 98.071 | 97.7448 | 98.0324 | 95.9938 | 97.5402 | 97.9409 | 98.1437 | 97.9732 | 97.6535 | 97.8883 | 95.0772 | 96.9768 | 97.5715 | 97.8841 | 97.7702 | 97.4644 | 97.6076 | 2018-08-01 | 2024-04-02
Delta Electronics | E8-TL-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6656 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 6.656 | 208 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.15 |  |  | 270 | 380 | 480 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 95.2308 | 96.891 | 97.3835 | 97.6343 | 97.4276 | 97.0506 | 97.3322 | 95.9476 | 97.4104 | 97.7946 | 97.9487 | 97.6997 | 97.3918 | 97.6634 | 94.855 | 96.7763 | 97.3739 | 97.6604 | 97.5174 | 97.1621 | 97.3689 | 2018-08-01 | 2024-04-02
Delta Electronics | E8 Plus-TL-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6656 W, 208 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 6.6768 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2023-02-01 | [6/2/2022] | 2023-02-01 | CSA Group | 2022-11-25 | 2023-02-01 |  | N | N | 3.22 |  |  | 280 | 380 | 480 | 0.66768 | 1.3354 | 2.003 | 3.3384 | 5.0076 | 6.6768 | 94.1111 | 96.1543 | 96.4098 | 96.628 | 96.563 | 96.3234 | 96.4278 | 95.4902 | 97.0363 | 97.4287 | 97.5565 | 97.4235 | 97.3169 | 97.35 | 94.0635 | 96.4144 | 97.0161 | 97.3508 | 97.3059 | 97.1682 | 97.0994 | 2023-02-01 | 2024-04-02
Delta Electronics | E8_BDI {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6656 W, 208 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 6.677 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 3.22 |  |  | 280 | 380 | 480 | 0.66768 | 1.3354 | 2.003 | 3.3384 | 5.0076 | 6.6768 | 94.1111 | 96.1543 | 96.4098 | 96.628 | 96.563 | 96.3234 | 96.4278 | 95.4902 | 97.0363 | 97.4287 | 97.5565 | 97.4235 | 97.3169 | 97.35 | 94.0635 | 96.4144 | 97.0161 | 97.3508 | 97.3059 | 97.1682 | 97.0994 | 2022-06-01 | 2024-04-02
Delta Electronics | E8 Plus-TL-US(AC) {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 6656 W, 208 Vac Transformerless Grid Support Utility Interactive Energy Storage Inverter with PCS functionality. | 6.685 | 208 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2023-02-01 | [6/2/2022] | 2023-02-01 | CSA Group | 2022-11-25 | 2023-02-01 |  | N | N | 3.34 |  |  | 350 | 400 | 480 | 0.6685 | 1.337 | 2.0055 | 3.3425 | 5.0137 | 6.685 | 96.1833 | 97.5759 | 97.9061 | 98.0415 | 97.9585 | 97.7769 | 97.8704 | 95.4242 | 97.2205 | 97.6765 | 97.8879 | 97.835 | 97.6734 | 97.6918 | 94.0718 | 96.6287 | 97.2804 | 97.6297 | 97.6325 | 97.5042 | 97.3906 | 2023-02-01 | 2024-04-02
Delta Electronics | E8-TL-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 7.68 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2018-10-15 | [6/2/2022] | 2020-03-11 | CSA Group | 2022-11-25 | 2020-03-11 |  | Y | N | 1.19 |  |  | 270 | 380 | 480 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.2202 | 96.7865 | 97.3605 | 97.6615 | 97.5147 | 97.0633 | 97.3763 | 96.5571 | 97.7682 | 98.0917 | 98.1644 | 97.9971 | 97.6404 | 97.9567 | 95.5533 | 97.2136 | 97.7339 | 97.9476 | 97.8481 | 97.5018 | 97.7144 | 2018-08-01 | 2024-04-02
Delta Electronics | E8 Plus-TL-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7680 W, 240 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 7.716 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2023-02-01 | [6/2/2022] | 2023-02-01 | CSA Group | 2022-11-25 | 2023-02-01 |  | N | N | 2.72 |  |  | 280 | 380 | 480 | 0.7716 | 1.5432 | 2.3148 | 3.858 | 5.787 | 7.716 | 94.8576 | 96.6091 | 96.812 | 97.0141 | 96.9294 | 96.6893 | 96.8222 | 96.1358 | 97.4848 | 97.7923 | 97.8646 | 97.7763 | 97.6446 | 97.71 | 92.947 | 96.8614 | 97.4026 | 97.6609 | 97.6155 | 97.5054 | 97.3695 | 2023-02-01 | 2024-04-02
Delta Electronics | E8_BDI {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7680 W, 240 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 7.716 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 2.72 |  |  | 280 | 380 | 480 | 0.7716 | 1.5432 | 2.3148 | 3.858 | 5.787 | 7.716 | 94.8576 | 96.6091 | 96.812 | 97.0141 | 96.9294 | 96.6893 | 96.8222 | 96.1358 | 97.4848 | 97.7923 | 97.8646 | 97.7763 | 97.6446 | 97.71 | 92.947 | 96.8614 | 97.4026 | 97.6609 | 97.6155 | 97.5054 | 97.3695 | 2022-06-01 | 2024-04-02
Delta Electronics | E8 Plus-TL-US(AC) {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7680 W, 240 Vac Transformerless Grid Support Utility Interactive Energy Storage Inverter with PCS functionality. | 7.72 | 240 | 98 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2023-02-01 | [6/2/2022] | 2023-02-01 | CSA Group | 2022-11-25 | 2023-02-01 |  | N | N | 3.21 |  |  | 350 | 400 | 480 | 0.772 | 1.544 | 2.316 | 3.86 | 5.79 | 7.72 | 96.9307 | 97.9653 | 98.2277 | 98.3389 | 98.2408 | 98.094 | 98.1863 | 96.2137 | 97.6928 | 98.0262 | 98.2055 | 98.138 | 97.9695 | 98.0311 | 94.8714 | 97.0622 | 97.6391 | 97.9508 | 97.9477 | 97.784 | 97.7358 | 2023-02-01 | 2024-04-02
Delta Electronics | E10-TL-US(AC) {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 8320 W, 208 Vac, transformerless Grid Support Utility Interactive Energy Storage Inverter with PCS functionality. | 8.3272 | 208 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 2 |  |  | 350 | 400 | 480 | 0.83272 | 1.6654 | 2.4982 | 4.1636 | 6.2454 | 8.3272 | 96.6951 | 97.7427 | 97.9764 | 97.9793 | 97.8189 | 97.5501 | 97.8093 | 96.1537 | 97.486 | 97.8027 | 97.8492 | 97.6998 | 97.4636 | 97.6592 | 95.1567 | 96.9945 | 97.4585 | 97.629 | 97.5107 | 97.2973 | 97.3987 | 2022-06-01 | 2024-04-02
Delta Electronics | E10_BDI {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8320 W, 208 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 8.4 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.35 |  |  | 280 | 380 | 480 | 0.83996 | 1.6799 | 2.5199 | 4.1998 | 6.2997 | 8.3996 | 95.9763 | 97.0349 | 97.2944 | 97.3825 | 97.18 | 96.8443 | 97.164 | 96.7105 | 97.4869 | 97.6286 | 97.5273 | 97.1983 | 96.819 | 97.295 | 95.5251 | 96.9805 | 97.3434 | 97.441 | 97.2115 | 96.9273 | 97.1823 | 2022-06-01 | 2024-04-02
Delta Electronics | E10-TL-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8320 W, 208 Vac, transformerless Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 8.4 | 208 | 97 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.35 |  |  | 280 | 380 | 480 | 0.83996 | 1.6799 | 2.5199 | 4.1998 | 6.2997 | 8.3996 | 95.9763 | 97.0349 | 97.2944 | 97.3825 | 97.18 | 96.8443 | 97.164 | 96.7105 | 97.4869 | 97.6286 | 97.5273 | 97.1983 | 96.819 | 97.295 | 95.5251 | 96.9805 | 97.3434 | 97.441 | 97.2115 | 96.9273 | 97.1823 | 2022-06-01 | 2024-04-02
Delta Electronics | E10-TL-US(AC) {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 9600 W, 240 Vac, transformerless Grid Support Utility Interactive Energy Storage Inverter with PCS functionality. | 9.6318 | 240 | 98 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 3.14 |  |  | 350 | 400 | 480 | 0.96318 | 1.9264 | 2.8895 | 4.8159 | 7.2239 | 9.6318 | 97.2351 | 98.1257 | 98.2956 | 98.2753 | 98.1128 | 97.8731 | 98.1224 | 96.7547 | 97.8874 | 98.2576 | 98.1631 | 98.0356 | 97.7952 | 98.0183 | 95.7886 | 97.3995 | 97.8157 | 97.9673 | 97.8809 | 97.6389 | 97.7714 | 2022-06-01 | 2024-04-02
Delta Electronics | E10_BDI {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9600 W, 240 Vac, transformerless Grid Support Utility Interactive Hybrid Inverter capable of receiving input from EVSE Box with PCS functionality. | 9.674 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.38 |  |  | 280 | 380 | 480 | 0.96742 | 1.9348 | 2.9023 | 4.8371 | 7.2557 | 9.6742 | 96.0741 | 97.0988 | 97.3615 | 97.4925 | 97.321 | 96.9976 | 97.2847 | 97.044 | 97.7732 | 97.9269 | 97.8348 | 97.6061 | 97.3666 | 97.6665 | 96.1551 | 97.378 | 97.6757 | 97.7252 | 97.497 | 97.2601 | 97.4949 | 2022-06-01 | 2024-04-02
Delta Electronics | E10-TL-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9600 W, 240 Vac, transformerless Grid Support Utility Interactive Solar and Energy Storage Inverter with PCS functionality. | 9.674 | 240 | 97.5 | CSA Group | [9/15/2023] | CSA Group | [6/2/2022] | [1.6.2] | 2022-06-01 | [6/2/2022] | 2022-06-01 | CSA Group | 2022-11-25 | 2022-06-01 |  | Y | N | 1.38 |  |  | 280 | 380 | 480 | 0.96742 | 1.9348 | 2.9023 | 4.8371 | 7.2557 | 9.6742 | 96.0741 | 97.0988 | 97.3615 | 97.4925 | 97.321 | 96.9976 | 97.2847 | 97.044 | 97.7732 | 97.9269 | 97.8348 | 97.6061 | 97.3666 | 97.6665 | 96.1551 | 97.378 | 97.6757 | 97.7252 | 97.497 | 97.2601 | 97.4949 | 2022-06-01 | 2024-04-02
Delta Electronics | S12_BDI {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.984 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 10.0568 | 208 | 97 | CSA Group | [5/6/2024] | CSA Group | [5/6/2024] | [01.00.17] | 2024-08-12 | [5/6/2024] | 2024-08-12 | CSA Group | 2023-11-01 | 2024-06-11 |  | N | N | 16.23 |  |  | 200 | 380 | 480 | 1.0057 | 2.0114 | 3.017 | 5.0284 | 7.5426 | 10.0568 | 94.5201 | 96.389 | 96.8997 | 96.9415 | 96.5333 | 95.9709 | 96.5472 | 95.9899 | 97.4283 | 97.7143 | 97.6655 | 97.2997 | 96.965 | 97.3636 | 95.4895 | 97.1344 | 97.5396 | 97.6477 | 97.4208 | 96.8726 | 97.3637 | 2024-06-11 | 2024-08-12
Delta Electronics | S12_BDI {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.520 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.5886 | 240 | 97.5 | CSA Group | [5/6/2024] | CSA Group | [5/6/2024] | [01.00.17] | 2024-08-12 | [5/6/2024] | 2024-08-12 | CSA Group | 2023-11-01 | 2024-06-11 |  | N | N | 16.48 |  |  | 200 | 380 | 480 | 1.1589 | 2.3177 | 3.4766 | 5.7943 | 8.6914 | 11.5886 | 94.7826 | 96.6129 | 97.0546 | 97.1271 | 96.6484 | 96.0211 | 96.6899 | 96.5172 | 97.7857 | 97.9547 | 97.9185 | 97.5962 | 97.3165 | 97.6593 | 96.0248 | 97.4984 | 97.8115 | 97.8312 | 97.6456 | 97.2776 | 97.6139 | 2024-06-11 | 2024-08-12
Delta Electronics | E30-TL {277V} | Y | N | Y | Y | Y | N | N | N | 30 kW, 277 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 30.488 | 277 | 98 | No Information Submitted | No Information Submitted | CSA Group | [07/01/2019] | [Controller A: V1.1.3, Controller B: V1.1.1] | 2019-08-01 | [07/01/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1.59 |  |  | 515 | 750 | 830 | 3.0488 | 6.0975 | 9.1463 | 15.2438 | 22.8657 | 30.4876 | 95.9222 | 97.1353 | 97.5449 | 97.7515 | 97.701 | 97.4796 | 97.5823 | 97.4461 | 98.3209 | 98.5555 | 98.6266 | 98.581 | 98.4647 | 98.5233 | 96.9725 | 98.1055 | 98.382 | 98.4809 | 98.4516 | 98.3166 | 98.3662 | 2019-08-01
Delta Electronics | PCS125HV {480V} | N | Y | N | N | N | N | Y* | Y | 125 kW, 480 Vac, Bi-directional, Transformerless Grid support Utility Interactive Inverter with PCS functionality. | 124.312 | 480 | 98 | CSA Group | [11/14/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-10-27 | 2023-01-23 |  | N | N | 19 |  |  | 815 | 950 | 1250 | 12.4312 | 24.8623 | 37.2935 | 62.1558 | 93.2337 | 124.3116 | 97.1554 | 97.93 | 98.143 | 98.1667 | 98.0012 | 97.776 | 98.0043 | 96.6424 | 97.6625 | 97.9417 | 98.0068 | 97.8706 | 97.6448 | 97.8369 | 95.1613 | 97.0788 | 97.492 | 97.7004 | 97.5873 | 97.3834 | 97.467 | 2022-11-01 | 2024-02-12
Delta Electronics | DES10JB125K01 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 125 kW, 480 Vac, 3-phase bi-directional Grid Support Utility Interactive Inverter | 125 | 480 | 97 | No Information Submitted | No Information Submitted | CSA Group | [3/24/2020] | [1.1.8.4] | 2018-10-15 | [3/24/2020] | 2020-05-11 | CSA Group | 2020-03-05 | 2020-05-11 |  | N | N | 22.4 |  |  | 750 | 900 | 1000 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 95.731 | 97.1982 | 97.5482 | 97.6472 | 97.4412 | 97.2142 | 97.4054 | 93.8046 | 96.324 | 96.9331 | 97.278 | 97.2686 | 97.1169 | 97.037 | 92.3112 | 95.6622 | 96.4776 | 96.9704 | 97.0348 | 96.8004 | 96.6851 | 2017-11-01 | 2020-05-11
Delta Electronics | PCS125 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 125 kW, 480 Vac, 3-phase bi-directional Grid Support Utility Interactive Inverter | 125 | 480 | 97 | No Information Submitted | No Information Submitted | CSA Group | [3/24/2020] | [1.1.8.4] | 2018-10-15 | [3/24/2020] | 2020-05-11 | CSA Group | 2020-03-05 | 2020-05-11 |  | N | N | 22.4 |  |  | 750 | 900 | 1000 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 95.731 | 97.1982 | 97.5482 | 97.6472 | 97.4412 | 97.2142 | 97.4054 | 93.8046 | 96.324 | 96.9331 | 97.278 | 97.2686 | 97.1169 | 97.037 | 92.3112 | 95.6622 | 96.4776 | 96.9704 | 97.0348 | 96.8004 | 96.6851 | 2020-05-11
Delta Electronics | PCS125HVM {480V} | N | Y | N | N | N | N | N |  | 125 kW, 480 Vac Transformerless Grid Support Utility Interactive Inverter | 125.18 | 480 | 98 | TUV Rheinland of North America | [4/30/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 397.4 |  |  | 750 | 1000 | 1250 | 12.518 | 25.036 | 37.554 | 62.59 | 93.885 | 125.18 | 97.04 | 98.04 | 98.22 | 98.23 | 98.07 | 97.85 | 98.07 | 96.25 | 97.66 | 97.92 | 98.01 | 97.86 | 97.62 | 97.81 | 95.02 | 97.16 | 97.57 | 97.76 | 97.64 | 97.39 | 97.51 | 2026-08-03 |  | Y | N | N | N | N | N | N | N | N
Delta Electronics | EPCS-1200US {480V} | N | Y | N | N | N | N | N | N | 1200 kW, 480 Vac, 3-phase bi-directional Grid Support Utility Interactive Inverter with PCS functionality. | 1216.71 | 480 | 98 | CSA Group | [9/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 47.294 |  |  | 720 | 1000 | 1500 | 121.671 | 243.342 | 365.0131 | 608.3551 | 912.5326 | 1216.7102 | 97.3959 | 98.2647 | 98.4374 | 98.4374 | 98.2757 | 98.0804 | 98.2835 | 96.5254 | 97.6991 | 97.9564 | 98.1 | 97.9586 | 97.7928 | 97.9094 | 94.6822 | 96.6784 | 97.2233 | 97.5717 | 97.5783 | 97.4323 | 97.3662 | 2024-01-02
Delta Electronics | EPCS-1500US {600V} | N | Y | N | N | N | N | N | N | 1500 kW, 600 Vac, 3-phase bi-directional Grid Support Utility Interactive Inverter with PCS functionality. | 1509.889 | 600 | 98 | CSA Group | [9/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 46.128 |  |  | 893 | 1300 | 1500 | 150.9889 | 301.9778 | 452.9666 | 754.9444 | 1132.4166 | 1509.8888 | 97.2746 | 98.1625 | 98.3309 | 98.442 | 98.3132 | 98.184 | 98.2869 | 96.5684 | 97.7523 | 98.0557 | 98.2035 | 98.154 | 98.0385 | 98.0633 | 96.2355 | 97.5455 | 97.8922 | 98.072 | 98.0513 | 97.9394 | 97.933 | 2024-01-02
Delta Electronics | EPCS-1725US {690V} | N | Y | N | N | N | N | N | N | 1725 kW, 690 Vac, 3-phase bi-directional Grid Support Utility Interactive Inverter with PCS functionality. | 1725.451 | 690 | 98.5 | CSA Group | [9/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 45.762 |  |  | 1030 | 1300 | 1500 | 172.5451 | 345.0903 | 517.6354 | 862.7257 | 1294.0885 | 1725.4514 | 97.236 | 98.1757 | 98.4348 | 98.5561 | 98.4504 | 98.3326 | 98.4025 | 96.7316 | 97.9259 | 98.2596 | 98.4347 | 98.3642 | 98.2617 | 98.2741 | 96.452 | 97.7883 | 98.141 | 98.329 | 98.2941 | 98.1838 | 98.1786 | 2024-01-02
Delta Electronics | DWE2100-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 2100 kW, 480 Vac Bi-directional, Multi-Mode Grid Support Utility Interactive Battery Inverter | 1887.74 | 480 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [04/13/2020] | [V01.02] | 2021-01-21 | [04/13/2020] | 2021-03-01 | CSA Group | 2021-01-22 | 2021-03-01 | Efficiency data inclusive of transformer effect based on a 2100 kVA medium voltage transformer where suitability is to be determined in the end application. | N | N | 18.253 |  |  | 760 | 900 | 1200 | 188.774 | 377.548 | 566.322 | 943.87 | 1415.805 | 1887.74 | 93.78 | 96.05 | 96.72 | 97.12 | 97.15 | 96.97 | 96.9 | 92.72 | 95.43 | 96.24 | 96.74 | 96.83 | 96.68 | 96.5 | 90.39 | 94.23 | 95.23 | 95.96 | 96.14 | 96.03 | 95.66 | 2021-01-21 | 2021-03-01
Delta Electronics | PCSC1935 {480V} | N | Y | N | N | N | N | Y* |  | 1938 kW, 480 Vac Bi-directional, Transformerless Grid support Utility Interactive Battery Inverter | 1938.126 | 480 | 98 | CSA Group | [4/18/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-04-13 |  |  | N | N | 477 |  |  | 723 | 900 | 1500 | 193.813 | 387.625 | 581.438 | 969.063 | 1453.595 | 1938.126 | 98.04 | 98.53 | 98.62 | 98.55 | 98.27 | 98.12 | 98.37 | 97.67 | 98.34 | 98.53 | 98.44 | 98.24 | 98.11 | 98.29 | 95.89 | 97.42 | 97.9 | 98.05 | 97.99 | 97.71 | 97.86 | 2026-07-01 |  | Y | N | N | N | N | N | N | N | N
Delta Electronics | PCS2328S-XXX-US {600V} | N | Y | N | N | N | N | N | N | 2328 kW, 600 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, where the first x can be "S" or Blank and second and third XX can be "00" or "01" | 2327.94 | 600 | 98 | CSA Group | [8/23/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 695.7 |  |  | 920 | 1300 | 1500 | 232.794 | 465.588 | 698.382 | 1163.97 | 1745.955 | 2327.94 | 96.41 | 98.54 | 98.66 | 98.71 | 98.49 | 98.23 | 98.46 | 96.02 | 97.95 | 97.95 | 98.34 | 98.21 | 98.01 | 98.1 | 95.25 | 97.6 | 97.57 | 98.1 | 97.6 | 97.87 | 97.62 | 2024-03-01
Delta Electronics | DWE2800-US {480V} | N | N | Y | Y | Y | Y | Y* | Y | 2800 kW, 480 Vac Bi-directional, Multi-Mode Grid Support Utility Interactive Battery Inverter | 2513.388 | 480 | 96 | No Information Submitted | No Information Submitted | CSA Group | [04/13/2020] | [V01.02] | 2020-11-02 | [04/13/2020] | 2021-03-01 | CSA Group | 2021-01-22 | 2021-03-01 | Efficiency data inclusive of transformer effect based on a 2800 kVA medium voltage transformer where suitability is to be determined in the end application. | N | N | 1114 |  |  | 760 | 900 | 1200 | 251.3388 | 502.6776 | 754.0164 | 1256.694 | 1885.041 | 2513.388 | 93.9278 | 95.5206 | 96.4052 | 96.8951 | 96.9203 | 96.67 | 96.651 | 92.904 | 94.7314 | 95.8013 | 96.4366 | 96.5493 | 96.3786 | 96.1906 | 90.6966 | 93.4081 | 94.7591 | 95.6698 | 95.8648 | 95.7398 | 95.3554 | 2020-11-02 | 2021-03-01
Delta Electronics | PCS2580X-X00-US {690V} | N | Y | N | N | N | N | N | N | 2580 kW, 690 Vac, Bi-directional, Transformerless Grid support Utility Interactive Battery Inverter, where the first X can be replaced by the letter "S" or "C", and the second X will be replaced by letter "S" | 2582.5 | 690 | 98.5 | CSA Group | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 336 |  |  | 1040 | 1300 | 1500 | 258.25 | 516.5 | 774.75 | 1291.25 | 1936.875 | 2582.5 | 97.9175 | 98.6042 | 98.7888 | 98.8448 | 98.6586 | 98.4374 | 98.6699 | 97.309 | 98.2475 | 98.5353 | 98.6614 | 98.5302 | 98.3281 | 98.4853 | 96.6274 | 97.976 | 98.3155 | 98.5449 | 98.4362 | 98.2438 | 98.3396 | 2025-08-11
Delta Electronics | PCSC2782 {690V} | N | Y | N | N | N | N | Y* |  | 2813 kW, 690 Vac Bi-directional, Transformerless Grid support Utility Interactive Battery Inverter | 2813.66 | 690 | 98.5 | CSA Group | [4/18/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-04-13 |  |  | N | N | 477 |  |  | 1040 | 1300 | 1500 | 281.366 | 562.732 | 844.098 | 1406.83 | 2110.245 | 2813.66 | 97.4323 | 98.3889 | 98.6463 | 98.7771 | 98.7256 | 98.6117 | 98.6527 | 96.8879 | 98.1099 | 98.448 | 98.6465 | 98.6209 | 98.5145 | 98.5053 | 96.5669 | 97.94 | 98.3159 | 98.5496 | 98.5431 | 98.4455 | 98.4031 | 2026-04-01 | 2026-07-01 | Y | N | N | N | N | N | N | N | N
Delta Electronics | PCSC2834 {550V} | N | Y | N | N | N | N | Y* |  | 2842 kW, 550 Vac Bi-directional, Transformerless Grid support Utility Interactive Battery Inverter | 2842.48 | 550 | 98.5 | CSA Group | [4/18/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-04-13 |  |  | N | N | 477 |  |  | 829 | 1300 | 1500 | 284.248 | 568.496 | 852.744 | 1421.24 | 2131.86 | 2842.48 | 98.07 | 98.64 | 98.68 | 98.62 | 98.41 | 98.17 | 98.47 | 97.43 | 98.29 | 98.38 | 98.41 | 98.24 | 98 | 98.25 | 97.02 | 98.07 | 98.2 | 98.3 | 98.13 | 97.9 | 98.12 | 2026-07-01 |  | Y | N | N | N | N | N | N | N | N
Delta Electronics | PCSC3556 {690V} | N | Y | N | N | N | N | Y* |  | 3570 kW, 690 Vac Bi-directional, Transformerless Grid support Utility Interactive Battery Inverter | 3570.33 | 690 | 98.5 | CSA Group | [4/18/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-04-13 |  |  | N | N | 477 |  |  | 1040 | 1300 | 1500 | 357.033 | 714.066 | 1071.099 | 1785.165 | 2677.7475 | 3570.33 | 98.2717 | 98.7672 | 98.8535 | 98.8432 | 98.6497 | 98.4719 | 98.6967 | 97.9428 | 98.6051 | 98.7349 | 98.7551 | 98.5698 | 98.3989 | 98.5966 | 97.7507 | 98.4955 | 98.6258 | 98.6615 | 98.5056 | 98.3318 | 98.5134 | 2026-04-01 | 2026-07-01 | Y | N | N | N | N | N | N | N | N
Delta Electronics | PCS4300X-X01-US {690V} | N | Y | N | N | N | N | N | N | 4000 kW, 690 Vac, Bi-directional, Transformerless Grid support Utility Interactive Battery Inverter, where the first X can be replaced by the letter "S" or "C", and the second X will be replaced by letter "S" | 4009 | 690 | 98.5 | CSA Group | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 550 |  |  | 1040 | 1300 | 1500 | 400.9 | 801.8 | 1202.7 | 2004.5 | 3006.75 | 4009 | 98.3313 | 98.8176 | 98.9182 | 98.8679 | 98.6429 | 98.4 | 98.7073 | 97.791 | 98.522 | 98.6945 | 98.7171 | 98.5648 | 98.3458 | 98.5683 | 97.1725 | 98.3056 | 98.5005 | 98.5828 | 98.4912 | 98.3135 | 98.4406 | 2025-08-11
Delta Electronics | DWE4150-EV-US {600V} | N | Y | N | N | N | N | N | N | 4156 kW, 600Vac, Bi-directional Grid Support Utility Interactive Inverter with Medium-voltage dry-type distribution transformer. | 4162.102 | 600 | 97 | CSA Group | [3/11/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1.729 |  |  | 875 | 1100 | 1350 | 416.2102 | 832.4204 | 1248.6306 | 2081.051 | 3121.5765 | 4162.102 | 95.3303 | 97.1473 | 97.5497 | 97.6796 | 97.4288 | 96.9617 | 97.3746 | 94.7154 | 96.7724 | 97.3415 | 97.5062 | 97.348 | 96.885 | 97.2232 | 94.3273 | 96.6111 | 97.2173 | 97.4797 | 97.2574 | 96.8815 | 97.131 | 2023-05-22 | 2024-09-03
Delta Electronics | PCS4300X-X00-US {690V} | N | Y | N | N | N | N | N | N | 4300 kW, 690 Vac, Bi-directional, Transformerless Grid support Utility Interactive Battery Inverter, where the first X can be replaced by the letter "S" or "C", and the second X will be replaced by letter "S" | 4308.4 | 690 | 98.5 | CSA Group | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 580 |  |  | 1040 | 1300 | 1500 | 430.84 | 861.68 | 1292.52 | 2154.2 | 3231.3 | 4308.4 | 98.5333 | 98.8744 | 99.0201 | 98.9214 | 98.6493 | 98.366 | 98.7434 | 98.0626 | 98.6079 | 98.8385 | 98.8033 | 98.5423 | 98.2702 | 98.6031 | 97.2235 | 98.2487 | 98.6908 | 98.6602 | 98.4581 | 98.2196 | 98.4567 | 2025-08-11
DYNAPOWER COMPANY LLC | MPS-100 {480V} | N | N | Y | N | Y | N | N | N | 100 kVA, 3-phase, 4-quadrant, bidirectional, 350-600VDC, 422-528VAC Grid Support Utility Interactive Battery Inverter with optional standalone mode. Inclusive of internal isolation transformer. | 98.861 | 480 | 93 | No Information Submitted | No Information Submitted | Intertek | [12/06/2017] | [251.25] | No Information Submitted | [12/06/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 803.97 |  |  | 350 | 475 | 600 | 9.8861 | 19.7722 | 29.6583 | 49.4305 | 74.1458 | 98.861 | 81.5497 | 89.9745 | 92.7648 | 95.0554 | 95.9538 | 96.2674 | 94.523 | 76.874 | 87.5246 | 90.7261 | 93.6858 | 95.0811 | 95.5789 | 93.1843 | 73.018 | 84.9646 | 89.0409 | 92.3812 | 94.007 | 94.6159 | 91.8084 | 2018-06-15
DYNAPOWER COMPANY LLC | MPS-125EHV {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 125 kW, 480 Vac Grid Support Utility Interactive Battery Inverter | 123.458 | 480 | 97.5 | TUV Rheinland | [5/9/2024] | Intertek | [6/18/2021] | [125_1_6];[125_2_47] | 2022-04-01 | [6/18/2020] | 2022-05-23 | Intertek | 2022-04-04 | 2022-05-23 |  | N | N | 50.5 |  |  | 740 | 1120 | 1500 | 12.3428 | 24.6856 | 37.0284 | 61.714 | 92.571 | 123.428 | 96.9341 | 97.9979 | 98.1549 | 98.2922 | 98.1811 | 97.8729 | 98.1269 | 94.6207 | 97.2918 | 97.6955 | 97.8474 | 97.7925 | 97.4855 | 97.6251 | 92.6142 | 96.1839 | 97.1727 | 97.4259 | 97.3864 | 96.9146 | 97.0944 | 2022-04-01 | 2024-08-01
DYNAPOWER COMPANY LLC | MPS-250 {480V} | N | N | Y | Y | Y | N | N | N | 250 kVA, 3-phase, 4-quadrant, bidirectional, 350-600 VDC, 422-528 VAC Grid Support Utility Interactive Battery Inverter with optional standalone mode. Inclusive of internal isolation transformer. | 248.91 | 480 | 95 | No Information Submitted | No Information Submitted | Intertek | [12/06/2017];[12/06/2017] | [V251.125];[251.25] | 2018-10-15 | [12/06/2017];[12/06/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1638.5 |  |  | 350 | 475 | 600 | 24.891 | 49.7812 | 74.6718 | 124.453 | 186.68 | 248.906 | 89.1 | 93.5 | 95 | 95.9 | 96 | 95.8 | 95.4 | 87.1 | 92.3 | 94.1 | 95.3 | 95.6 | 95.3 | 94.8 | 85.6 | 91.1 | 93 | 94.5 | 94.9 | 94.6 | 94 | 2018-02-15 | 2018-10-15
DYNAPOWER COMPANY LLC | MPS-250HV {480V} | N | N | Y | N | Y | N | N | N | 250 kVA, 3-phase, 4-quadrant, bidirectional, 580-835VDC, 422-528VAC Grid Support Utility Interactive Battery Inverter with optional standalone mode. Inclusive of internal isolation transformer. | 249.619 | 480 | 95.5 | No Information Submitted | No Information Submitted | Intertek | [12/06/2017] | [252.01] | No Information Submitted | [12/06/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 437.7 |  |  | 580 | 705 | 830 | 24.9619 | 49.9238 | 74.8857 | 124.8095 | 187.2142 | 249.619 | 89.1625 | 93.2778 | 94.9436 | 96.6352 | 96.5073 | 96.4981 | 95.8908 | 87.1443 | 92.741 | 94.1606 | 95.6894 | 96.3244 | 96.1982 | 95.3787 | 86.2167 | 91.8394 | 93.7002 | 95.0852 | 95.7877 | 95.8819 | 94.8141 | 2018-06-15
DYNAPOWER COMPANY LLC | CPS-1250 Gen5 {350V} | N | Y | N | N | N | N | N | N | 584 kW, 350Vac Grid Support Utility Interactive Battery Inverter | 582.49 | 350 | 97.5 | TUV Rheinland of North America | [12/9/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 130 |  |  | 530 | 1000 | 1500 | 58.249 | 116.498 | 174.747 | 291.245 | 436.868 | 582.49 | 98.42 | 98.51 | 98.34 | 98.11 | 97.82 | 97.46 | 97.98 | 97.23 | 97.81 | 97.93 | 97.8 | 97.63 | 97.34 | 97.68 | 95.39 | 96.94 | 97.28 | 97.3 | 97.18 | 97 | 97.12 | 2025-03-21
DYNAPOWER COMPANY LLC | CPS-1250 Gen5 {415V} | N | Y | N | N | N | N | N | N | 693 kW, 415Vac Grid Support Utility Interactive Battery Inverter | 691.248 | 415 | 98 | TUV Rheinland of North America | [12/9/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2200 |  |  | 630 | 1050 | 1500 | 69.125 | 138.25 | 207.374 | 345.624 | 518.436 | 691.248 | 98.19 | 98.53 | 98.5 | 98.34 | 98.06 | 97.8 | 98.19 | 97.49 | 98.11 | 98.21 | 98.16 | 97.96 | 97.72 | 98.01 | 96.21 | 97.42 | 97.73 | 97.83 | 97.73 | 97.55 | 97.66 | 2025-03-21
DYNAPOWER COMPANY LLC | CPS-1250 Gen5 {480V} | N | Y | N | N | N | N | N | N | 800 kW, 480 Vac, Grid Support Utility Interactive Inverter | 799.592 | 480 | 98 | TUV Rheinland of North America | [6/24/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 70 |  |  | 800 | 1145 | 1500 | 79.9592 | 159.9184 | 239.8776 | 399.796 | 599.694 | 799.592 | 98.0152 | 98.5205 | 98.5435 | 98.4684 | 98.2679 | 98.0261 | 98.3335 | 97.5394 | 98.2178 | 98.3553 | 98.3445 | 98.1952 | 97.9647 | 98.2091 | 96.9031 | 97.8225 | 98.093 | 98.154 | 98.0542 | 97.8993 | 98.0144 | 2024-12-11
DYNAPOWER COMPANY LLC | CPS-1250 Gen5 {600V} | N | Y | N | N | N | N | N | N | 1002 kW, 600Vac Grid Support Utility Interactive Battery Inverter | 999.576 | 600 | 98.5 | TUV Rheinland of North America | [12/9/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2400 |  |  | 900 | 1185 | 1500 | 99.958 | 199.915 | 299.873 | 499.788 | 749.682 | 999.576 | 98.09 | 98.66 | 98.76 | 98.76 | 98.64 | 98.47 | 98.65 | 97.62 | 98.38 | 98.6 | 98.65 | 98.58 | 98.43 | 98.54 | 97.45 | 98.26 | 98.52 | 98.57 | 98.53 | 98.41 | 98.47 | 2025-03-21
DYNAPOWER COMPANY LLC | CPS-1250 Gen5 {690V} | N | Y | N | N | N | N | N | N | 2300 kW, 690Vac Grid Support Utility Interactive Battery Inverter | 1146.1 | 690 | 98.5 | TUV Rheinland of North America | [12/9/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2400 |  |  | 1020 | 1250 | 1500 | 114.61 | 229.22 | 343.83 | 573.05 | 859.575 | 1146.1 | 98.05 | 98.7 | 98.85 | 98.88 | 98.8 | 98.64 | 98.78 | 97.68 | 98.51 | 98.72 | 98.79 | 98.75 | 98.6 | 98.69 | 97.61 | 98.46 | 98.66 | 98.72 | 98.7 | 98.59 | 98.64 | 2025-03-21
DYNAPOWER COMPANY LLC | CPS-1500 Gen4 {480V} | N | N | Y | Y | Y | N | Y* | N | 1200 kW, 480Vac Grid Support Utility Interactive Battery Inverter | 1199.64 | 480 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [08/31/2020] | [1500.01.27] | 2020-10-21 | [08/31/2020] | No Information Submitted | Intertek | 2022-12-05 | No Information Submitted |  | N | N | 438.5 |  |  | 740 | 1000 | 1500 | 119.964 | 239.928 | 359.892 | 599.82 | 899.73 | 1199.64 | 95.1475 | 96.6264 | 97.0793 | 97.0011 | 96.684 | 96.1612 | 96.7076 | 95.0089 | 96.2444 | 97.0385 | 96.8739 | 96.63 | 96.1664 | 96.623 | 95.054 | 95.9477 | 97.1667 | 96.6824 | 95.7593 | 96.1358 | 96.1221 | 2020-10-21 | 2024-03-21
DYNAPOWER COMPANY LLC | CPS-1250 Gen5 {800V} | N | Y | N | N | N | N | N | N | 2666 kW, 800Vac Grid Support Utility Interactive Battery Inverter | 1294.18 | 800 | 99 | TUV Rheinland of North America | [12/9/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2700 |  |  | 1020 | 1250 | 1500 | 129.418 | 258.836 | 388.254 | 647.09 | 970.635 | 1294.18 | 97.98 | 98.76 | 98.93 | 99.02 | 98.96 | 98.84 | 98.91 | 97.75 | 98.64 | 98.83 | 98.98 | 98.92 | 98.81 | 98.85 | 97.59 | 98.55 | 98.8 | 98.9 | 98.87 | 98.8 | 98.8 | 2025-03-21
DYNAPOWER COMPANY LLC | CPS-2500 Gen5 {415V} | N | Y | N | N | N | N | N |  | 1386 kW, 415Vac Grid Support Utility Interactive Battery Inverter | 1353.7 | 415 | 97 | TUV Rheinland of North America | [12/9/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 70.51 |  |  | 730 | 1100 | 1400 | 135.37 | 270.74 | 406.11 | 676.85 | 1015.275 | 1353.7 | 97.47 | 97.82 | 97.87 | 97.68 | 97.4 | 97.22 | 97.53 | 95.67 | 96.99 | 97.36 | 97.36 | 97.24 | 96.99 | 97.19 | 93.82 | 95.72 | 96.14 | 96.46 | 96.55 | 96.57 | 96.33 | 2026-04-13 |  | Y | Y | Y | Y | N | N | N | N | No Information Submitted
DYNAPOWER COMPANY LLC | CPS-1500 Gen4 {600V} | N | N | Y | Y | Y | N | Y* | N | 1500 kW, 600Vac Grid Support Utility Interactive Battery Inverter | 1498.66 | 600 | 97 | No Information Submitted | No Information Submitted | Intertek | [08/31/2020] | [1500.01.27] | 2020-10-21 | [08/31/2020] | No Information Submitted | Intertek | 2022-12-05 | No Information Submitted |  | N | N | 1241 |  |  | 900 | 1200 | 1500 | 149.866 | 299.732 | 449.598 | 749.33 | 1123.995 | 1498.66 | 93.9516 | 95.1495 | 98.053 | 97.386 | 97.3516 | 97.084 | 97.1835 | 93.453 | 94.8268 | 98.4238 | 97.4076 | 97.3745 | 97.0496 | 97.2069 | 93.0695 | 94.5456 | 98.6194 | 97.4606 | 97.3881 | 96.9779 | 97.2157 | 2020-10-21 | 2024-03-21
DYNAPOWER COMPANY LLC | CPS-2500 Gen5 {480V} | N | Y | N | N | N | N | N |  | 1603 kW, 480Vac Grid Support Utility Interactive Battery Inverter | 1572.92 | 480 | 98 | TUV Rheinland of North America | [12/9/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 25.49 |  |  | 810 | 1150 | 1500 | 157.292 | 314.584 | 471.876 | 786.46 | 1179.69 | 1572.92 | 98.78 | 98.93 | 98.69 | 98.27 | 97.93 | 97.65 | 98.16 | 99.02 | 98.71 | 98.42 | 98.08 | 97.76 | 97.35 | 97.98 | 97.88 | 98.87 | 98.56 | 97.98 | 97.62 | 97.36 | 97.87 | 2026-04-13 |  | Y | Y | Y | Y | N | N | N | N | No Information Submitted
DYNAPOWER COMPANY LLC | CPS-2500 Gen5 {600V} | N | Y | N | N | N | N | N |  | 2004 kW, 600Vac Grid Support Utility Interactive Battery Inverter | 1922.32 | 600 | 98.5 | TUV Rheinland of North America | [12/9/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 16.71 |  |  | 1150 | 1250 | 1500 | 192.232 | 384.464 | 576.696 | 961.16 | 1441.74 | 1922.32 | 98.28 | 99.01 | 98.68 | 98.4 | 98.11 | 97.88 | 98.28 | 98.48 | 99 | 98.74 | 98.39 | 98.05 | 97.82 | 98.26 | 99.2 | 98.77 | 98.85 | 98.41 | 98.05 | 97.8 | 98.29 | 2026-04-13 |  | Y | Y | Y | Y | N | N | N | N | No Information Submitted
DYNAPOWER COMPANY LLC | CPS-2500 Gen5 {690V} | N | Y | N | N | N | N | N |  | 2304 kW, 690Vac Grid Support Utility Interactive Battery Inverter | 2212.64 | 690 | 98 | TUV Rheinland of North America | [12/9/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 44.08 |  |  | 1150 | 1250 | 1500 | 221.264 | 442.528 | 663.792 | 1106.32 | 1659.48 | 2212.64 | 96.39 | 97.5545 | 97.8544 | 98.1343 | 98.045 | 97.8885 | 97.9423 | 95.7881 | 97.5545 | 97.8524 | 97.9981 | 97.9865 | 97.8334 | 97.8557 | 96.2267 | 96.9406 | 97.5031 | 97.6354 | 97.6972 | 97.6333 | 97.561 | 2026-04-13 |  | Y | Y | Y | Y | N | N | N | N | No Information Submitted
Dyness Digital Energy Technology Co., LTD. | TX5K-AM {240V} | N | Y | N | N | N | N | Y* | Y | 5kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment | 5.016 | 240 | 96.5 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.12 |  |  | 130 | 400 | 490 | 0.50164 | 1.0033 | 1.5049 | 2.5082 | 3.7623 | 5.0164 | 93.6066 | 94.7282 | 95.3523 | 95.6921 | 95.5212 | 95.2876 | 95.4089 | 93.5701 | 96.2214 | 96.6405 | 97.0866 | 97.1921 | 97.0586 | 96.9036 | 92.5682 | 95.2828 | 96.1683 | 96.8028 | 96.9149 | 96.8903 | 96.5451 | 2023-12-21 | 2024-01-22
Dyness Digital Energy Technology Co., LTD. | TX5K-HM {240V} | Y | Y | N | N | N | N | Y* | Y | 5kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment with PCS functionality | 5.02 | 240 | 96.5 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.13 |  |  | 180 | 390 | 500 | 0.50196 | 1.0039 | 1.5059 | 2.5098 | 3.7647 | 5.0196 | 94.3948 | 95.1559 | 95.9225 | 96.4043 | 96.1781 | 95.982 | 96.0627 | 95.6471 | 95.6407 | 96.5546 | 97.0291 | 97.2939 | 97.4239 | 97.0075 | 94.6422 | 95.0472 | 96.6033 | 97.424 | 97.4802 | 97.2415 | 97.1161 | 2023-12-21 | 2026-08-11 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Dyness Digital Energy Technology Co., LTD. | TX6K-HM {240V} | Y | Y | N | N | N | N | Y* | Y | 6kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment with PCS functionality | 6.018 | 240 | 97 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.12 |  |  | 210 | 390 | 500 | 0.60182 | 1.2036 | 1.8055 | 3.0091 | 4.5137 | 6.0182 | 92.6479 | 95.9948 | 96.4057 | 96.7027 | 96.4924 | 96.2024 | 96.333 | 93.9821 | 96.2752 | 96.9071 | 97.4028 | 97.411 | 97.3709 | 97.1529 | 91.4555 | 96.2207 | 97.4889 | 97.3222 | 97.4054 | 97.242 | 97.0925 | 2023-12-21 | 2026-08-11 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Dyness Digital Energy Technology Co., LTD. | TX6K-AM {240V} | N | Y | N | N | N | N | Y* | Y | 6kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment | 6.028 | 240 | 96.5 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.12 |  |  | 160 | 400 | 490 | 0.60284 | 1.2057 | 1.8085 | 3.0142 | 4.5213 | 6.0284 | 94.2402 | 95.2848 | 95.8773 | 96.2296 | 96.0133 | 95.4489 | 95.9069 | 92.8018 | 96.2268 | 96.8021 | 97.0567 | 97.1031 | 96.9812 | 96.8353 | 95.0941 | 96.1813 | 96.5091 | 96.8292 | 97.0898 | 96.8605 | 96.8287 | 2023-12-21 | 2024-01-22
Dyness Digital Energy Technology Co., LTD. | TX7.6K-AM {240V} | N | Y | N | N | N | N | Y* | Y | 7.6kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment | 7.636 | 240 | 96.5 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.11 |  |  | 200 | 400 | 490 | 0.7636 | 1.5272 | 2.2908 | 3.818 | 5.727 | 7.636 | 95.355 | 95.9138 | 96.3846 | 96.4714 | 96.3493 | 95.7019 | 96.2852 | 95.2791 | 96.6903 | 96.8339 | 97.123 | 97.0584 | 96.8301 | 96.944 | 93.8503 | 96.3626 | 96.55 | 96.772 | 96.9197 | 96.6794 | 96.6817 | 2023-12-21 | 2024-01-22
Dyness Digital Energy Technology Co., LTD. | TX7.6K-HM {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment with PCS functionality | 7.64 | 240 | 97 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.12 |  |  | 185 | 390 | 500 | 0.76402 | 1.528 | 2.2921 | 3.8201 | 5.7302 | 7.6402 | 95.2305 | 95.9104 | 96.3382 | 96.39 | 96.181 | 95.7506 | 96.1707 | 95.4068 | 96.4292 | 97.2246 | 97.2413 | 97.0365 | 97.244 | 97.0169 | 96.2864 | 96.8139 | 97.017 | 97.3106 | 97.2882 | 97.0989 | 97.1871 | 2023-12-21 | 2026-08-11 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Dyness Digital Energy Technology Co., LTD. | TX9.6K-HM {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment with PCS functionality | 9.648 | 240 | 96.5 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.14 |  |  | 170 | 390 | 500 | 0.96476 | 1.9295 | 2.8943 | 4.8238 | 7.2357 | 9.6476 | 94.8673 | 95.8966 | 96.2493 | 96.2284 | 95.8369 | 95.1616 | 95.899 | 95.3977 | 96.8238 | 96.9913 | 97.2596 | 96.9305 | 97.0122 | 96.9444 | 96.3825 | 97.453 | 97.2273 | 97.3321 | 97.3189 | 96.8944 | 97.2587 | 2023-12-21 | 2026-08-11 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Dyness Digital Energy Technology Co., LTD. | TX9.6K-AM {240V} | N | Y | N | N | N | N | Y* | Y | 9.6kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment | 9.662 | 240 | 97 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.12 |  |  | 250 | 400 | 490 | 0.96618 | 1.9324 | 2.8985 | 4.8309 | 7.2463 | 9.6618 | 96.1324 | 96.5324 | 96.7527 | 96.7781 | 96.5409 | 96.1796 | 96.5813 | 96.4805 | 96.9319 | 97.1305 | 97.1372 | 96.9534 | 96.5977 | 96.9755 | 96.3368 | 96.6259 | 96.8278 | 97.0017 | 96.8093 | 96.4763 | 96.8072 | 2023-12-21 | 2024-01-22
Dyness Digital Energy Technology Co., LTD. | TX11.4K-HM {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment with PCS functionality | 11.498 | 240 | 96.5 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.13 |  |  | 200 | 390 | 500 | 1.1498 | 2.2996 | 3.4495 | 5.7491 | 8.6237 | 11.4982 | 95.0784 | 96.3007 | 96.5753 | 96.4491 | 96.0568 | 95.4541 | 96.1443 | 95.9408 | 96.9844 | 97.1686 | 97.3098 | 96.831 | 96.8025 | 96.9427 | 97.1581 | 97.7094 | 97.3526 | 97.3607 | 97.0294 | 96.6666 | 97.1588 | 2023-12-21 | 2026-08-11 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Dyness Digital Energy Technology Co., LTD. | TX11.4K-AM {240V} | N | Y | N | N | N | N | Y* | Y | 11.4kW, 240Vac output,Bi-directional Transformerless Grid Support Utility Interactive Power Conversion Equipment | 11.519 | 240 | 97 | CSA Group | [9/8/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-26 | 2023-10-21 |  | N | N | 0.12 |  |  | 300 | 400 | 490 | 1.1519 | 2.3039 | 3.4558 | 5.7597 | 8.6395 | 11.5194 | 96.2623 | 96.946 | 97.0982 | 97.0339 | 96.6708 | 95.9998 | 96.7622 | 95.9719 | 96.9835 | 97.1749 | 97.0941 | 96.8145 | 96.339 | 96.8674 | 96.1402 | 96.7125 | 96.9553 | 96.933 | 96.687 | 96.2298 | 96.7274 | 2023-12-21 | 2024-01-22
EcoFlow Inc. | EF-PCS-24 {208V, 11.5kW} | Y | Y | N | N | N | N | Y* | Y | 11.5 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.4436 | 208 | 96 | SGS | [6/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-06-18 | 2025-08-11 |  | N | N | 115.89 |  |  | 120 | 370 | 480 | 1.1444 | 2.2887 | 3.4331 | 5.7218 | 8.5827 | 11.4436 | 92.506 | 94.602 | 94.35 | 96.164 | 95.27 | 95.384 | 95.2091 | 91.666 | 95.36 | 95.804 | 96.418 | 96.484 | 96.6 | 96.1454 | 91.85 | 95.408 | 96.364 | 96.98 | 97.104 | 97.006 | 96.6893 | 2025-08-11 | 2026-06-01 | N | Y | N | N | N | N | N | N | No Information Submitted
EcoFlow Inc. | EF-PCS-24 {240V, 11.5kW} | Y | Y | N | N | N | N | Y* | Y | 11.5 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.4442 | 240 | 96 | SGS | [6/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-06-18 | 2025-08-11 |  | N | N | 115.86 |  |  | 120 | 370 | 480 | 1.1444 | 2.2888 | 3.4333 | 5.7221 | 8.5832 | 11.4442 | 92.636 | 94.348 | 94.39 | 95.352 | 95.612 | 95.088 | 95.2023 | 91.72 | 94.64 | 95.876 | 96.482 | 96.608 | 96.79 | 96.2089 | 91.818 | 95.37 | 96.352 | 96.966 | 97.104 | 97.02 | 96.6824 | 2025-08-11 | 2026-06-01 | N | Y | N | N | N | N | N | N | No Information Submitted
EcoFlow Inc. | EF-PCS-24 {240V, 24kW} | Y | Y | N | N | N | N | Y* | Y | 24 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 24.0123 | 240 | 97 | SGS | [6/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-06-18 | 2025-08-11 |  | N | N | 117.14 |  |  | 320 | 400 | 480 | 2.4012 | 4.8025 | 7.2037 | 12.0062 | 18.0092 | 24.0123 | 94.74 | 96.484 | 97.044 | 96.952 | 96.8 | 96.472 | 96.7466 | 96.168 | 97.278 | 97.586 | 97.364 | 97.03 | 96.856 | 97.1361 | 95.304 | 96.724 | 97.242 | 97.44 | 97.262 | 96.942 | 97.1758 | 2025-08-11 | 2026-06-01 | N | Y | N | N | N | N | N | N | No Information Submitted
EcoFlow Inc. | EF-PCS-24 {208V, 24kW} | Y | Y | N | N | N | N | Y* | Y | 24 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 24.2914 | 208 | 96.5 | SGS | [6/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-06-18 | 2025-08-11 |  | N | N | 117.25 |  |  | 320 | 400 | 480 | 2.4291 | 4.8583 | 7.2874 | 12.1457 | 18.2185 | 24.2914 | 94.72 | 96.05 | 96.45 | 96.43 | 96.162 | 95.75 | 96.169 | 95.394 | 96.162 | 96.556 | 96.588 | 96.37 | 96.008 | 96.3706 | 95.09 | 96.7 | 97.03 | 96.99 | 96.684 | 96.272 | 96.7062 | 2025-08-11 | 2026-06-01 | N | Y | N | N | N | N | N | N | No Information Submitted
Eco-Worthy | ECO-INV-48V12KWSR01 {208V} | Y | Y | N | N | N | N | N |  | 10.4 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.397 | 208 | 96.5 | Intertek/ETL | [8/10/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.04 | 2.079 | 3.119 | 5.199 | 7.798 | 10.397 | 95.11 | 95.71 | 96.53 | 96.55 | 96.71 | 95.27 | 96.47 | 95.33 | 96.1 | 96.62 | 96.92 | 97.48 | 95.26 | 96.99 | 95.04 | 95.77 | 96.6 | 96.55 | 96.67 | 95.19 | 96.45 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Eco-Worthy | ECO-INV-48V12KWSR01 {240V} | Y | Y | N | N | N | N | N |  | 12 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.996 | 240 | 96.5 | Intertek/ETL | [8/10/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.2 | 2.399 | 3.599 | 5.998 | 8.997 | 11.996 | 95.45 | 95.69 | 96.38 | 96.39 | 96.5 | 95.23 | 96.32 | 95.57 | 96.17 | 96.69 | 96.87 | 97.43 | 95.23 | 96.98 | 95.53 | 95.87 | 96.6 | 96.46 | 96.54 | 95.32 | 96.39 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
EG4 Electronics LLC | IV-8000-HYB-AW {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 208 Vac Grid Support Hybrid 12kPV Inverter with PCS functionality. | 7.8599 | 208 | 96.5 | Intertek | [4/10/2024] | Intertek | [4/3/2025] | [EA1.0] | 2025-06-11 | [4/3/2025] | 2025-06-11 | Intertek | 2024-02-22 | 2024-06-21 |  | N | N | 18.53 |  |  | 210 | 360 | 480 | 0.78599 | 1.572 | 2.358 | 3.93 | 5.895 | 7.8599 | 92.7458 | 94.8821 | 95.7877 | 96.2814 | 95.7548 | 95.5452 | 95.6949 | 95.3183 | 96.7852 | 96.9298 | 97.2401 | 96.7733 | 96.6331 | 96.8255 | 94.866 | 96.387 | 96.7215 | 97.1053 | 96.6941 | 96.6144 | 96.6913 | 2024-06-21 | 2025-06-11
EG4 Electronics LLC | IV-8000-HYB-AW {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac Grid Support Hybrid 12kPV Inverter with PCS functionality. | 7.8627 | 240 | 96.5 | Intertek | [4/10/2024] | Intertek | [4/3/2025] | [EA1.0] | 2025-06-11 | [4/3/2025] | 2025-06-11 | Intertek | 2024-02-22 | 2024-06-21 |  | N | N | 18.84 |  |  | 210 | 360 | 480 | 0.78627 | 1.5725 | 2.3588 | 3.9313 | 5.897 | 7.8627 | 92.9578 | 94.8899 | 95.7481 | 96.2838 | 95.9702 | 95.8604 | 95.8294 | 95.5741 | 96.5787 | 96.6854 | 97.0389 | 96.7425 | 96.7486 | 96.7433 | 94.682 | 96.1785 | 96.6318 | 96.9367 | 96.7571 | 96.7998 | 96.67 | 2024-06-21 | 2025-06-11
EG4 Electronics LLC | 18KPV-12LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.4 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter (IV-12000-HYB-AW- may be followed by 00-99) with PCS functionality. | 10.499 | 208 | 96.5 | Intertek | [4/3/2025] | Intertek | [4/3/2025] | [fA1.0] | 2025-06-02 | [4/3/2025] | 2025-06-02 | Intertek | 2022-05-27 | 2024-02-21 |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.05 | 2.1 | 3.15 | 5.25 | 7.875 | 10.499 | 93.48 | 95.27 | 95.93 | 95.85 | 95.61 | 95.29 | 95.58 | 95.07 | 96.66 | 97.03 | 97.31 | 97.1 | 96.41 | 96.99 | 94.29 | 96.71 | 97.16 | 96.95 | 96.77 | 96.47 | 96.74 | 2023-06-21 | 2025-06-02
EG4 Electronics LLC | IV-13000-HYB-AW-FX-xx {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.3 kW, 208 Vac Grid Support Utility Interactive FlexBOSS18 Inverter, where xx = 00-99. Inverter with PCS functionality. | 11.325 | 208 | 97 | Intertek | [1/23/2025] | Intertek | [3/13/2025] | [fA1.0] | 2025-05-21 | [3/13/2025] | 2025-05-21 | Intertek | 2025-04-15 | 2025-06-23 |  | N | N | 31.95 |  |  | 250 | 360 | 440 | 1.133 | 2.265 | 3.398 | 5.663 | 8.494 | 11.325 | 96.29 | 96.28 | 96.21 | 96.25 | 96.23 | 96.33 | 96.24 | 96.07 | 96.94 | 97.19 | 97.71 | 97.5 | 96.64 | 97.38 | 95.73 | 97.68 | 97.82 | 98 | 97.11 | 97.31 | 97.36 | 2025-04-01 | 2025-06-23
EG4 Electronics LLC | 18KPV-12LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter (IV-12000-HYB-AW- may be followed by 00-99) with PCS functionality. | 11.933 | 240 | 97 | Intertek | [4/3/2025] | Intertek | [4/3/2025] | [fA1.0] | 2025-06-02 | [4/3/2025] | 2025-06-02 | Intertek | 2022-05-27 | 2024-02-21 |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.193 | 2.387 | 3.58 | 5.966 | 8.949 | 11.933 | 95.02 | 96.1 | 96.54 | 96.5 | 96.13 | 95.9 | 96.2 | 96.59 | 97.19 | 97.51 | 97.34 | 97.24 | 97.1 | 97.26 | 95.82 | 97.01 | 97.42 | 97.26 | 97.14 | 97.04 | 97.13 | 2023-06-21 | 2025-06-02
EG4 Electronics LLC | IV-13000-HYB-AW-FX-xx {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12.9 kW, 240 Vac Grid Support Utility Interactive FlexBOSS18 Inverter, where xx = 00-99. Inverter with PCS functionality. | 12.997 | 240 | 96.5 | Intertek | [1/23/2025] | Intertek | [3/13/2025] | [fA1.0] | 2025-05-21 | [3/13/2025] | 2025-05-21 | Intertek | 2025-04-15 | 2025-06-23 |  | N | N | 29.57 |  |  | 250 | 360 | 440 | 1.3 | 2.599 | 3.899 | 6.499 | 9.748 | 12.997 | 95.84 | 96.15 | 95.67 | 96.57 | 96.39 | 96.14 | 96.3 | 96.62 | 97.05 | 97.3 | 98.11 | 96.99 | 96.68 | 97.24 | 96.24 | 96.52 | 96.56 | 96.51 | 96.26 | 96.12 | 96.35 | 2025-04-01 | 2025-06-23
EG4 Electronics LLC | IV-16000-HYB-AW-FX-xx {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 13.8 kW, 208 Vac Grid Support Utility Interactive FlexBOSS21 Inverter, where xx = 00-99. Inverter with PCS functionality. | 13.8987 | 208 | 96.5 | Intertek | [10/23/2024] | Intertek | [3/13/2025] | [fA1.0] | 2025-05-21 | [3/13/2025] | 2025-05-21 | Intertek | 2025-04-15 | 2025-06-23 |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.3899 | 2.7797 | 4.1696 | 6.9494 | 10.424 | 13.8987 | 95.2216 | 96.3623 | 96.3314 | 96.3567 | 96.0039 | 95.9864 | 96.103 | 95.5416 | 96.5717 | 96.9718 | 97.1706 | 97.0713 | 96.2488 | 96.9529 | 95.5994 | 96.8339 | 97.3771 | 97.1744 | 97.0907 | 96.9737 | 97.0643 | 2025-01-02 | 2025-06-23
EG4 Electronics LLC | IV-16000-HYB-AW-FX-xx {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 16 kW, 240 Vac Grid Support Utility Interactive FlexBOSS21 Inverter, where xx = 00-99. Inverter with PCS functionality. | 16.1532 | 240 | 97 | Intertek | [10/23/2024] | Intertek | [3/13/2025] | [fA1.0] | 2025-05-21 | [3/13/2025] | 2025-05-21 | Intertek | 2025-04-15 | 2025-06-23 |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.6153 | 3.2306 | 4.846 | 8.0766 | 12.1149 | 16.1532 | 95.0963 | 95.9965 | 96.3882 | 96.4022 | 96.7311 | 95.8608 | 96.4752 | 96.4687 | 97.0976 | 97.478 | 97.1222 | 97.077 | 96.941 | 97.1045 | 95.4554 | 96.9149 | 97.2473 | 97.1696 | 96.9929 | 96.8158 | 96.9863 | 2025-01-02 | 2025-06-23
Energizer Solar | Force 3.8DC {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 3.713 | 240 | 96 | CSA Group | [11/20/2023] | CSA Group | [11/20/2023] | [V1.08, V1.02] | 2024-02-01 | [11/20/2023] | 2024-02-01 | CSA Group | 2023-11-22 | 2024-02-01 |  | N | N | 27.23 |  |  | 204 | 380 | 480 | 0.3713 | 0.74261 | 1.1139 | 1.8565 | 2.7848 | 3.713 | 88.7571 | 93.1319 | 94.7403 | 95.8238 | 96.4154 | 96.5626 | 95.627 | 90.646 | 94.5568 | 95.593 | 96.5203 | 97.3128 | 97.201 | 96.5299 | 87.3378 | 93.647 | 95.4273 | 96.4142 | 97.3282 | 97.4961 | 96.3329 | 2024-02-01 | 2024-05-21
Energizer Solar | Force 5.7DC {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 5.7482 | 240 | 97 | CSA Group | [11/20/2023] | CSA Group | [11/20/2023] | [V1.08, V1.02] | 2024-02-01 | [11/20/2023] | 2024-02-01 | CSA Group | 2023-11-22 | 2024-02-01 |  | N | N | 27.23 |  |  | 204 | 380 | 480 | 0.57482 | 1.1496 | 1.7245 | 2.8741 | 4.3111 | 5.7482 | 90.8808 | 94.8098 | 95.7632 | 96.4753 | 96.7386 | 96.703 | 96.2337 | 91.5018 | 95.6465 | 97.2168 | 97.6379 | 97.868 | 97.771 | 97.371 | 89.8373 | 95.634 | 96.4644 | 97.2092 | 97.4788 | 97.595 | 96.9084 | 2024-02-01 | 2024-05-21
Energizer Solar | Force 7.6DC {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 7.7203 | 240 | 97 | CSA Group | [11/20/2023] | CSA Group | [11/20/2023] | [V1.08, V1.02] | 2024-02-01 | [11/20/2023] | 2024-02-01 | CSA Group | 2023-11-22 | 2024-02-01 |  | N | N | 27.23 |  |  | 271 | 380 | 480 | 0.77203 | 1.5441 | 2.3161 | 3.8602 | 5.7903 | 7.7203 | 93.4996 | 95.7999 | 96.5407 | 97.0482 | 97.1101 | 96.8974 | 96.8082 | 93.8722 | 96.8306 | 97.0752 | 97.4311 | 97.293 | 97.6679 | 97.1547 | 92.4126 | 96.3152 | 97.0656 | 97.6101 | 97.731 | 97.5149 | 97.3315 | 2024-02-01 | 2024-05-21
Energizer Solar | Force 9.6DC {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 9.6091 | 240 | 97 | CSA Group | [11/20/2023] | CSA Group | [11/20/2023] | [V1.08, V1.02] | 2024-02-01 | [11/20/2023] | 2024-02-01 | CSA Group | 2023-11-22 | 2024-02-01 |  | N | N | 27.23 |  |  | 257 | 380 | 480 | 0.96091 | 1.9218 | 2.8827 | 4.8046 | 7.2068 | 9.6091 | 94.0151 | 96.18 | 96.7302 | 97.0459 | 96.9854 | 96.7841 | 96.7983 | 95.6441 | 97.147 | 97.1617 | 97.4712 | 97.3224 | 97.1525 | 97.25 | 94.7056 | 96.5502 | 97.2561 | 97.5742 | 97.6405 | 97.2619 | 97.3896 | 2024-02-01 | 2024-05-21
Energizer Solar | Force 11.4DC {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 11.5119 | 240 | 97.5 | CSA Group | [11/20/2023] | CSA Group | [11/20/2023] | [V1.08, V1.02] | 2024-02-01 | [11/20/2023] | 2024-02-01 | CSA Group | 2023-11-22 | 2024-02-01 |  | N | N | 27.23 |  |  | 305 | 380 | 480 | 1.1512 | 2.3024 | 3.4536 | 5.756 | 8.6339 | 11.5119 | 95.5005 | 96.9797 | 97.2834 | 97.3603 | 97.1804 | 96.9301 | 97.1408 | 96.2352 | 97.384 | 97.7697 | 97.5626 | 97.4234 | 97.4212 | 97.4446 | 95.7811 | 97.2716 | 97.6352 | 97.6967 | 97.6385 | 97.1496 | 97.5332 | 2024-02-01 | 2024-05-21
Enphase Energy, Inc. | IQ8X-BAT-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 V, Grid Support Utility Interactive Microinverter for use in Enphase's storage system | 0.315 | 240 | 96.5 | UL | [10/7/2024] | UL | [11/17/2020];[11/17/2020];[08/26/2021];[09/17/2021];[04/22/2022];[9/30/2022];[6/23/2023];[11/30/2023]; [10/7/2024] | [v01.30.01];[v01.31.1];[V3.11.01];[V3.19.02];[V3.21.02];[V3.24.01];[V3.25.01];[V3.26.01];[V3.32.01]; [V3.38.01] | [11/17/2020];[11/17/2020];[08/26/2021];[09/17/2021];[04/22/2022];[9/30/2022];[6/23/2023];[11/30/2023]; [10/7/2024] | [11/17/2020];[11/17/2020];[08/26/2021];[09/17/2021];[04/22/2022];[9/30/2022];[6/23/2023];[11/30/2023] | 2020-07-01 | UL | 2020-06-11 | 2020-07-01 | IQ8X-BAT-US is for use in Enphase Energy's energy storage product named Encharge in either an individual unit configuration (ENCHARGE-3-1P-NA), or as a trio of units (ENCHARGE-10-1P-NA). Model IQ8X-BAT-US is not intended for use with other third-party battery sources. | N | Y | 0.024 |  |  | 52.5 | 63 | 73.5 | 0.031776 | 0.063551 | 0.095327 | 0.15888 | 0.23832 | 0.31776 | 88.1194 | 93.9712 | 96.1546 | 97.3997 | 97.4828 | 97.2008 | 96.7418 | 87.7712 | 93.4122 | 95.6873 | 97.1995 | 97.4368 | 97.2642 | 96.5805 | 87.0694 | 92.8086 | 95.2929 | 96.9958 | 97.3087 | 97.1752 | 96.3598 | 2020-07-01 | 2024-11-12
Enphase Energy, Inc. | IQ8X-BAT-US-NB {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 315 VA, 240 V, Grid Support Utility Interactive Microinverter for use in Enphase's energy storage system | 0.315 | 240 | 96.5 | UL | [10/7/2024] | UL | [11/17/2020];[11/17/2020];[08/26/2021];[09/17/2021];[04/22/2022];[9/30/2022];[6/23/2023];[11/30/2023]; [10/7/2024] | [v01.30.01];[v01.31.1];[V3.11.01];[V3.19.02];[V3.21.02];[V3.24.01];[V3.25.01];[V3.26.01];[V3.32.01]; [V3.38.01] | [11/17/2020];[11/17/2020];[08/26/2021];[09/17/2021];[04/22/2022];[9/30/2022];[6/23/2023];[11/30/2023]; [10/7/2024] | [11/17/2020];[11/17/2020];[08/26/2021];[09/17/2021];[04/22/2022];[9/30/2022];[6/23/2023];[11/30/2023] | 2021-01-21 | UL | 2020-12-14 | 2021-01-21 | IQ8X-BAT-US-NB is for use in Enphase Energy's energy storage product named Encharge in either an individual unit configuration (ENCHARGE-3T-1P-NA), or as a trio of units (ENCHARGE-10T-1P-NA). Model IQ8X-BAT-US-NB is not intended for use with other third-party battery sources. | N | Y | 0.024 |  |  | 52.5 | 63 | 73.5 | 0.031776 | 0.063551 | 0.095327 | 0.15888 | 0.23832 | 0.31776 | 88.1194 | 93.9712 | 96.1546 | 97.3997 | 97.4828 | 97.2008 | 96.7418 | 87.7712 | 93.4122 | 95.6873 | 97.1995 | 97.4368 | 97.2642 | 96.5805 | 87.0694 | 92.8086 | 95.2929 | 96.9958 | 97.3087 | 97.1752 | 96.3598 | 2021-01-21 | 2024-11-12
Enphase Energy, Inc. | IQ8D-BAT {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 555 VA, 208 Vac, Grid Support Utility Interactive Inverter Multimode Inverter for use in Enphase's energy storage system. Inverter with PCS functionality. | 0.55492 | 208 | 96.5 | UL | [1/30/2025] | UL | [10/24/2024] | [4.64.01] | 2024-12-23 | [10/24/2024] | 2024-12-23 | UL | 2024-08-20 | 2024-12-23 |  | N | Y | 0.033 |  |  | 60 | 73.5 | 87 | 0.055492 | 0.11098 | 0.16648 | 0.27746 | 0.41619 | 0.55492 | 88.831 | 94.4293 | 96.4257 | 97.4583 | 97.2696 | 96.7655 | 96.7032 | 88.1035 | 94.1487 | 95.9675 | 97.5432 | 97.5926 | 97.308 | 96.8212 | 87.2298 | 93.6079 | 95.5183 | 97.3384 | 97.4968 | 97.2546 | 96.6089 | 2024-12-23 | 2025-07-11
Enphase Energy, Inc. | IQ8D-BAT-DOM {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 555 VA, 208 Vac, Grid Support Utility Interactive Inverter Multimode Inverter for use in Enphase's Energy Storage System | 0.55492 | 208 | 96.5 | UL | [10/24/2024] | UL | [10/24/2024] | [4.64.01] | 2024-12-23 | [10/24/2024] | 2024-12-23 | UL | 2024-08-20 | 2024-12-23 |  | N | Y | 0.033 |  |  | 60 | 73.5 | 87 | 0.055492 | 0.11098 | 0.16648 | 0.27746 | 0.41619 | 0.55492 | 88.831 | 94.4293 | 96.4257 | 97.4583 | 97.2696 | 96.7655 | 96.7032 | 88.1035 | 94.1487 | 95.9675 | 97.5432 | 97.5926 | 97.308 | 96.8212 | 87.2298 | 93.6079 | 95.5183 | 97.3384 | 97.4968 | 97.2546 | 96.6089 | 2024-12-23
Enphase Energy, Inc. | IQ8D-BAT {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.64 VA, 240 Vac, Grid Support Utility Interactive Microvinverter for use in Enphase's energy storage system. Inverter with PCS functionality. | 0.63877 | 240 | 97 | UL | [1/30/2025] | UL | [10/24/2024] | [4.31.01, 4.35.01, 4.36.01, 4.62.01, 4.64.01] | 2023-08-01 | [10/24/2024] | 2023-08-01 | UL | 2023-04-25 | 2023-08-01 |  | N | Y | 0.0579 |  |  | 60 | 73.5 | 87 | 0.063877 | 0.12775 | 0.19163 | 0.31939 | 0.47908 | 0.63877 | 88.2248 | 94.8375 | 96.6348 | 97.4758 | 97.2706 | 96.7177 | 96.7262 | 88.1568 | 94.331 | 96.4651 | 97.5546 | 97.7186 | 97.4633 | 96.9692 | 87.3024 | 94.0526 | 95.7927 | 97.5278 | 97.7771 | 97.6332 | 96.8742 | 2023-08-01 | 2025-07-11
Enphase Energy, Inc. | IQ8D-BAT-240 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 0.64 kW, 240 Vac, Grid Support Utility Interactive Microvinverter for use in Enphase's energy storage system | 0.63877 | 240 | 97 | UL | [10/30/2023] | UL | [10/30/2023] | [4.31.01, 4.35.01, 4.36.01] | 2023-05-22 | [10/30/2023] | 2023-05-22 | UL | 2023-04-25 | 2023-05-22 | IQ8D-BAT-240 is for use in Enphase Energy's energy storage product named, IQBATTERY-5P-1P-NA. Model IQ8D-BAT-240 is not intended for use with other third-party battery sources. | N | Y | 0.0579 |  |  | 60 | 73.5 | 87 | 0.063877 | 0.12775 | 0.19163 | 0.31939 | 0.47908 | 0.63877 | 88.2248 | 94.8375 | 96.6348 | 97.4758 | 97.2706 | 96.7177 | 96.7262 | 88.1568 | 94.331 | 96.4651 | 97.5546 | 97.7186 | 97.4633 | 96.9692 | 87.3024 | 94.0526 | 95.7927 | 97.5278 | 97.7771 | 97.6332 | 96.8742 | 2023-05-22 | 2024-01-02
Enphase Energy, Inc. | IQ8D-BAT-DOM {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 640 VA, 240 V, Grid Support Utility Interactive Microinverter for use in Enphase's energy storage system | 0.63877 | 240 | 97 | UL | [10/24/2024] | UL | [10/24/2024] | [4.31.01, 4.35.01, 4.36.01, 4.62.01, 4.64.01] | 2024-10-01 | [10/24/2024] | 2024-10-01 | UL | 2024-08-20 | 2024-10-01 | IQ8D-BAT-DOM is for use in Enphase Energy's energy storage system named IQBATTERY-5P-1P-NA. Model IQ8D-BAT-DOM is not intended for use with other third-party battery sources. | N | Y | 0.0579 |  |  | 60 | 73.5 | 87 | 0.063877 | 0.12775 | 0.19163 | 0.31939 | 0.47908 | 0.63877 | 88.2248 | 94.8375 | 96.6348 | 97.4758 | 97.2706 | 96.7177 | 96.7262 | 88.1568 | 94.331 | 96.4651 | 97.5546 | 97.7186 | 97.4633 | 96.9692 | 87.3024 | 94.0526 | 95.7927 | 97.5278 | 97.7771 | 97.6332 | 96.8742 | 2024-10-01 | 2024-12-23
Enphase Energy, Inc. | IQBATTERY-10C-1P-NA {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.08 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.08 | 240 | 96 | Bureau Veritas Consumer Products Services | [4/2/2025] | Bureau Veritas Consumer Products Services | [12/4/2025] | [4.4.28, 10.9.45, 10.9.46], [4.5.35, 10.09.63, 10.09.64], [4.5.37, 10.09.67, 10.09.68], [4.5.46, 10.09.79, 10.09.80], [4.7.4, 10.09.81, 10.09.82], [4.7.14, 10.09.99, 10.09.100], [4.7.15, 10.09.103, 10.09.104] | 2025-06-02 | [4/2/2025] | 2025-06-02 | Bureau Veritas Consumer Products Services | 2025-03-11 | 2025-06-02 |  | N | N | 0.62 |  |  | 70 | 77 | 84 | 0.70925 | 1.4185 | 2.1277 | 3.5462 | 5.3193 | 7.0925 | 83.9052 | 92.582 | 95.2861 | 96.9667 | 97.0276 | 96.635 | 96.039 | 83.454 | 92.251 | 94.9857 | 96.851 | 97.0966 | 96.8952 | 95.9937 | 82.7297 | 91.7904 | 94.6251 | 96.6391 | 96.9609 | 96.8354 | 95.779 | 2025-06-02 | 2026-01-21
Enphase Energy, Inc. | IQBATTERY-10CS-1P-NA {240V} | N | Y | Y | Y | Y | Y | Y* |  | 7.08 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.08 | 240 | 96 | Bureau Veritas Consumer Products Services | [4/2/2025] | Bureau Veritas Consumer Products Services | [1/21/2026] | [4.4.28, 10.9.45, 10.9.46], [4.5.35, 10.09.63, 10.09.64], [4.5.37, 10.09.67, 10.09.68], [4.5.46, 10.09.79, 10.09.80], [4.7.4, 10.09.81, 10.09.82], [4.7.14, 10.09.99, 10.09.100], [4.7.15, 10.09.103, 10.09.104] | 2026-03-11 | [1/21/2026] | 2026-03-11 | Bureau Veritas Consumer Products Services | 2025-03-11 |  |  | N | N | 0.62 |  |  | 70 | 77 | 84 | 0.709 | 1.418 | 2.128 | 3.546 | 5.319 | 7.092 | 83.91 | 92.58 | 95.29 | 96.97 | 97.03 | 96.64 | 96.04 | 83.45 | 92.25 | 94.99 | 96.85 | 97.1 | 96.9 | 95.99 | 82.73 | 91.79 | 94.63 | 96.64 | 96.96 | 96.84 | 95.78 | 2026-03-11
EPC Power Corp. | HY LC12/6-7 {480V} | Y | N | Y | Y | Y | N | N | N | 220 kVA, 480 Vac, 3 phase Grid Support Utility Interactive Hybrid Inverter with PV MPPT and DC input | 220.033 | 480 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [09/25/2018] | [042C314] | 2019-01-15 | [09/25/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 19.2 |  |  | 455 | 475 | 600 | 22.0033 | 44.0067 | 66.01 | 110.0167 | 165.025 | 220.0333 | 95.0157 | 96.16 | 96.4114 | 96.3571 | 96.0943 | 95.7657 | 96.1313 | 93.9614 | 95.3957 | 95.6729 | 95.7343 | 95.5243 | 95.18 | 95.5001 | 94.3386 | 95.8 | 96.0971 | 96.1657 | 96.0143 | 95.7186 | 95.9635 | 2019-01-15
EPC Power Corp. | 50-100122 {480V} | N | N | Y | Y | Y | Y | N | N | 250 kVA, 480Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 250.19 | 480 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [2/26/2019] | [8669C3F];[a501a47];[fe924e5] | 2019-04-15 | [2/26/2019] | 2021-05-03 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 20 |  |  | 710 | 950 | 1250 | 25.019 | 50.038 | 75.057 | 125.095 | 187.643 | 250.19 | 94.8 | 96.79 | 97.38 | 97.66 | 97.6 | 97.44 | 97.42 | 94.12 | 96.48 | 97.08 | 97.37 | 97.29 | 97.04 | 97.1 | 92.55 | 95.64 | 96.52 | 96.95 | 96.97 | 96.78 | 96.66 | 2019-04-15 | 2021-05-03
EPC Power Corp. | 50-100205 {480V} | N | Y | Y | Y | Y | Y | Y* | N | 250 kVA, 480Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 250.19 | 480 | 97 | TUV Rheinland of North America | [6/13/2024] | TUV Rheinland of North America | [04/14/2021];[10/07/2020];[02/21/2021] | [fe924e5];[a501a47];[8669C3F] | 2021-05-03 | [07/27/2020] | 2021-05-03 | TUV Rheinland | 2022-01-24 | No Information Submitted | Grid Support Utility Interactive type for the requested model is already listed; this request is to add the CSIP tests for the same model number. | N | N | 20 |  |  | 710 | 950 | 1250 | 25.019 | 50.038 | 75.057 | 125.095 | 187.643 | 250.19 | 94.8 | 96.79 | 97.38 | 97.66 | 97.6 | 97.44 | 97.42 | 94.12 | 96.48 | 97.08 | 97.37 | 97.29 | 97.04 | 97.1 | 92.55 | 95.64 | 96.52 | 96.95 | 96.97 | 96.78 | 96.66 | 2021-05-03 | 2024-08-01
EPC Power Corp. | 50-200100 {350V} | N | Y | N | N | N | N | N |  | 273 kVA, 350 Vac 3 phase Grid Support Utility Interactive Battery Inverter | 273.231 | 350 | 98 | TUV Rheinland of North America | [4/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 0 |  |  | 575 | 887.5 | 1200 | 27.323 | 54.646 | 81.969 | 136.615 | 204.923 | 273.231 | 98.46 | 98.95 | 99.01 | 98.88 | 98.56 | 98.17 | 98.68 | 96.45 | 97.8 | 98.22 | 98.29 | 98.09 | 97.7 | 98.05 | 93.02 | 96.22 | 97.06 | 97.45 | 97.44 | 97.08 | 97.14 | 2025-10-01
EPC Power Corp. | 50-200100 {480V} | N | Y | N | N | N | N | N |  | 375 kVA, 480 Vac 3 phase Grid Support Utility Interactive Battery Inverter | 375.012 | 480 | 98.5 | TUV Rheinland of North America | [4/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 0 |  |  | 784 | 992 | 1200 | 37.501 | 75.002 | 112.503 | 187.506 | 281.259 | 375.012 | 98.35 | 98.92 | 99.05 | 98.99 | 98.77 | 98.48 | 98.83 | 97.45 | 98.33 | 98.64 | 98.7 | 98.55 | 98.27 | 98.52 | 95.74 | 97.58 | 98.06 | 98.3 | 98.24 | 97.97 | 98.08 | 2025-10-01
EPC Power Corp. | 50-100100 {208V} | N | Y | Y | Y | Y | Y | Y* | N | 450 kVA, 208Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 452.6 | 208 | 95.5 | TUV Rheinland of North America | [6/27/2024] | TUV Rheinland of North America | [07/07/2021];[07/07/2021] | [a501a47];[fe924e5] | 2021-08-02 | [07/07/2021];[07/07/2021] | 2021-08-02 | TUV Rheinland | 2022-01-24 | No Information Submitted |  | N | N | 0 |  |  | 400 | 700 | 1000 | 45.26 | 90.52 | 135.78 | 226.3 | 339.45 | 452.6 | 94.6568 | 96.9294 | 97.2858 | 97.2732 | 96.0412 | 93.8658 | 96.3295 | 92.5436 | 95.2824 | 96.104 | 96.3762 | 95.149 | 92.7892 | 95.3058 | 90.0808 | 93.6788 | 94.7806 | 95.3118 | 94.371 | 92.6334 | 94.3246 | 2021-08-02 | 2024-08-01
EPC Power Corp. | 50-200100 {600V} | N | Y | N | N | N | N | N |  | 468 kVA, 600 Vac 3 phase Grid Support Utility Interactive Battery Inverter | 468.347 | 600 | 98.5 | TUV Rheinland of North America | [4/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 0 |  |  | 985 | 1242.5 | 1500 | 46.835 | 93.669 | 140.504 | 234.173 | 351.26 | 468.347 | 98.24 | 98.89 | 99.05 | 99.05 | 98.9 | 98.67 | 98.91 | 97.02 | 98.16 | 98.55 | 98.67 | 98.62 | 98.39 | 98.52 | 94.85 | 97.18 | 97.84 | 98.14 | 98.21 | 97.99 | 97.96 | 2025-10-01
EPC Power Corp. | 50-200100 {630V} | N | Y | N | N | N | N | N |  | 491 kVA, 630 Vac 3 phase Grid Support Utility Interactive Battery Inverter | 491.262 | 630 | 98.5 | TUV Rheinland of North America | [4/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 0 |  |  | 1034 | 1267 | 1500 | 49.1262 | 98.2524 | 147.3786 | 245.631 | 368.4465 | 491.262 | 98.2091 | 98.8527 | 99.0289 | 99.0368 | 98.8837 | 98.6477 | 98.893 | 97.1329 | 98.1998 | 98.592 | 98.6956 | 98.6498 | 98.413 | 98.5575 | 95.1043 | 97.3394 | 97.9598 | 98.2463 | 98.2754 | 98.0926 | 98.0486 | 2025-10-01
EPC Power Corp. | 50-100A-BCDEF-G {480V} | N | N | Y | Y | Y | Y | N | N | 500 kVA, 480 Vac, 3 phase, 3 wire, Bi-directional Grid Support Utility Interactive Battery Inverter, where A=099, B=61-64 or 81-84, C=A or B or D or Z, D=1-3, E=A or B, F=1 or 3, G=Re or EX or N. | 499.13 | 480 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [03/21/2019] | [042c314] | 2019-05-01 | [03/21/2019] | 2022-01-03 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 20 |  |  | 710 | 950 | 1250 | 49.913 | 99.826 | 149.739 | 249.565 | 374.3475 | 499.13 | 96.5303 | 97.7501 | 98.003 | 98.0553 | 97.9146 | 97.7354 | 97.8822 | 96.0808 | 97.5448 | 97.8618 | 97.9256 | 97.7387 | 97.4688 | 97.7032 | 93.7308 | 95.6096 | 96.015 | 96.1378 | 95.982 | 95.7344 | 95.8976 | 2019-05-01 | 2022-01-03
EPC Power Corp. | 50-100195 {480V} | N | Y | Y | Y | Y | Y | Y* | N | 500 kVA, 480 Vac, 3 phase Bi-directional Grid Support Utility Interactive Battery Inverter | 502.268 | 480 | 97.5 | TUV Rheinland of North America | [6/13/2024] | TUV Rheinland of North America | [07/27/2020] | [fe924e5] | 2021-12-01 | [07/27/2020] | 2021-12-01 | TUV Rheinland | 2022-01-24 | No Information Submitted |  | N | N | 21.08 |  |  | 710 | 980 | 1250 | 50.2268 | 100.4536 | 150.6804 | 251.134 | 376.701 | 502.268 | 96.4879 | 97.9546 | 98.2025 | 98.1965 | 98.0176 | 97.7082 | 97.9975 | 95.3275 | 97.2064 | 97.5783 | 97.6305 | 97.4503 | 97.139 | 97.3908 | 93.9502 | 96.6644 | 97.142 | 97.2884 | 97.1646 | 96.9435 | 97.0232 | 2021-12-01 | 2024-08-01
EPC Power Corp. | 50-200100 {660V} | N | Y | N | N | N | N | N |  | 515 kVA, 660 Vac 3 phase Grid Support Utility Interactive Battery Inverter | 515.0717 | 660 | 98.5 | TUV Rheinland of North America | [4/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 0 |  |  | 1083 | 1291.5 | 1500 | 51.5072 | 103.0143 | 154.5215 | 257.5359 | 386.3038 | 515.0717 | 98.3068 | 98.9166 | 99.0672 | 99.0933 | 98.9255 | 98.6947 | 98.941 | 97.4781 | 98.3688 | 98.7041 | 98.8086 | 98.728 | 98.4955 | 98.6625 | 95.745 | 97.7152 | 98.188 | 98.4336 | 98.4218 | 98.2138 | 98.2434 | 2025-10-01
EPC Power Corp. | 50-200100 {690V} | N | Y | N | N | N | N | N |  | 537 kVA, 690 Vac 3 phase Grid Support Utility Interactive Battery Inverter | 537.035 | 690 | 98.5 | TUV Rheinland of North America | [4/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 0 |  |  | 1127 | 1313.5 | 1500 | 53.703 | 107.407 | 161.11 | 268.517 | 402.776 | 537.035 | 98.31 | 98.9 | 99.08 | 99.09 | 98.93 | 98.72 | 98.95 | 97.58 | 98.44 | 98.76 | 98.85 | 98.77 | 98.54 | 98.71 | 96.23 | 97.86 | 98.3 | 98.53 | 98.51 | 98.31 | 98.35 | 2025-10-01
EPC Power Corp. | 50-200100 {720V} | N | Y | N | N | N | N | N |  | 561 kVA, 720 Vac 3 phase Grid Support Utility Interactive Battery Inverter | 561.806 | 720 | 98.5 | TUV Rheinland of North America | [4/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 0 |  |  | 1181 | 1340 | 1500 | 56.181 | 112.361 | 168.542 | 280.903 | 421.354 | 561.806 | 98.2 | 98.86 | 99.06 | 99.08 | 98.94 | 98.72 | 98.94 | 97.48 | 98.49 | 98.74 | 98.89 | 98.79 | 98.59 | 98.73 | 96.29 | 98.09 | 98.38 | 98.65 | 98.6 | 98.42 | 98.46 | 2025-10-01
EPC Power Corp. | 50-200100 {850V} | N | Y | N | N | N | N | N |  | 663 kVA, 850 Vac 3 phase Grid Support Utility Interactive Battery Inverter | 663.5778 | 850 | 99 | TUV Rheinland of North America | [4/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 0 |  |  | 1388 | 1444 | 1500 | 66.3578 | 132.7156 | 199.0733 | 331.7889 | 497.6833 | 663.5778 | 98.0914 | 98.7705 | 99.024 | 99.0974 | 98.982 | 98.811 | 98.9565 | 97.8919 | 98.6889 | 98.9205 | 99.0182 | 98.9503 | 98.7732 | 98.8967 | 97.651 | 98.5598 | 98.8306 | 98.963 | 98.8729 | 98.7248 | 98.8148 | 2025-10-01
EPC Power Corp. | 50-100100 {480V} | N | Y | Y | Y | Y | Y | Y* | N | 1000 kVA, 480Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 1036.84 | 480 | 97.5 | TUV Rheinland of North America | [6/27/2024] | TUV Rheinland of North America | [07/07/2021];[07/07/2021] | [a501a47];[fe924e5] | 2021-08-02 | [07/07/2021];[07/07/2021] | 2021-08-02 | TUV Rheinland | 2022-01-24 | No Information Submitted |  | N | N | 0 |  |  | 750 | 1000 | 1250 | 103.684 | 207.368 | 311.052 | 518.42 | 777.63 | 1036.84 | 96.6166 | 98.1318 | 98.5074 | 98.6706 | 97.7058 | 95.8714 | 97.8906 | 95.134 | 97.31 | 97.9136 | 98.2396 | 97.1842 | 95.0338 | 97.3101 | 93.4078 | 96.4116 | 97.2556 | 97.7718 | 96.9296 | 95.129 | 96.8888 | 2021-08-02 | 2024-08-01
EPC Power Corp. | 50-100181 {480V} | Y | Y | Y | Y | Y | Y | Y* | N | 1043 kVA, 480Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 1044.2 | 480 | 98 | TUV Rheinland | [3/4/2024] | TUV Rheinland of North America | [04/14/2021] | [fe924e5] | 2022-01-03 | [04/14/2021] | 2022-01-03 | TUV Rheinland | 2022-01-24 | No Information Submitted |  | N | N | 291.17 |  |  | 720 | 1110 | 1500 | 104.42 | 208.84 | 313.26 | 522.1 | 783.15 | 1044.2 | 97.9098 | 98.5852 | 98.6358 | 98.4572 | 98.0884 | 97.6996 | 98.2298 | 97.9854 | 98.6056 | 98.5864 | 98.3194 | 97.897 | 97.4388 | 98.0845 | 95.7674 | 97.4938 | 97.8344 | 97.9364 | 97.6856 | 97.3356 | 97.6523 | 2022-01-03 | 2024-09-03
EPC Power Corp. | 50-100181 {600V} | Y | Y | Y | Y | Y | Y | Y* | N | 1300 kVA, 600Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 1304.151 | 600 | 98.5 | TUV Rheinland | [3/4/2024] | TUV Rheinland of North America | [04/14/2021] | [fe924e5] | 2022-01-03 | [04/14/2021] | 2022-01-03 | TUV Rheinland | 2022-01-24 | No Information Submitted |  | N | N | 248 |  |  | 925 | 1225 | 1500 | 130.4151 | 260.8303 | 391.2454 | 652.0756 | 978.1135 | 1304.1513 | 98.0532 | 98.725 | 98.788 | 98.674 | 98.3996 | 98.0802 | 98.4903 | 97.3176 | 98.4686 | 98.6054 | 98.5492 | 98.2394 | 97.8678 | 98.3044 | 97.389 | 98.2938 | 98.479 | 98.4228 | 98.1552 | 97.8514 | 98.2113 | 2022-01-03 | 2024-09-03
EPC Power Corp. | 50-100100 {690V} | N | Y | Y | Y | Y | Y | Y* | N | 1500 kVA, 690Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 1499.86 | 690 | 98 | TUV Rheinland of North America | [6/27/2024] | TUV Rheinland of North America | [07/07/2021];[07/07/2021] | [a501a47];[fe924e5] | 2021-08-02 | [07/07/2021];[07/07/2021] | 2021-08-02 | TUV Rheinland | 2022-01-24 | No Information Submitted |  | N | N | 0 |  |  | 1050 | 1150 | 1250 | 149.986 | 299.972 | 449.958 | 749.93 | 1124.895 | 1499.86 | 95.8536 | 98.1434 | 98.6344 | 98.8788 | 98.0058 | 96.3586 | 98.103 | 95.7388 | 97.7892 | 98.3848 | 98.733 | 97.9086 | 96.281 | 97.9647 | 95.6382 | 97.6778 | 98.2602 | 98.588 | 97.7562 | 96.1748 | 97.8236 | 2021-08-02 | 2024-08-01
EPC Power Corp. | 50-100181 {690V} | Y | Y | Y | Y | Y | Y | Y* | N | 1500 kVA, 690Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 1504.9 | 690 | 98.5 | TUV Rheinland | [3/4/2024] | TUV Rheinland of North America | [04/14/2021] | [fe924e5] | 2022-01-03 | [04/14/2021] | 2022-01-03 | TUV Rheinland | 2022-01-24 | No Information Submitted |  | N | N | 250.08 |  |  | 1100 | 1330 | 1500 | 150.49 | 300.98 | 451.47 | 752.45 | 1128.675 | 1504.9 | 98.0852 | 98.4231 | 98.6012 | 98.6169 | 98.4248 | 98.1524 | 98.459 | 97.9106 | 98.3437 | 98.5608 | 98.5504 | 98.3682 | 98.0579 | 98.3945 | 97.5318 | 98.1167 | 98.3924 | 98.4846 | 98.3078 | 98.0463 | 98.3014 | 2022-01-03 | 2024-09-03
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {240V} | Y | Y | N | N | N | N | Y* |  | 11.5 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 11.349 | 240 | 96 | TUV Rheinland of North America | [09/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-09-30 |  |  | N | N | 14.23 |  |  | 250 | 375 | 480 | 1.135 | 2.27 | 3.405 | 5.675 | 8.512 | 11.349 | 94.73 | 96.12 | 96.22 | 96.17 | 95.69 | 95.04 | 95.81 | 95.27 | 96.65 | 96.8 | 96.78 | 96.32 | 95.6 | 96.41 | 94.61 | 96.12 | 96.41 | 96.41 | 96.04 | 95.54 | 96.08 | 2025-12-11 | 2026-01-12
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {240V} | Y | Y | N | N | N | N | Y* |  | 11.5 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 11.349 | 240 | 96 | TUV Rheinland of North America | [09/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-09-30 |  |  | N | N | 14.23 |  |  | 250 | 375 | 480 | 1.135 | 2.27 | 3.405 | 5.675 | 8.512 | 11.349 | 94.73 | 96.12 | 96.22 | 96.17 | 95.69 | 95.04 | 95.81 | 95.27 | 96.65 | 96.8 | 96.78 | 96.32 | 95.6 | 96.41 | 94.61 | 96.12 | 96.41 | 96.41 | 96.04 | 95.54 | 96.08 | 2025-12-11 | 2026-01-12
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {208V, 5.0kW} | Y | Y | N | N | N | N | Y* |  | 5.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.0315 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.50315 | 1.0063 | 1.5094 | 2.5158 | 3.7736 | 5.0315 | 90.6481 | 94.2205 | 95.2844 | 95.818 | 95.719 | 95.6238 | 95.4051 | 91.4714 | 94.6072 | 95.6642 | 96.2334 | 96.1263 | 96.1763 | 95.8337 | 91.2682 | 94.5047 | 95.3835 | 95.9362 | 95.9699 | 95.8838 | 95.6268 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {208V, 5.0kW} | Y | Y | N | N | N | N | Y* |  | 5.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.0315 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.50315 | 1.0063 | 1.5094 | 2.5158 | 3.7736 | 5.0315 | 90.6481 | 94.2205 | 95.2844 | 95.818 | 95.719 | 95.6238 | 95.4051 | 91.4714 | 94.6072 | 95.6642 | 96.2334 | 96.1263 | 96.1763 | 95.8337 | 91.2682 | 94.5047 | 95.3835 | 95.9362 | 95.9699 | 95.8838 | 95.6268 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {208V, 5.0kW} | Y | Y | N | N | N | N | Y* |  | 5.0 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.0315 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.50315 | 1.0063 | 1.5094 | 2.5158 | 3.7736 | 5.0315 | 90.6481 | 94.2205 | 95.2844 | 95.818 | 95.719 | 95.6238 | 95.4051 | 91.4714 | 94.6072 | 95.6642 | 96.2334 | 96.1263 | 96.1763 | 95.8337 | 91.2682 | 94.5047 | 95.3835 | 95.9362 | 95.9699 | 95.8838 | 95.6268 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {240V, 5.8kW} | Y | Y | N | N | N | N | Y* |  | 5.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.8122 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.58122 | 1.1624 | 1.7437 | 2.9061 | 4.3591 | 5.8122 | 91.6915 | 94.9083 | 95.8501 | 96.1662 | 96.2831 | 96.1082 | 95.9454 | 92.4874 | 95.3794 | 96.2015 | 96.7833 | 96.8356 | 96.7084 | 96.4954 | 92.0025 | 94.966 | 95.8275 | 96.5099 | 96.4855 | 96.4554 | 96.1548 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {240V, 5.8kW} | Y | Y | N | N | N | N | Y* |  | 5.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.8122 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.58122 | 1.1624 | 1.7437 | 2.9061 | 4.3591 | 5.8122 | 91.6915 | 94.9083 | 95.8501 | 96.1662 | 96.2831 | 96.1082 | 95.9454 | 92.4874 | 95.3794 | 96.2015 | 96.7833 | 96.8356 | 96.7084 | 96.4954 | 92.0025 | 94.966 | 95.8275 | 96.5099 | 96.4855 | 96.4554 | 96.1548 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {240V, 5.8kW} | Y | Y | N | N | N | N | Y* |  | 5.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.8122 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.58122 | 1.1624 | 1.7437 | 2.9061 | 4.3591 | 5.8122 | 91.6915 | 94.9083 | 95.8501 | 96.1662 | 96.2831 | 96.1082 | 95.9454 | 92.4874 | 95.3794 | 96.2015 | 96.7833 | 96.8356 | 96.7084 | 96.4954 | 92.0025 | 94.966 | 95.8275 | 96.5099 | 96.4855 | 96.4554 | 96.1548 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {208V, 6.6kW} | Y | Y | N | N | N | N | Y* |  | 6.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.68 | 208 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.6682 | 1.3364 | 2.0046 | 3.341 | 5.0115 | 6.682 | 92.4875 | 95.2327 | 95.7798 | 95.8418 | 95.7669 | 95.3992 | 95.6079 | 92.8564 | 95.463 | 96.1177 | 96.1376 | 96.3349 | 96.0108 | 96.0685 | 92.4878 | 95.063 | 95.7129 | 96.0218 | 95.909 | 95.7447 | 95.7218 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {208V, 6.6kW} | Y | Y | N | N | N | N | Y* |  | 6.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.68 | 208 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.6682 | 1.3364 | 2.0046 | 3.341 | 5.0115 | 6.682 | 92.4875 | 95.2327 | 95.7798 | 95.8418 | 95.7669 | 95.3992 | 95.6079 | 92.8564 | 95.463 | 96.1177 | 96.1376 | 96.3349 | 96.0108 | 96.0685 | 92.4878 | 95.063 | 95.7129 | 96.0218 | 95.909 | 95.7447 | 95.7218 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {208V, 6.6kW} | Y | Y | N | N | N | N | Y* |  | 6.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.68 | 208 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.6682 | 1.3364 | 2.0046 | 3.341 | 5.0115 | 6.682 | 92.4875 | 95.2327 | 95.7798 | 95.8418 | 95.7669 | 95.3992 | 95.6079 | 92.8564 | 95.463 | 96.1177 | 96.1376 | 96.3349 | 96.0108 | 96.0685 | 92.4878 | 95.063 | 95.7129 | 96.0218 | 95.909 | 95.7447 | 95.7218 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {240V, 7.6kW} | Y | Y | N | N | N | N | Y* |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6 | 240 | 96.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.76013 | 1.5203 | 2.2804 | 3.8007 | 5.701 | 7.6013 | 93.2739 | 95.6475 | 96.2084 | 96.2358 | 96.0886 | 95.7839 | 95.984 | 93.6997 | 95.9983 | 96.6393 | 96.8057 | 96.6768 | 96.4222 | 96.5336 | 93.4787 | 95.6119 | 96.2598 | 96.5683 | 96.4535 | 96.187 | 96.28 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {240V, 7.6kW} | Y | Y | N | N | N | N | Y* |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6 | 240 | 96.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.76013 | 1.5203 | 2.2804 | 3.8007 | 5.701 | 7.6013 | 93.2739 | 95.6475 | 96.2084 | 96.2358 | 96.0886 | 95.7839 | 95.984 | 93.6997 | 95.9983 | 96.6393 | 96.8057 | 96.6768 | 96.4222 | 96.5336 | 93.4787 | 95.6119 | 96.2598 | 96.5683 | 96.4535 | 96.187 | 96.28 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {240V, 7.6kW} | Y | Y | N | N | N | N | Y* |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6 | 240 | 96.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.76013 | 1.5203 | 2.2804 | 3.8007 | 5.701 | 7.6013 | 93.2739 | 95.6475 | 96.2084 | 96.2358 | 96.0886 | 95.7839 | 95.984 | 93.6997 | 95.9983 | 96.6393 | 96.8057 | 96.6768 | 96.4222 | 96.5336 | 93.4787 | 95.6119 | 96.2598 | 96.5683 | 96.4535 | 96.187 | 96.28 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {240V, 9.6kW} | Y | Y | N | N | N | N | Y* |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.63 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.963 | 1.926 | 2.889 | 4.815 | 7.2225 | 9.63 | 94.1685 | 95.9701 | 96.256 | 96.1966 | 95.8452 | 95.4484 | 95.8876 | 94.6628 | 96.3268 | 96.7267 | 96.772 | 96.422 | 95.9912 | 96.4354 | 94.1688 | 95.9942 | 96.4864 | 96.5372 | 96.2844 | 95.7755 | 96.2371 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {240V, 9.6kW} | Y | Y | N | N | N | N | Y* |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.63 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.963 | 1.926 | 2.889 | 4.815 | 7.2225 | 9.63 | 94.1685 | 95.9701 | 96.256 | 96.1966 | 95.8452 | 95.4484 | 95.8876 | 94.6628 | 96.3268 | 96.7267 | 96.772 | 96.422 | 95.9912 | 96.4354 | 94.1688 | 95.9942 | 96.4864 | 96.5372 | 96.2844 | 95.7755 | 96.2371 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {240V, 9.6kW} | Y | Y | N | N | N | N | Y* |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.63 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 20.14 |  |  | 250 | 375 | 480 | 0.963 | 1.926 | 2.889 | 4.815 | 7.2225 | 9.63 | 94.1685 | 95.9701 | 96.256 | 96.1966 | 95.8452 | 95.4484 | 95.8876 | 94.6628 | 96.3268 | 96.7267 | 96.772 | 96.422 | 95.9912 | 96.4354 | 94.1688 | 95.9942 | 96.4864 | 96.5372 | 96.2844 | 95.7755 | 96.2371 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {208V, 9.9kW} | Y | Y | N | N | N | N | Y* |  | 9.9 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.9 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.99008 | 1.9802 | 2.9702 | 4.9504 | 7.4256 | 9.9008 | 94.0773 | 95.7729 | 95.5128 | 95.2461 | 95.2174 | 94.5651 | 95.2084 | 94.6946 | 96.18 | 96.3538 | 96.3192 | 95.6452 | 95.1092 | 95.8337 | 94.0239 | 95.6448 | 95.9748 | 95.8924 | 95.5 | 94.9997 | 95.5626 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G6 {208V, 9.9kW} | Y | Y | N | N | N | N | Y* |  | 9.9 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.9 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.99008 | 1.9802 | 2.9702 | 4.9504 | 7.4256 | 9.9008 | 94.0773 | 95.7729 | 95.5128 | 95.2461 | 95.2174 | 94.5651 | 95.2084 | 94.6946 | 96.18 | 96.3538 | 96.3192 | 95.6452 | 95.1092 | 95.8337 | 94.0239 | 95.6448 | 95.9748 | 95.8924 | 95.5 | 94.9997 | 95.5626 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G7 {208V, 9.9kW} | Y | Y | N | N | N | N | Y* |  | 9.9 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.9 | 208 | 95.5 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 19.77 |  |  | 250 | 360 | 480 | 0.99008 | 1.9802 | 2.9702 | 4.9504 | 7.4256 | 9.9008 | 94.0773 | 95.7729 | 95.5128 | 95.2461 | 95.2174 | 94.5651 | 95.2084 | 94.6946 | 96.18 | 96.3538 | 96.3192 | 95.6452 | 95.1092 | 95.8337 | 94.0239 | 95.6448 | 95.9748 | 95.8924 | 95.5 | 94.9997 | 95.5626 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Eternalplanet Energy Co., Ltd | HNA2-S11G5 {240V, 11.5kW} | Y | Y | N | N | N | N | Y* |  | 11.5 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.3494 | 240 | 96 | TUV Rheinland of North America | [03/17/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-03-03 |  |  | N | N | 14.23 |  |  | 250 | 375 | 480 | 1.1349 | 2.2699 | 3.4048 | 5.6747 | 8.512 | 11.3494 | 94.727 | 96.1155 | 96.2152 | 96.1709 | 95.6922 | 95.0392 | 95.8054 | 95.2658 | 96.6478 | 96.8035 | 96.7768 | 96.3178 | 95.6015 | 96.4111 | 94.6132 | 96.1217 | 96.4059 | 96.407 | 96.0399 | 95.5409 | 96.083 | 2026-07-21 |  | Y | N | N | N | N | N | N | N | N
Expert Computer Int'l Inc. | ExpertPower 10KW Hybrid Inverter {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.0186 | 240 | 95.5 | Intertek | [3/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.8 | 9 | 91.6 | 92.9 | 94.6 | 95.8 | 95.4 | 95.6 | 95.4 | 92.1 | 93.3 | 95 | 96.2 | 96.4 | 96.1 | 95.8 | 89.3 | 92.1 | 93.6 | 95.2 | 96 | 95.7 | 95 | 2026-01-12
Fengfan Co., Ltd. Power Supply Branch | SPT-OMOBFP1-A-6KW {120V} | Y | Y | N | N | N | N | N | N | 6 kW, 120 Vac Split Phase, Transformerless Grid Support Utility Interactive Inverter | 6.0177 | 120 | 93.5 | Intertek | [1/17/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 43 |  |  | 250 | 370 | 500 | 0.60177 | 1.2035 | 1.8053 | 3.0088 | 4.5132 | 6.0177 | 84.5 | 90.4 | 92.4 | 93.9 | 94.5 | 94.4 | 93.5 | 83.8 | 90.3 | 92.5 | 94.1 | 94.9 | 94.9 | 93.7 | 80.8 | 88.9 | 91 | 93.4 | 94.1 | 94.3 | 92.8 | 2024-05-13
Fortress Power LLC | Avalon HV PC50 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.0017 | 240 | 96.5 | CSA Group | [9/8/2023] | CSA Group | [9/8/2023] | [A2] | 2024-08-01 | [9/8/2023] | 2024-08-01 | CSA Group | 2024-01-05 | 2024-08-01 |  | N | N | 18.83 |  |  | 140 | 370 | 450 | 0.50017 | 1.0003 | 1.5005 | 2.5008 | 3.7512 | 5.0017 | 94.2264 | 95.2572 | 96.6079 | 96.5986 | 96.7891 | 96.6855 | 96.5431 | 95.3984 | 95.7768 | 96.5277 | 96.5548 | 96.8363 | 96.978 | 96.6367 | 95.1057 | 95.5303 | 96.4585 | 96.5737 | 96.7108 | 96.7105 | 96.5285 | 2024-08-01
Fortress Power LLC | EdgeOn Duo 7.5 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 5 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 5.02 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 92.68 | 95.266 | 95.93 | 96.35 | 96.16 | 95.992 | 95.98 | 93.568 | 95.856 | 96.53 | 97.03 | 97.08 | 96.97 | 96.7963 | 93.73 | 95.934 | 96.5 | 96.81 | 96.9 | 96.81 | 96.6535 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 7.5 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 5 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 5.04 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.504 | 1.008 | 1.512 | 2.52 | 3.78 | 5.04 | 92.994 | 95.51 | 96.13 | 96.56 | 96.34 | 96.22 | 96.1797 | 93.67 | 95.992 | 96.75 | 97.31 | 97.43 | 97.378 | 97.0983 | 93.79 | 96.142 | 96.614 | 96.98 | 97.24 | 97.24 | 96.9174 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 9 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 6 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 6.1237 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 19.2 |  |  | 200 | 360 | 480 | 0.61237 | 1.2247 | 1.8371 | 3.0618 | 4.5927 | 6.1237 | 91.5057 | 94.3751 | 95.4429 | 96.1451 | 96.2033 | 96.0221 | 95.8115 | 93.6071 | 95.9507 | 96.6981 | 97.1632 | 97.1394 | 97.0155 | 96.8845 | 93.0132 | 95.454 | 96.3177 | 96.9016 | 96.9299 | 96.7629 | 96.6117 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 9 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 6 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 6.1493 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 19.2 |  |  | 200 | 360 | 480 | 0.61493 | 1.2299 | 1.8448 | 3.0747 | 4.612 | 6.1493 | 91.5991 | 94.4496 | 95.4631 | 96.2597 | 96.4111 | 96.355 | 95.9722 | 93.875 | 96.1389 | 96.881 | 97.3815 | 97.4928 | 97.4245 | 97.1802 | 92.6866 | 95.4464 | 96.4097 | 97.0954 | 97.2951 | 97.2686 | 96.8688 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | Avalon HV PC76 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6043 | 240 | 97 | CSA Group | [9/8/2023] | CSA Group | [9/8/2023] | [A2] | 2024-08-01 | [9/8/2023] | 2024-08-01 | CSA Group | 2024-01-05 | 2024-08-01 |  | N | N | 16.33 |  |  | 175 | 380 | 450 | 0.76043 | 1.5209 | 2.2813 | 3.8022 | 5.7032 | 7.6043 | 95.7781 | 96.5695 | 97.1423 | 97.1163 | 97.2718 | 97.3248 | 97.1314 | 95.0243 | 96.1104 | 97.1692 | 97.2619 | 97.2861 | 97.6278 | 97.1348 | 94.7344 | 96.1352 | 96.951 | 97.088 | 97.1471 | 97.3269 | 96.973 | 2024-08-01
Fortress Power LLC | EdgeOn Duo 12 Lite {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 7.6 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 7.6472 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.76472 | 1.5294 | 2.2942 | 3.8236 | 5.7354 | 7.6472 | 92.9526 | 95.5516 | 96.215 | 96.6536 | 96.4528 | 96.189 | 96.2682 | 89.7494 | 96.0782 | 96.7932 | 97.1622 | 96.9742 | 96.771 | 96.648 | 94.0664 | 96.2374 | 96.769 | 97.1184 | 96.9078 | 96.7056 | 96.7781 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 12 Lite {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 7.6 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 7.648 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.736 | 7.648 | 92.946 | 95.544 | 96.21 | 96.648 | 96.448 | 96.186 | 96.2631 | 93.74 | 96.074 | 96.788 | 97.158 | 96.97 | 96.766 | 96.8034 | 94.064 | 96.234 | 96.766 | 97.116 | 96.906 | 96.704 | 96.7759 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-ENVY-8K {208V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 7.8599 | 208 | 96.5 | Intertek | [3/21/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-04-03 |  | N | N | 18.53 |  |  | 210 | 360 | 480 | 0.78599 | 1.572 | 2.358 | 3.93 | 5.895 | 7.8599 | 92.7458 | 94.8821 | 95.7877 | 96.2814 | 95.7548 | 95.5452 | 95.6949 | 95.3183 | 96.7852 | 96.9298 | 97.2401 | 96.7733 | 96.6331 | 96.8255 | 94.866 | 96.387 | 96.7215 | 97.1053 | 96.6941 | 96.6144 | 96.6913 | 2023-04-03 | 2025-05-12
Fortress Power LLC | FP-ENVY-8K {240V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 7.8627 | 240 | 96.5 | Intertek | [3/21/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-04-03 |  | N | N | 18.84 |  |  | 210 | 360 | 480 | 0.78627 | 1.5725 | 2.3588 | 3.9313 | 5.897 | 7.8627 | 92.9578 | 94.8899 | 95.7481 | 96.2838 | 95.9702 | 95.8604 | 95.8294 | 95.5741 | 96.5787 | 96.6854 | 97.0389 | 96.7425 | 96.7486 | 96.7433 | 94.682 | 96.1785 | 96.6318 | 96.9367 | 96.7571 | 96.7998 | 96.67 | 2023-04-03 | 2025-05-12
Fortress Power LLC | EdgeOn Duo 12 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 8.0472 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.80472 | 1.6094 | 2.4142 | 4.0236 | 6.0354 | 8.0472 | 92.9526 | 95.5528 | 96.2152 | 96.6546 | 96.452 | 96.1892 | 96.2681 | 93.7514 | 96.077 | 96.7964 | 97.1666 | 96.974 | 96.7728 | 96.8093 | 94.0688 | 96.2392 | 96.77 | 97.1224 | 96.9124 | 96.6488 | 96.7788 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 12 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 8 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 8.06 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 15 |  |  | 200 | 360 | 480 | 0.806 | 1.612 | 2.418 | 4.03 | 6.045 | 8.06 | 92.852 | 95.4494 | 96.1102 | 96.5538 | 96.3506 | 96.0918 | 96.1665 | 93.649 | 95.9818 | 96.693 | 97.0644 | 96.8732 | 96.6702 | 96.708 | 93.969 | 96.1426 | 96.6718 | 97.023 | 96.8134 | 96.5544 | 96.6802 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-ENVY-10K {208V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 9.7577 | 208 | 96.5 | Intertek | [3/21/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-04-03 |  | N | N | 14.8 |  |  | 210 | 360 | 480 | 0.97577 | 1.9515 | 2.9273 | 4.8789 | 7.3183 | 9.7577 | 92.7092 | 94.8879 | 95.3456 | 95.9721 | 95.5079 | 95.3565 | 95.4354 | 96.1203 | 96.8726 | 97.0518 | 97.3038 | 96.7285 | 96.5437 | 96.8618 | 95.0454 | 96.5267 | 96.8926 | 97.167 | 96.5064 | 96.4285 | 96.6301 | 2023-04-03 | 2025-05-12
Fortress Power LLC | FP-ENVY-10K {240V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 9.7586 | 240 | 96.5 | Intertek | [3/21/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-04-03 |  | N | N | 14.3 |  |  | 210 | 360 | 480 | 0.97586 | 1.9517 | 2.9276 | 4.8793 | 7.3189 | 9.7586 | 93.035 | 95.0464 | 95.7433 | 96.0352 | 95.4309 | 95.34 | 95.4757 | 95.1061 | 96.6509 | 97.0749 | 97.2195 | 96.6243 | 96.5263 | 96.7391 | 94.2113 | 96.1002 | 96.6822 | 96.9911 | 96.5706 | 96.5369 | 96.5527 | 2023-04-03 | 2025-05-12
Fortress Power LLC | Avalon HV PC100 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.0007 | 240 | 97 | CSA Group | [9/8/2023] | CSA Group | [9/8/2023] | [A2] | 2024-08-01 | [9/8/2023] | 2024-08-01 | CSA Group | 2024-01-05 | 2024-08-01 |  | N | N | 16.38 |  |  | 230 | 380 | 450 | 1.0001 | 2.0001 | 3.0002 | 5.0003 | 7.5005 | 10.0007 | 93.5666 | 96.1068 | 97.393 | 97.2724 | 97.3298 | 97.2051 | 97.1074 | 93.5201 | 95.7429 | 97.2657 | 97.3249 | 97.2118 | 97.3903 | 97.0298 | 92.7828 | 95.4556 | 97.3767 | 97.3334 | 97.2796 | 97.6002 | 97.0475 | 2024-08-01
Fortress Power LLC | EdgeOn Duo 15 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 10.1396 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 16.94 |  |  | 200 | 360 | 480 | 1.014 | 2.0279 | 3.0419 | 5.0698 | 7.6047 | 10.1396 | 93.0477 | 95.5809 | 96.2415 | 96.6629 | 96.4516 | 96.2021 | 96.2786 | 93.7158 | 96.0665 | 96.8163 | 97.1487 | 96.9642 | 96.7822 | 96.8013 | 94.0472 | 96.2511 | 96.7916 | 97.1155 | 96.9244 | 96.6588 | 96.7866 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 15 Lite {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 10.1472 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 18 |  |  | 200 | 360 | 480 | 1.0147 | 2.0294 | 3.0442 | 5.0736 | 7.6104 | 10.1472 | 92.9963 | 95.5759 | 96.2237 | 96.6613 | 96.4562 | 96.1983 | 96.2761 | 93.7907 | 96.1027 | 96.8102 | 97.1618 | 96.9743 | 96.7739 | 96.8131 | 94.1119 | 96.2672 | 96.7835 | 97.1258 | 96.9159 | 96.6586 | 96.7866 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 15 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 10.1858 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 16.94 |  |  | 200 | 360 | 480 | 1.0186 | 2.0372 | 3.0557 | 5.0929 | 7.6393 | 10.1858 | 92.9095 | 95.4795 | 96.1203 | 96.5624 | 96.3577 | 96.1012 | 96.1775 | 93.6611 | 96.0245 | 96.7245 | 97.0669 | 96.879 | 96.6799 | 96.7185 | 94.0672 | 96.1747 | 96.6706 | 96.9939 | 96.8177 | 96.5602 | 96.682 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 15 Lite {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 208 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 10.1858 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 18 |  |  | 200 | 360 | 480 | 1.0186 | 2.0372 | 3.0557 | 5.0929 | 7.6393 | 10.1858 | 92.8933 | 95.4787 | 96.1281 | 96.5592 | 96.3579 | 96.0975 | 96.177 | 93.6955 | 96.0051 | 96.7063 | 97.0717 | 96.8789 | 96.675 | 96.7174 | 94.0173 | 96.1625 | 96.6817 | 96.9927 | 96.8158 | 96.5601 | 96.6795 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-ENVY-12K {208V} | Y | Y | N | N | N | N | Y* | Y | 12 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 10.4994 | 208 | 96.5 | Intertek | [3/22/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-03-13 |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.0499 | 2.0999 | 3.1498 | 5.2497 | 7.8745 | 10.4994 | 93.4773 | 95.2677 | 95.9298 | 95.8461 | 95.6083 | 95.2856 | 95.5784 | 95.0713 | 96.6555 | 97.0252 | 97.3102 | 97.0957 | 96.4058 | 96.9948 | 94.2867 | 96.7139 | 97.1633 | 96.953 | 96.7744 | 96.4653 | 96.7406 | 2023-03-13 | 2025-02-11
Fortress Power LLC | Avalon HV PC114 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.406 | 240 | 97 | CSA Group | [9/8/2023] | CSA Group | [9/8/2023] | [A2] | 2024-08-01 | [9/8/2023] | 2024-08-01 | CSA Group | 2024-01-05 | 2024-08-01 |  | N | N | 15.36 |  |  | 245 | 380 | 450 | 1.1406 | 2.2812 | 3.4218 | 5.703 | 8.5545 | 11.406 | 94.7721 | 96.19 | 97.0866 | 97.3773 | 97.2555 | 97.2709 | 97.109 | 95.985 | 96.8789 | 96.8812 | 97.034 | 97.2274 | 97.345 | 97.084 | 95.5491 | 96.6497 | 97.0462 | 97.1786 | 97.2181 | 97.5716 | 97.1117 | 2024-08-01
Fortress Power LLC | EdgeOn Duo 15 Pro {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.4 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 11.5669 | 240 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 19 |  |  | 200 | 360 | 480 | 1.1567 | 2.3134 | 3.4701 | 5.7834 | 8.6752 | 11.5669 | 93.0675 | 95.5749 | 96.2997 | 96.6409 | 96.4392 | 96.2088 | 96.2752 | 93.6781 | 96.0439 | 96.7972 | 97.1353 | 96.9536 | 96.7793 | 96.7878 | 94.0465 | 96.3229 | 96.8228 | 97.1182 | 96.9286 | 96.6545 | 96.7965 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | EdgeOn Duo 15 Pro {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.4 kW, 240 Vac Grid Support Hybrid Utility Interactive with PCS functionality. | 11.6088 | 208 | 96.5 | SGS | [12/8/2025] | SGS | [12/8/2025] | [51001] | 46245 | [12/8/2025] | 46245 | SGS | 45988 |  |  | Y | N | 19 |  |  | 200 | 360 | 480 | 1.1609 | 2.3218 | 3.4827 | 5.8044 | 8.7066 | 11.6088 | 92.8881 | 95.4935 | 96.1138 | 96.5693 | 96.353 | 96.1025 | 96.1756 | 93.6426 | 96.0296 | 96.7159 | 97.0645 | 96.8809 | 96.677 | 96.7174 | 94.0961 | 96.1711 | 96.6734 | 96.9968 | 96.8241 | 96.5565 | 96.6871 | 2026-08-11 |  | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-ENVY-12K {240V} | Y | Y | N | N | N | N | Y* | Y | 12 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 11.9326 | 240 | 97 | Intertek | [3/22/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-02-17 | 2023-03-13 |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.1933 | 2.3865 | 3.5798 | 5.9663 | 8.9494 | 11.9326 | 95.0246 | 96.0981 | 96.5396 | 96.4958 | 96.126 | 95.9005 | 96.1965 | 96.5925 | 97.1942 | 97.5102 | 97.3417 | 97.2365 | 97.1037 | 97.2569 | 95.8173 | 97.0077 | 97.4221 | 97.2641 | 97.1385 | 97.0353 | 97.1344 | 2023-03-13 | 2025-02-11
Fortress Power LLC | FP-Envy 15K {208V} | Y | Y | Y | Y | Y | Y | Y |  | 12.9 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 13.899 | 208 | 96.5 | Intertek | [9/1/2025] | Intertek | [9/1/2025] | [fA1.0] | 2025-11-21 | [8/1/2025] | 2025-11-21 | Intertek | 2025-10-28 |  |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.39 | 2.78 | 4.17 | 6.949 | 10.424 | 13.899 | 95.22 | 96.36 | 96.33 | 96.36 | 96 | 95.99 | 96.1 | 95.54 | 96.57 | 96.97 | 97.17 | 97.07 | 96.25 | 96.95 | 95.6 | 96.83 | 97.38 | 97.17 | 97.09 | 96.97 | 97.06 | 2025-11-21 | 2026-01-12
Fortress Power LLC | FP-Envy Duo 21 {208V} | Y | Y | Y | Y | Y | Y | Y |  | 13.8 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 13.899 | 208 | 96.5 | Intertek | [9/1/2025] | Intertek | [9/1/2025] | [fA1.0] | 2025-11-21 | [8/1/2025] | 2025-11-21 | Intertek | 2025-10-28 |  |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.39 | 2.78 | 4.17 | 6.949 | 10.424 | 13.899 | 95.22 | 96.36 | 96.33 | 96.36 | 96 | 95.99 | 96.1 | 95.54 | 96.57 | 96.97 | 97.17 | 97.07 | 96.25 | 96.95 | 95.6 | 96.83 | 97.38 | 97.17 | 97.09 | 96.97 | 97.06 | 2025-11-21 | 2026-01-12
Fortress Power LLC | FP-Envy 15K {240V} | Y | Y | Y | Y | Y | Y | Y |  | 15 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 16.153 | 240 | 97 | Intertek | [9/1/2025] | Intertek | [9/1/2025] | [fA1.0] | 2025-11-21 | [8/1/2025] | 2025-11-21 | Intertek | 2025-10-28 |  |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.615 | 3.231 | 4.846 | 8.077 | 12.115 | 16.153 | 95.1 | 96 | 96.39 | 96.4 | 96.73 | 95.86 | 96.48 | 96.47 | 97.1 | 97.48 | 97.12 | 97.08 | 96.94 | 97.1 | 95.46 | 96.91 | 97.25 | 97.17 | 96.99 | 96.82 | 96.99 | 2025-11-21 | 2026-01-12
Fortress Power LLC | FP-Envy Duo 21 {240V} | Y | Y | Y | Y | Y | Y | Y |  | 16 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 16.153 | 240 | 97 | Intertek | [9/1/2025] | Intertek | [9/1/2025] | [fA1.0] | 2025-11-21 | [8/1/2025] | 2025-11-21 | Intertek | 2025-10-28 |  |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.615 | 3.231 | 4.846 | 8.077 | 12.115 | 16.153 | 95.1 | 96 | 96.39 | 96.4 | 96.73 | 95.86 | 96.48 | 96.47 | 97.1 | 97.48 | 97.12 | 97.08 | 96.94 | 97.1 | 95.46 | 96.91 | 97.25 | 97.17 | 96.99 | 96.82 | 96.99 | 2025-11-21 | 2026-01-12
Fortress Power LLC | FP-Nano-30k-L {208V} | Y | Y | N | N | N | N | Y |  | 25.883548 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality | 25.8835 | 208 | 97 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 57.3 |  |  | 500 | 675 | 850 | 2.5884 | 5.1767 | 7.7651 | 12.9418 | 19.4127 | 25.8835 | 93.9922 | 95.7952 | 96.926 | 96.8916 | 97.1284 | 97.2124 | 96.8665 | 95.8284 | 95.9332 | 96.6126 | 96.9374 | 97.4868 | 97.2454 | 97.1104 | 89.5538 | 94.454 | 95.935 | 96.8496 | 97.2484 | 97.382 | 96.5662 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-30k-L {220V} | Y | Y | N | N | N | N | Y |  | 27.379 kW, 220 Vac Grid Support Utility Interactive Inverter with PCS functionality | 27.379 | 220 | 97 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 67.5 |  |  | 500 | 675 | 850 | 2.7378 | 5.4756 | 8.2134 | 13.689 | 20.5336 | 27.3781 | 94.062 | 95.658 | 95.876 | 96.926 | 97.104 | 97.23 | 96.7316 | 95.828 | 95.938 | 96.636 | 96.904 | 97.512 | 97.416 | 97.1283 | 89.634 | 95.716 | 96.816 | 97.218 | 97.562 | 97.588 | 96.9921 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-30k-L {240V} | Y | Y | N | N | N | N | Y |  | 29.834174 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality | 29.8342 | 240 | 97 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 70.7 |  |  | 500 | 675 | 850 | 2.9834 | 5.9668 | 8.9503 | 14.9171 | 22.3756 | 29.8342 | 94.1056 | 95.74 | 95.9364 | 96.9676 | 97.0914 | 97.208 | 96.7456 | 95.8062 | 95.9614 | 96.708 | 96.93 | 97.4686 | 97.4116 | 97.1195 | 89.631 | 95.7398 | 96.8554 | 97.2412 | 97.5684 | 97.5508 | 97.0043 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-30k-N {480V} | Y | Y | N | N | N | N | Y |  | 29.884702 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 29.8847 | 480 | 97 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 54.5 |  |  | 500 | 675 | 850 | 2.9885 | 5.9769 | 8.9654 | 14.9424 | 22.4135 | 29.8847 | 94.0686 | 95.8068 | 96.0994 | 97.282 | 97.2044 | 97.2516 | 96.8951 | 95.8456 | 96.0126 | 96.686 | 97.236 | 97.5746 | 97.4406 | 97.2429 | 89.6642 | 95.7374 | 96.8292 | 97.2394 | 97.57 | 97.6 | 97.0053 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-40k-N {480V} | Y | Y | N | N | N | N | Y |  | 39.844002 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 39.844 | 480 | 97 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 70 |  |  | 500 | 675 | 850 | 3.9844 | 7.9688 | 11.9532 | 19.922 | 29.883 | 39.844 | 94.1092 | 95.8522 | 97.0008 | 97.3276 | 97.3346 | 97.4462 | 97.0955 | 96.0928 | 96.5924 | 96.914 | 97.447 | 97.4484 | 97.357 | 97.2824 | 94.472 | 96.3238 | 97.1636 | 97.5694 | 97.6026 | 97.3274 | 97.34 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-50k-N {480V} | Y | Y | N | N | N | N | Y |  | 49.80341867 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 49.8034 | 480 | 97.5 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 76 |  |  | 600 | 725 | 850 | 4.9803 | 9.9607 | 14.941 | 24.9017 | 37.3526 | 49.8034 | 94.4062 | 96.4892 | 97.322 | 97.4496 | 97.3804 | 97.2358 | 97.2172 | 94.4798 | 96.4874 | 97.138 | 97.616 | 97.5676 | 97.5136 | 97.346 | 95.4054 | 96.9518 | 97.2974 | 97.5806 | 97.5812 | 97.4988 | 97.4244 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
Fortress Power LLC | FP-Nano-60k-N {480V} | Y | Y | N | N | N | N | Y |  | 59.763 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 59.763 | 480 | 97.5 | TUV Rheinland of North America | [2/11/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TÜV Rheinland | 2025-12-29 |  |  | Y | N | 76 |  |  | 600 | 725 | 850 | 5.976 | 11.953 | 17.929 | 29.882 | 44.822 | 59.763 | 96.01 | 97.2 | 97.59 | 97.54 | 97.42 | 97.28 | 97.39 | 95.84 | 96.83 | 97.37 | 97.65 | 97.49 | 97.31 | 97.4 | 95.74 | 97.17 | 97.55 | 97.61 | 97.51 | 97.39 | 97.44 | 2026-04-21 | 2026-05-21 | Y | Y | Y | Y | Y | Y | Y | Y | No Information Submitted
FOXESS CO., LTD. | H1-3.8-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 3.713 | 240 | 96 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 204 | 380 | 480 | 0.3713 | 0.74261 | 1.1139 | 1.8565 | 2.7848 | 3.713 | 88.7571 | 93.1319 | 94.7403 | 95.8238 | 96.4154 | 96.5626 | 95.627 | 90.646 | 94.5568 | 95.593 | 96.5203 | 97.3128 | 97.201 | 96.5299 | 87.3378 | 93.647 | 95.4273 | 96.4142 | 97.3282 | 97.4961 | 96.3329 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | AC1-3.8-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 3.738 | 240 | 95.5 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 95 | 360 | 460 | 0.3738 | 0.74759 | 1.1214 | 1.869 | 2.8035 | 3.738 | 86.3322 | 92.1833 | 93.8215 | 95.1152 | 95.6033 | 95.6605 | 94.748 | 87.9782 | 93.5008 | 95.0313 | 96.3382 | 97.0031 | 97.2605 | 96.1036 | 85.2107 | 92.2373 | 94.2958 | 95.8134 | 96.6065 | 96.9214 | 95.5041 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | AIO-AC1-3.8-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 3.7818 | 240 | 95.5 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 85 | 360 | 460 | 0.37818 | 0.75636 | 1.1345 | 1.8909 | 2.8363 | 3.7818 | 86.7152 | 92.3308 | 93.8479 | 95.5213 | 95.6483 | 95.3669 | 94.8683 | 88.0769 | 93.4997 | 94.9969 | 96.4142 | 96.9227 | 97.1481 | 96.0711 | 85.7761 | 92.2863 | 94.3295 | 95.8014 | 96.4647 | 96.7141 | 95.4452 | 2025-07-01
FOXESS CO., LTD. | AIO-H1-3.8-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 3.7972 | 240 | 96 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 204 | 380 | 500 | 0.37972 | 0.75944 | 1.1392 | 1.8986 | 2.8479 | 3.7972 | 89.6627 | 93.2292 | 94.5681 | 95.9692 | 96.4301 | 96.5483 | 95.685 | 91.725 | 94.6987 | 95.7083 | 96.7501 | 96.9842 | 97.1693 | 96.4665 | 88.9624 | 93.5492 | 95.5387 | 97.0122 | 97.3598 | 97.5206 | 96.5499 | 2025-07-01
FOXESS CO., LTD. | AIO-H1-5.7-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.7 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 5.6866 | 240 | 97 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 204 | 380 | 500 | 0.56866 | 1.1373 | 1.706 | 2.8433 | 4.265 | 5.6866 | 90.9696 | 94.7434 | 95.8003 | 96.4201 | 96.6721 | 96.5359 | 96.1832 | 91.1194 | 95.495 | 96.9717 | 97.7104 | 97.7396 | 97.8212 | 97.2684 | 91.0574 | 96.0199 | 96.4362 | 96.7768 | 97.6862 | 97.512 | 96.9881 | 2025-07-01
FOXESS CO., LTD. | AIO-AC1-5.7-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 5.7 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 5.698 | 240 | 96.5 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 122 | 360 | 460 | 0.5698 | 1.1396 | 1.7094 | 2.849 | 4.2735 | 5.698 | 89.5353 | 94.2198 | 95.2248 | 96.1504 | 96.5285 | 96.2615 | 95.8842 | 91.3601 | 95.0587 | 96.1376 | 97.2407 | 97.4013 | 97.3947 | 96.8568 | 89.6198 | 94.431 | 95.5761 | 96.5999 | 96.9559 | 96.905 | 96.2933 | 2025-07-01
FOXESS CO., LTD. | AC1-5.7-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 5.7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 5.7235 | 240 | 96.5 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 140 | 360 | 460 | 0.57235 | 1.1447 | 1.717 | 2.8617 | 4.2926 | 5.7235 | 89.666 | 94.2066 | 95.2859 | 96.1523 | 96.4018 | 96.4323 | 95.8378 | 91.4009 | 95.1478 | 96.1514 | 97.0313 | 97.3459 | 97.4247 | 96.7927 | 89.8821 | 94.4112 | 95.649 | 96.6201 | 97.0644 | 97.199 | 96.388 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | H1-5.7-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 5.7482 | 240 | 97 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 204 | 380 | 480 | 0.57482 | 1.1496 | 1.7245 | 2.8741 | 4.3111 | 5.7482 | 90.8808 | 94.8098 | 95.7632 | 96.4753 | 96.7386 | 96.703 | 96.2337 | 91.5018 | 95.6465 | 97.2168 | 97.6379 | 97.868 | 97.771 | 97.371 | 89.8373 | 95.634 | 96.4644 | 97.2092 | 97.4788 | 97.595 | 96.9084 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | AC1-7.6-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 7.5641 | 240 | 96.5 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 190 | 360 | 460 | 0.75641 | 1.5128 | 2.2692 | 3.7821 | 5.6731 | 7.5641 | 91.3118 | 95.2143 | 96.0739 | 96.6876 | 96.8419 | 96.7797 | 96.4117 | 93.5848 | 95.9114 | 96.6903 | 97.2821 | 97.4247 | 97.3795 | 97.0751 | 91.9271 | 95.2615 | 96.1801 | 96.9515 | 97.1884 | 97.1768 | 96.7103 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | AIO-H1-7.6-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.5857 | 240 | 97.5 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 271 | 380 | 500 | 0.75857 | 1.5171 | 2.2757 | 3.7928 | 5.6893 | 7.5857 | 95.214 | 96.6078 | 97.1112 | 97.4349 | 97.5337 | 97.4987 | 97.3214 | 95.8601 | 97.1947 | 97.6786 | 97.8404 | 97.7797 | 97.7298 | 97.6718 | 95.0767 | 96.615 | 97.41 | 97.5037 | 97.6476 | 97.3909 | 97.4216 | 2025-07-01
FOXESS CO., LTD. | AIO-AC1-7.6-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.5932 | 240 | 97 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 158 | 360 | 460 | 0.75932 | 1.5186 | 2.2779 | 3.7966 | 5.6949 | 7.5932 | 91.4134 | 95.8998 | 96.5732 | 97.0433 | 97.2446 | 97.1324 | 96.8157 | 93.7375 | 96.087 | 96.754 | 97.3608 | 97.4127 | 97.3315 | 97.1054 | 92.0805 | 95.0892 | 95.9891 | 96.9017 | 97.1046 | 97.0666 | 96.6245 | 2025-07-01
FOXESS CO., LTD. | H1-7.6-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 7.7203 | 240 | 97 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 271 | 380 | 480 | 0.77203 | 1.5441 | 2.3161 | 3.8602 | 5.7903 | 7.7203 | 93.4996 | 95.7999 | 96.5407 | 97.0482 | 97.1101 | 96.8974 | 96.8082 | 93.8722 | 96.8306 | 97.0752 | 97.4311 | 97.293 | 97.6679 | 97.1547 | 92.4126 | 96.3152 | 97.0656 | 97.6101 | 97.731 | 97.5149 | 97.3315 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | AC1-9.6-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 9.4186 | 240 | 97 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 235 | 360 | 460 | 0.94186 | 1.8837 | 2.8256 | 4.7093 | 7.064 | 9.4186 | 93.0657 | 96.0025 | 96.609 | 97.0187 | 97.0387 | 96.9068 | 96.7656 | 94.0523 | 96.3742 | 97.006 | 97.3916 | 97.389 | 97.2583 | 97.1529 | 93.1309 | 95.8075 | 96.5767 | 97.1174 | 97.1817 | 97.0369 | 96.8576 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | AIO-H1-9.6-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.5752 | 240 | 97.5 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 257 | 380 | 500 | 0.95752 | 1.915 | 2.8726 | 4.7876 | 7.1814 | 9.5752 | 95.5716 | 96.9652 | 97.2989 | 97.5667 | 97.3513 | 97.0646 | 97.2854 | 96.4655 | 97.5565 | 97.7877 | 97.8147 | 97.7869 | 97.5106 | 97.7147 | 95.5032 | 96.9894 | 97.3765 | 97.569 | 97.4942 | 97.2838 | 97.3804 | 2025-07-01
FOXESS CO., LTD. | AIO-AC1-9.6-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.5849 | 240 | 97 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 200 | 360 | 460 | 0.95849 | 1.917 | 2.8755 | 4.7924 | 7.1886 | 9.5849 | 94.3025 | 96.0314 | 96.7372 | 97.1264 | 97.3227 | 96.9997 | 97.0097 | 94.6333 | 96.5029 | 97.0075 | 97.5172 | 97.4837 | 97.2243 | 97.2575 | 94.3237 | 96.2477 | 96.5266 | 96.9987 | 97.0646 | 97.0981 | 96.8374 | 2025-07-01
FOXESS CO., LTD. | H1-9.6-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 9.6091 | 240 | 97 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 257 | 380 | 480 | 0.96091 | 1.9218 | 2.8827 | 4.8046 | 7.2068 | 9.6091 | 94.0151 | 96.18 | 96.7302 | 97.0459 | 96.9854 | 96.7841 | 96.7983 | 95.6441 | 97.147 | 97.1617 | 97.4712 | 97.3224 | 97.1525 | 97.25 | 94.7056 | 96.5502 | 97.2561 | 97.5742 | 97.6405 | 97.2619 | 97.3896 | 2023-02-13 | 2024-02-12
FOXESS CO., LTD. | AIO-AC1-11.4-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.3393 | 240 | 97 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 257 | 380 | 500 | 1.1339 | 2.2679 | 3.4018 | 5.6696 | 8.5045 | 11.3393 | 94.6817 | 96.7121 | 96.9792 | 97.2808 | 97.0578 | 96.9833 | 96.9792 | 95.1731 | 96.8796 | 97.2222 | 97.5014 | 97.4433 | 96.9206 | 97.2838 | 94.465 | 96.355 | 96.9573 | 97.1896 | 97.0529 | 96.9239 | 96.9253 | 2025-07-01
FOXESS CO., LTD. | AIO-H1-11.4-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.3612 | 240 | 97.5 | CSA Group | [1/17/2025] | CSA Group | [1/17/2025] | [V1.08] | 2025-06-11 | [1/17/2025] | 2025-06-11 | CSA Group | 2024-02-02 | 2025-06-11 |  | N | N | 13.3488 |  |  | 257 | 380 | 500 | 1.1361 | 2.2722 | 3.4084 | 5.6806 | 8.5209 | 11.3612 | 95.4936 | 97.0984 | 97.3469 | 97.5337 | 97.2494 | 96.9259 | 97.2268 | 96.3704 | 97.3767 | 97.7788 | 97.5807 | 97.5045 | 97.4531 | 97.4991 | 95.4259 | 97.3169 | 97.5648 | 97.6753 | 97.5094 | 97.1914 | 97.442 | 2025-07-01
FOXESS CO., LTD. | AC1-11.4-US {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 11.4397 | 240 | 97 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 280 | 360 | 460 | 1.144 | 2.2879 | 3.4319 | 5.7198 | 8.5798 | 11.4397 | 94.7428 | 96.7386 | 97.1288 | 97.3109 | 97.2085 | 97.0299 | 97.0894 | 95.1938 | 96.966 | 97.3493 | 97.506 | 97.4064 | 97.1657 | 97.2979 | 94.4093 | 96.4403 | 96.9949 | 97.2931 | 97.2201 | 96.888 | 97.0404 | 2022-10-21 | 2024-02-12
FOXESS CO., LTD. | H1-11.4-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 11.5119 | 240 | 97.5 | CSA Group | [7/12/2023] | CSA Group | [7/12/2023] | [V1.08, V1.02] | 2023-08-11 | [7/12/2023] | 2023-08-11 | CSA Group | 2023-11-13 | 2023-12-11 |  | N | N | 27.23 |  |  | 305 | 380 | 480 | 1.1512 | 2.3024 | 3.4536 | 5.756 | 8.6339 | 11.5119 | 95.5005 | 96.9797 | 97.2834 | 97.3603 | 97.1804 | 96.9301 | 97.1408 | 96.2352 | 97.384 | 97.7697 | 97.5626 | 97.4234 | 97.4212 | 97.4446 | 95.7811 | 97.2716 | 97.6352 | 97.6967 | 97.6385 | 97.1496 | 97.5332 | 2022-10-21 | 2024-02-12
FOXESS CO., LTD. | H3-70-Plus-US-L {208V} | Y | Y | N | N | N | N | Y* |  | 70 kW, 208 Vac Transformerless Grid Support Utility Interactive Inverter | 69.35 | 208 | 96 | CSA Group | [6/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-06-18 |  |  | N | N | 32.2 |  |  | 240 | 400 | 700 | 6.935 | 13.87 | 20.805 | 34.675 | 52.012 | 69.35 | 94.95 | 96.31 | 96.49 | 96.31 | 95.76 | 94.41 | 95.89 | 95.42 | 96.58 | 96.83 | 96.75 | 96.38 | 95.92 | 96.46 | 93.65 | 95.64 | 96.05 | 96.08 | 95.75 | 95.28 | 95.74 | 2026-09-01 |  | Y | Y | Y | Y | N | Y | Y | N | No Information Submitted
FOXESS CO., LTD. | H3-150-Plus-US-H {480V} | Y | Y | N | N | N | N | Y* |  | 150 kW, 480 Vac Transformerless Grid Support Utility Interactive Inverter | 149.243 | 480 | 97.5 | CSA Group | [6/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-06-18 |  |  | N | N | 26.4 |  |  | 540 | 700 | 850 | 14.924 | 29.849 | 44.773 | 74.621 | 111.932 | 149.243 | 95.84 | 97.1 | 97.46 | 97.61 | 97.38 | 97.14 | 97.35 | 96.26 | 97.54 | 97.86 | 97.96 | 97.8 | 97.25 | 97.74 | 96.63 | 97.84 | 98.11 | 98.18 | 98.07 | 97.32 | 97.99 | 2026-09-01 |  | Y | Y | Y | Y | N | Y | Y | N | No Information Submitted
FranklinWH Energy Storage Inc. | aPower Syyy {240V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.7764 | 240 | 97.5 | CSA Group | [12/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-04-14 | 2025-05-01 |  | N | N | 59.3 |  |  | 250 | 400 | 480 | 0.97764 | 1.9553 | 2.9329 | 4.8882 | 7.3323 | 9.7764 | 94.0563 | 95.7656 | 96.7667 | 97.3048 | 97.3507 | 97.1855 | 97.0517 | 94.9793 | 97.4217 | 97.9049 | 98.0486 | 98.0031 | 97.8209 | 97.8418 | 94.3301 | 96.2484 | 97.1181 | 97.719 | 97.7563 | 97.6438 | 97.4538 | 2025-05-12
FranklinWH Energy Storage Inc. | aPower Syyy {208V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.7851 | 208 | 97.5 | CSA Group | [12/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-04-14 | 2025-05-01 |  | N | N | 58.7 |  |  | 250 | 400 | 480 | 0.97851 | 1.957 | 2.9355 | 4.8925 | 7.3388 | 9.7851 | 93.9597 | 95.7448 | 96.7603 | 97.2398 | 97.2409 | 97.0309 | 96.9665 | 94.9498 | 97.5429 | 98.0023 | 98.105 | 97.9495 | 97.7095 | 97.8362 | 94.1974 | 96.2048 | 97.1199 | 97.544 | 97.6082 | 97.4664 | 97.3224 | 2025-05-12
FranklinWH Energy Storage Inc. | aPower Syyy {208V, 10kW} | Y | Y | N | N | N | N | Y* |  | 10 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.016 | 208 | 95.5 | CSA Group | [4/22/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 45761 |  |  | N | N | 64.1 |  |  | 49.4 | 51.2 | 54.4 | 1.002 | 2.003 | 3.005 | 5.008 | 7.512 | 10.016 | 93.23 | 95.74 | 96.3 | 96.27 | 95.44 | 94.26 | 95.58 | 93.13 | 95.66 | 96.28 | 96.34 | 95.51 | 94.48 | 95.64 | 92.86 | 95.5 | 96.23 | 96.43 | 95.74 | 94.77 | 95.77 | 2026-08-11 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
FranklinWH Energy Storage Inc. | aPower Syyy {240V, 10kW} | Y | Y | N | N | N | N | Y* |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.076 | 240 | 96 | CSA Group | [4/22/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 45761 |  |  | N | N | 58 |  |  | 49.4 | 51.2 | 54.4 | 1.008 | 2.015 | 3.023 | 5.038 | 7.557 | 10.076 | 93.38 | 95.86 | 96.41 | 96.34 | 95.61 | 94.56 | 95.73 | 93.18 | 95.81 | 96.43 | 96.39 | 95.64 | 94.6 | 95.75 | 93.01 | 95.69 | 96.4 | 96.47 | 95.81 | 94.91 | 95.86 | 2026-08-11 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
FranklinWH Energy Storage Inc. | aPower Syyy {240V, 11.5kW} | Y | Y | N | N | N | N | Y* |  | 11 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.554 | 240 | 97.5 | CSA Group | [4/22/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 45761 |  |  | N | N | 32 |  |  | 250 | 400 | 480 | 1.155 | 2.311 | 3.466 | 5.777 | 8.666 | 11.554 | 94.75 | 95.98 | 96.79 | 97.2 | 97.05 | 96.81 | 96.89 | 94.82 | 96.47 | 97.5 | 97.96 | 97.86 | 97.6 | 97.63 | 93.46 | 95.73 | 96.81 | 97.68 | 97.57 | 97.4 | 97.24 | 2026-08-11 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
FranklinWH Energy Storage Inc. | aPower Syyy {208V, 11.5kW} | Y | Y | N | N | N | N | Y* |  | 11 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.577 | 208 | 97 | CSA Group | [4/22/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 45761 |  |  | N | N | 68 |  |  | 250 | 400 | 480 | 1.158 | 2.315 | 3.473 | 5.788 | 8.683 | 11.577 | 93.72 | 95.86 | 96.71 | 97.08 | 96.97 | 96.59 | 96.76 | 94.34 | 96.26 | 97.45 | 97.77 | 97.66 | 97.41 | 97.44 | 93.4 | 95.31 | 96.83 | 97.38 | 97.41 | 97.19 | 97.06 | 2026-08-11 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
Fronius International GmbH | Primo GEN24 3.8 208-240 Plus SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.8 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 3.7999 | 240 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.63 |  |  | 190 | 385 | 480 | 0.38 | 0.75999 | 1.14 | 1.9 | 2.85 | 3.7999 | 91.0973 | 94.7379 | 95.9993 | 96.4629 | 96.7029 | 96.7741 | 96.2491 | 92.6834 | 95.9716 | 96.7951 | 97.4158 | 97.5866 | 97.6284 | 97.181 | 90.9224 | 95.0813 | 96.174 | 97.0187 | 97.2843 | 97.3607 | 96.7345 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 3.8 208-240 SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.8 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 3.7999 | 240 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.63 |  |  | 190 | 385 | 480 | 0.38 | 0.75999 | 1.14 | 1.9 | 2.85 | 3.7999 | 91.0973 | 94.7379 | 95.9993 | 96.4629 | 96.7029 | 96.7741 | 96.2491 | 92.6834 | 95.9716 | 96.7951 | 97.4158 | 97.5866 | 97.6284 | 97.181 | 90.9224 | 95.0813 | 96.174 | 97.0187 | 97.2843 | 97.3607 | 96.7345 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 3.8 208-240 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 3.802 | 240 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.3 |  |  | 200 | 400 | 480 | 0.38018 | 0.76036 | 1.1405 | 1.9009 | 2.8514 | 3.8018 | 89.0285 | 93.9929 | 95.2684 | 96.142 | 96.561 | 96.6724 | 95.8938 | 93.396 | 96.2696 | 97.0028 | 97.4707 | 97.6461 | 97.6553 | 97.2937 | 91.8008 | 95.685 | 96.5943 | 97.2177 | 97.4303 | 97.467 | 96.9747 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 3.8 208-240 Plus {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 3.802 | 240 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.3 |  |  | 200 | 400 | 480 | 0.38018 | 0.76036 | 1.1405 | 1.9009 | 2.8514 | 3.8018 | 89.0285 | 93.9929 | 95.2684 | 96.142 | 96.561 | 96.6724 | 95.8938 | 93.396 | 96.2696 | 97.0028 | 97.4707 | 97.6461 | 97.6553 | 97.2937 | 91.8008 | 95.685 | 96.5943 | 97.2177 | 97.4303 | 97.467 | 96.9747 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 3.8 208-240 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 3.805 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.4 |  |  | 200 | 360 | 480 | 0.381 | 0.761 | 1.142 | 1.903 | 2.854 | 3.805 | 90.04 | 94.42 | 95.58 | 96.37 | 96.51 | 96.51 | 96.01 | 93.84 | 96.3 | 96.91 | 97.34 | 97.41 | 97.37 | 97.14 | 91.74 | 95.59 | 96.36 | 96.93 | 97.1 | 97.08 | 96.68 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 3.8 208-240 Plus {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 3.805 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.4 |  |  | 200 | 360 | 480 | 0.381 | 0.761 | 1.142 | 1.903 | 2.854 | 3.805 | 90.04 | 94.42 | 95.58 | 96.37 | 96.51 | 96.51 | 96.01 | 93.84 | 96.3 | 96.91 | 97.34 | 97.41 | 97.37 | 97.14 | 91.74 | 95.59 | 96.36 | 96.93 | 97.1 | 97.08 | 96.68 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 3.8 208-240 Plus SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.8 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 3.8147 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.74 |  |  | 190 | 365 | 480 | 0.38147 | 0.76293 | 1.1444 | 1.9073 | 2.861 | 3.8147 | 90.972 | 94.5295 | 95.784 | 96.188 | 96.388 | 96.4566 | 95.9674 | 92.9078 | 95.953 | 96.6908 | 97.2113 | 97.3462 | 97.3313 | 96.9913 | 90.9984 | 94.9841 | 96.0279 | 96.7766 | 96.9891 | 97.005 | 96.4901 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 3.8 208-240 SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.8 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 3.8147 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.74 |  |  | 190 | 365 | 480 | 0.38147 | 0.76293 | 1.1444 | 1.9073 | 2.861 | 3.8147 | 90.972 | 94.5295 | 95.784 | 96.188 | 96.388 | 96.4566 | 95.9674 | 92.9078 | 95.953 | 96.6908 | 97.2113 | 97.3462 | 97.3313 | 96.9913 | 90.9984 | 94.9841 | 96.0279 | 96.7766 | 96.9891 | 97.005 | 96.4901 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 5.0 208-240 Plus SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.0 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.0002 | 240 | 97 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.62 |  |  | 190 | 385 | 480 | 0.50002 | 1 | 1.5 | 2.5001 | 3.7501 | 5.0002 | 93.5288 | 95.5677 | 96.175 | 96.6246 | 96.7651 | 96.7308 | 96.4738 | 94.159 | 96.6219 | 97.2055 | 97.5096 | 97.624 | 97.6078 | 97.3602 | 92.7932 | 95.9577 | 96.7372 | 97.2239 | 97.3573 | 97.3834 | 97.0037 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 5.0 208-240 SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.0 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.0002 | 240 | 97 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.62 |  |  | 190 | 385 | 480 | 0.50002 | 1 | 1.5 | 2.5001 | 3.7501 | 5.0002 | 93.5288 | 95.5677 | 96.175 | 96.6246 | 96.7651 | 96.7308 | 96.4738 | 94.159 | 96.6219 | 97.2055 | 97.5096 | 97.624 | 97.6078 | 97.3602 | 92.7932 | 95.9577 | 96.7372 | 97.2239 | 97.3573 | 97.3834 | 97.0037 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 5.0 208-240 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.006 | 208 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.2 |  |  | 230 | 360 | 480 | 0.50064 | 1.0013 | 1.5019 | 2.5032 | 3.7548 | 5.0064 | 92.1068 | 95.559 | 96.333 | 96.7491 | 96.7615 | 96.6907 | 96.4576 | 94.9627 | 96.8248 | 97.2401 | 97.4415 | 97.3926 | 97.3272 | 97.2557 | 93.458 | 96.166 | 96.7617 | 97.1167 | 97.1328 | 96.9747 | 96.8816 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 5.0 208-240 Plus {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.006 | 208 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.2 |  |  | 230 | 360 | 480 | 0.50064 | 1.0013 | 1.5019 | 2.5032 | 3.7548 | 5.0064 | 92.1068 | 95.559 | 96.333 | 96.7491 | 96.7615 | 96.6907 | 96.4576 | 94.9627 | 96.8248 | 97.2401 | 97.4415 | 97.3926 | 97.3272 | 97.2557 | 93.458 | 96.166 | 96.7617 | 97.1167 | 97.1328 | 96.9747 | 96.8816 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 5.0 208-240 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.007 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.3 |  |  | 230 | 400 | 480 | 0.50072 | 1.0014 | 1.5022 | 2.5036 | 3.7554 | 5.0072 | 91.4981 | 95.117 | 95.9981 | 96.4863 | 96.8457 | 96.8711 | 96.3695 | 94.7183 | 96.7822 | 97.2832 | 97.6405 | 97.635 | 97.5893 | 97.4323 | 93.5556 | 96.3003 | 96.9674 | 97.3974 | 97.4608 | 97.4163 | 97.1718 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 5.0 208-240 Plus {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.007 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.3 |  |  | 230 | 400 | 480 | 0.50072 | 1.0014 | 1.5022 | 2.5036 | 3.7554 | 5.0072 | 91.4981 | 95.117 | 95.9981 | 96.4863 | 96.8457 | 96.8711 | 96.3695 | 94.7183 | 96.7822 | 97.2832 | 97.6405 | 97.635 | 97.5893 | 97.4323 | 93.5556 | 96.3003 | 96.9674 | 97.3974 | 97.4608 | 97.4163 | 97.1718 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 5.0 208-240 Plus SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.0 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.0224 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.6 |  |  | 190 | 365 | 480 | 0.50224 | 1.0045 | 1.5067 | 2.5112 | 3.7668 | 5.0224 | 93.399 | 95.8084 | 95.8707 | 96.3153 | 96.4507 | 96.3548 | 96.1937 | 94.2612 | 96.5214 | 97.0429 | 97.316 | 97.2855 | 97.2571 | 97.1022 | 92.8231 | 95.8202 | 96.5218 | 96.8849 | 97.0206 | 96.9716 | 96.7019 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 5.0 208-240 SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.0 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.0224 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.6 |  |  | 190 | 365 | 480 | 0.50224 | 1.0045 | 1.5067 | 2.5112 | 3.7668 | 5.0224 | 93.399 | 95.8084 | 95.8707 | 96.3153 | 96.4507 | 96.3548 | 96.1937 | 94.2612 | 96.5214 | 97.0429 | 97.316 | 97.2855 | 97.2571 | 97.1022 | 92.8231 | 95.8202 | 96.5218 | 96.8849 | 97.0206 | 96.9716 | 96.7019 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 6.0 208-240 Plus SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.0 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.7316 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.53 |  |  | 190 | 365 | 480 | 0.57316 | 1.1463 | 1.7195 | 2.8658 | 4.2987 | 5.7316 | 93.2421 | 95.7581 | 96.0497 | 96.3978 | 96.4338 | 96.2511 | 96.2095 | 94.7764 | 96.713 | 97.141 | 97.3368 | 97.3123 | 97.176 | 97.1587 | 93.4162 | 96.0496 | 96.6594 | 96.9506 | 97.0021 | 96.8982 | 96.7539 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 6.0 208-240 SC {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.0 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 5.7316 | 208 | 96.5 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.53 |  |  | 190 | 365 | 480 | 0.57316 | 1.1463 | 1.7195 | 2.8658 | 4.2987 | 5.7316 | 93.2421 | 95.7581 | 96.0497 | 96.3978 | 96.4338 | 96.2511 | 96.2095 | 94.7764 | 96.713 | 97.141 | 97.3368 | 97.3123 | 97.176 | 97.1587 | 93.4162 | 96.0496 | 96.6594 | 96.9506 | 97.0021 | 96.8982 | 96.7539 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 6.0 208-240 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.743 | 208 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.4 |  |  | 230 | 360 | 480 | 0.5743 | 1.1486 | 1.7229 | 2.8715 | 4.3072 | 5.743 | 93.0718 | 95.8262 | 96.3687 | 96.6826 | 96.6192 | 96.475 | 96.4137 | 95.3477 | 96.9249 | 97.2393 | 97.3708 | 97.3163 | 97.133 | 97.211 | 94.177 | 96.3803 | 96.8316 | 97.0907 | 97.0319 | 96.7863 | 96.8611 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 6.0 208-240 Plus {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 5.743 | 208 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.4 |  |  | 230 | 360 | 480 | 0.5743 | 1.1486 | 1.7229 | 2.8715 | 4.3072 | 5.743 | 93.0718 | 95.8262 | 96.3687 | 96.6826 | 96.6192 | 96.475 | 96.4137 | 95.3477 | 96.9249 | 97.2393 | 97.3708 | 97.3163 | 97.133 | 97.211 | 94.177 | 96.3803 | 96.8316 | 97.0907 | 97.0319 | 96.7863 | 96.8611 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 6.0 208-240 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 6.004 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted | Requires purchasing of a software package for utilization in energy storage application. | Y | N | 8.3 |  |  | 230 | 400 | 480 | 0.60044 | 1.2009 | 1.8013 | 3.0022 | 4.5033 | 6.0044 | 92.6588 | 95.6182 | 96.2204 | 96.7281 | 96.8629 | 96.79 | 96.5234 | 95.3651 | 97.0418 | 97.4249 | 97.6296 | 97.6221 | 97.5002 | 97.4746 | 94.4545 | 96.64 | 97.127 | 97.4435 | 97.436 | 97.2966 | 97.2344 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 6.0 208-240 Plus {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 6.004 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [05/25/2020]; [6/27/2024] | [ZEUS V2.10.2, KRONOS V2.16.2]; [ZEUS V2.28.5, KRONOS V2.36.6] | 2021-11-12 | [6/27/2024] | 2025-01-02 | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.3 |  |  | 230 | 400 | 480 | 0.60044 | 1.2009 | 1.8013 | 3.0022 | 4.5033 | 6.0044 | 92.6588 | 95.6182 | 96.2204 | 96.7281 | 96.8629 | 96.79 | 96.5234 | 95.3651 | 97.0418 | 97.4249 | 97.6296 | 97.6221 | 97.5002 | 97.4746 | 94.4545 | 96.64 | 97.127 | 97.4435 | 97.436 | 97.2966 | 97.2344 | 2021-11-12 | 2025-05-01
Fronius International GmbH | Primo GEN24 6.0 208-240 Plus SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.0 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 6.0047 | 240 | 97 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.53 |  |  | 190 | 385 | 480 | 0.60047 | 1.2009 | 1.8014 | 3.0023 | 4.5035 | 6.0047 | 93.4643 | 96.0718 | 96.3559 | 96.7017 | 96.7527 | 96.5931 | 96.5208 | 94.8709 | 96.8847 | 97.3598 | 97.6019 | 97.6102 | 97.5386 | 97.429 | 93.6473 | 96.3114 | 96.955 | 97.3069 | 97.3654 | 97.321 | 97.1002 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 6.0 208-240 SC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.0 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. | 6.0047 | 240 | 97 | CSA Group | [8/5/2026] | CSA Group | [8/5/2026] | [ZEUS V03.05.06, KRONOS V03.06.04] | 2026-10-12 | [8/5/2026] | 2026-10-12 | CSA Group | 2026-07-21 |  |  | Y | N | 7.53 |  |  | 190 | 385 | 480 | 0.60047 | 1.2009 | 1.8014 | 3.0023 | 4.5035 | 6.0047 | 93.4643 | 96.0718 | 96.3559 | 96.7017 | 96.7527 | 96.5931 | 96.5208 | 94.8709 | 96.8847 | 97.3598 | 97.6019 | 97.6102 | 97.5386 | 97.429 | 93.6473 | 96.3114 | 96.955 | 97.3069 | 97.3654 | 97.321 | 97.1002 | 2026-10-12 |  | Y | N | Y | N | N | N | N | N | Y
Fronius International GmbH | Primo GEN24 7.7 208-240 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.7 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 7.686 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 9.2 |  |  | 260 | 385 | 480 | 0.769 | 1.537 | 2.306 | 3.843 | 5.765 | 7.686 | 94.05 | 96.37 | 96.88 | 97.11 | 97.04 | 96.88 | 96.87 | 94.83 | 96.86 | 97.22 | 97.48 | 97.44 | 97.32 | 97.28 | 93.09 | 96.01 | 96.73 | 97.08 | 97.11 | 97.06 | 96.84 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 7.7 208-240 Plus {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.7 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 7.686 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 9.2 |  |  | 260 | 385 | 480 | 0.769 | 1.537 | 2.306 | 3.843 | 5.765 | 7.686 | 94.05 | 96.37 | 96.88 | 97.11 | 97.04 | 96.88 | 96.87 | 94.83 | 96.86 | 97.22 | 97.48 | 97.44 | 97.32 | 97.28 | 93.09 | 96.01 | 96.73 | 97.08 | 97.11 | 97.06 | 96.84 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 7.7 208-240 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.7 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 7.689 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 9.2 |  |  | 260 | 365 | 480 | 0.769 | 1.538 | 2.307 | 3.845 | 5.767 | 7.689 | 93.81 | 96.07 | 96.53 | 96.72 | 96.67 | 96.46 | 96.51 | 94.89 | 96.66 | 97.09 | 97.14 | 97.09 | 96.88 | 96.98 | 92.99 | 95.77 | 96.38 | 96.7 | 96.7 | 96.57 | 96.46 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 7.7 208-240 Plus {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.7 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 7.689 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 9.2 |  |  | 260 | 365 | 480 | 0.769 | 1.538 | 2.307 | 3.845 | 5.767 | 7.689 | 93.81 | 96.07 | 96.53 | 96.72 | 96.67 | 96.46 | 96.51 | 94.89 | 96.66 | 97.09 | 97.14 | 97.09 | 96.88 | 96.98 | 92.99 | 95.77 | 96.38 | 96.7 | 96.7 | 96.57 | 96.46 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 10.0 208-240 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.0 kW, 208 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 9.454 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.4 |  |  | 260 | 365 | 480 | 0.945 | 1.891 | 2.836 | 4.727 | 7.091 | 9.454 | 94.64 | 96.41 | 96.65 | 96.71 | 96.56 | 96.19 | 96.5 | 95.55 | 96.97 | 97.15 | 97.16 | 96.98 | 96.68 | 96.97 | 93.99 | 96.24 | 96.6 | 96.73 | 96.61 | 96.37 | 96.5 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 10.0 208-240 Plus {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.0 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 9.454 | 208 | 96.5 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.4 |  |  | 260 | 365 | 480 | 0.945 | 1.891 | 2.836 | 4.727 | 7.091 | 9.454 | 94.64 | 96.41 | 96.65 | 96.71 | 96.56 | 96.19 | 96.5 | 95.55 | 96.97 | 97.15 | 97.16 | 96.98 | 96.68 | 96.97 | 93.99 | 96.24 | 96.6 | 96.73 | 96.61 | 96.37 | 96.5 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 10.0 208-240 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.0 kW, 240 Vac Grid Support Utility Interactive PV and Battery (requires purchasing of a software package) Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 10.019 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.5 |  |  | 260 | 385 | 480 | 1.002 | 2.004 | 3.006 | 5.009 | 7.514 | 10.019 | 95.2 | 96.68 | 96.99 | 97.03 | 96.91 | 96.62 | 96.85 | 95.79 | 97.19 | 97.38 | 97.45 | 97.37 | 97.13 | 97.3 | 94.38 | 96.58 | 96.93 | 97.11 | 97.08 | 96.87 | 96.93 | 2024-09-03 | 2025-05-01
Fronius International GmbH | Primo GEN24 10.0 208-240 Plus {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.0 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with arc detector, PLC transmitter, and meter. Inverter with PCS functionality. | 10.019 | 240 | 97 | CSA Group | [4/9/2025] | CSA Group | [6/27/2024] | [ZEUS V2.28.5, KRONOS V2.36.6] | 2024-09-03 | [6/27/2024] | No Information Submitted | CSA Group | 2024-06-03 | No Information Submitted |  | Y | N | 8.5 |  |  | 260 | 385 | 480 | 1.002 | 2.004 | 3.006 | 5.009 | 7.514 | 10.019 | 95.2 | 96.68 | 96.99 | 97.03 | 96.91 | 96.62 | 96.85 | 95.79 | 97.19 | 97.38 | 97.45 | 97.37 | 97.13 | 97.3 | 94.38 | 96.58 | 96.93 | 97.11 | 97.08 | 96.87 | 96.93 | 2024-09-03 | 2025-05-01
GE Renewable Energy | RIU-2500-U {550V} | Y | N | Y | Y | Y | N | N | N | 2500 kVA, 550 Vac, Bi-directional, Grid Support Utility Interactive Hybrid Inverter | 2507.194 | 550 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [11/01/2019] | [DSP_RIU-2500-U_V11_V1_A, LCD_RIU-2500-U_V1_A] | 2020-03-23 | [11/01/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 2500 kVA Medium-Voltage Dry-Type Distribution Transformers Table in DOE216. | N | N | 62.8 |  |  | 800 | 975 | 1500 | 250.7194 | 501.4388 | 752.1582 | 1253.597 | 1880.3955 | 2507.194 | 96.1656 | 97.496 | 97.8461 | 97.9177 | 97.6547 | 97.324 | 97.6489 | 96.0246 | 97.2391 | 97.7308 | 97.8521 | 97.5444 | 97.19 | 97.5376 | 95.4326 | 96.8219 | 97.3458 | 97.4664 | 97.1968 | 96.9426 | 97.1693 | 2020-03-23 | 2021-03-01
Generac Power Systems, Inc. | X7602 {240V} | Y | N | Y | Y | Y | Y | Y | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS Functionality | 7.586 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [10/09/2020] | [13430];[13590] | 2020-02-03 | [10/09/2020] | 2020-03-23 | SunSpec Alliance | 2019-11-26 | 2020-02-03 | Model number formerly listed as Pika Energy | N | N | 1.2917 |  |  | 390 | 400 | 420 | 0.759 | 1.517 | 2.276 | 3.793 | 5.689 | 7.586 | 91.67 | 95.89 | 96.62 | 97.26 | 97.24 | 97.04 | 96.87 | 91.01 | 95.4 | 96.52 | 97.26 | 97.15 | 97.01 | 96.75 | 90.48 | 95.21 | 96.33 | 96.86 | 97.02 | 96.91 | 96.55 | 2020-02-03 | 2021-04-01
Generac Power Systems, Inc. | XVT076A03 {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS Functionality | 7.606 | 240 | 96.5 | Intertek | [6/30/2023] | Intertek | [10/09/2020] | [13430];[13590] | 2020-10-01 | [10/09/2020] | 2020-10-01 | SunSpec Alliance | 2023-06-13 | 2020-10-01 |  | N | N | 41.9 |  |  | 390 | 400 | 420 | 0.76057 | 1.5211 | 2.2817 | 3.8028 | 5.7042 | 7.6057 | 93.8895 | 96.2047 | 96.7309 | 96.8111 | 96.547 | 96.1964 | 96.4836 | 93.6733 | 96.1311 | 96.6969 | 96.8149 | 96.6123 | 96.2609 | 96.5058 | 93.0587 | 95.8723 | 96.494 | 96.6834 | 96.4511 | 96.1331 | 96.3245 | 2020-10-01 | 2023-08-11
Generac Power Systems, Inc. | X11402 {208V} | Y | N | Y | Y | Y | Y | Y | Y | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS Functionality | 11.18 | 208 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [10/09/2020] | [13430];[13590] | 2020-02-03 | [10/09/2020] | 2020-03-23 | SunSpec Alliance | 2019-11-26 | 2020-02-03 | Model number formerly listed as Pika Energy | N | N | 0.125 |  |  | 390 | 400 | 420 | 1.118 | 2.236 | 3.354 | 5.59 | 8.385 | 11.18 | 97.25 | 97.35 | 97.58 | 97.65 | 97.44 | 97.06 | 97.47 | 97.03 | 97.35 | 97.67 | 97.54 | 97.25 | 96.93 | 97.34 | 95.83 | 97.24 | 97.27 | 97.39 | 97.08 | 96.89 | 97.12 | 2020-02-03 | 2021-04-01
Generac Power Systems, Inc. | APKE00075 {240V} | N | Y | N | N | N | N | Y* | N | 11.5 kW, 240 Vac, 1-phase Grid Support Utility Interactive Battery Inverter with PCS functionality. | 11.4728 | 240 | 98.5 | TUV Rheinland of North America | [4/7/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2024-10-24 | No Information Submitted |  | N | N | 77.44 |  |  | 360 | 400 | 420 | 1.1473 | 2.2946 | 3.4418 | 5.7364 | 8.6046 | 11.4728 | 97.7085 | 98.4392 | 98.583 | 98.5419 | 98.2897 | 97.9564 | 98.3454 | 97.3841 | 98.2363 | 98.4481 | 98.4446 | 98.2172 | 97.8925 | 98.244 | 97.2191 | 98.1317 | 98.3686 | 98.421 | 98.2179 | 97.9373 | 98.2203 | 2025-07-11
Generac Power Systems, Inc. | XVT114G03 {208V} | Y | N | Y | Y | Y | Y | Y | Y | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS Functionality | 11.748 | 208 | 97 | No Information Submitted | No Information Submitted | Intertek | [10/09/2020] | [13430];[13590] | 2020-10-01 | [10/09/2020] | 2020-10-01 | SunSpec Alliance | 2019-11-26 | 2020-10-01 |  | N | N | 0.13 |  |  | 390 | 400 | 420 | 1.1748 | 2.3496 | 3.5243 | 5.8739 | 8.8109 | 11.7478 | 94.3952 | 96.3614 | 96.9844 | 97.3488 | 97.3913 | 97.3223 | 97.1588 | 93.8375 | 96.116 | 96.8135 | 97.3003 | 97.2556 | 97.1149 | 97.0112 | 92.9035 | 95.7659 | 96.54 | 97.0771 | 97.168 | 97.0658 | 96.8278 | 2020-10-01 | 2021-04-01
General Motors Energy LLC | GM Energy Inverter e1.11 {208V} | Y | Y | N | N | N | N | Y* | Y | 11.520 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.0568 | 208 | 97 | CSA Group | [5/15/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-28 | 2024-08-21 |  | N | N | 16.23 |  |  | 200 | 380 | 480 | 1.0057 | 2.0114 | 3.017 | 5.0284 | 7.5426 | 10.0568 | 94.5201 | 96.389 | 96.8997 | 96.9415 | 96.5333 | 95.9709 | 96.5472 | 95.9899 | 97.4283 | 97.7143 | 97.6655 | 97.2997 | 96.965 | 97.3636 | 95.4895 | 97.1344 | 97.5396 | 97.6477 | 97.4208 | 96.8726 | 97.3637 | 2024-08-21
General Motors Energy LLC | GM Energy Inverter e1.11 {240V} | Y | Y | N | N | N | N | Y* | Y | 11.520 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.5886 | 240 | 97.5 | CSA Group | [5/15/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-28 | 2024-08-21 |  | N | N | 16.48 |  |  | 200 | 380 | 480 | 1.1589 | 2.3177 | 3.4766 | 5.7943 | 8.6914 | 11.5886 | 94.7826 | 96.6129 | 97.0546 | 97.1271 | 96.6484 | 96.0211 | 96.6899 | 96.5172 | 97.7857 | 97.9547 | 97.9185 | 97.5962 | 97.3165 | 97.6593 | 96.0248 | 97.4984 | 97.8115 | 97.8312 | 97.6456 | 97.2776 | 97.6139 | 2024-08-21
Geneverse Energy Inc. | GVI-HS-5K-USM {240V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac, Grid Support Utility Interactive Inverter | 5.0897 | 240 | 97 | SGS | [6/2/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-07-03 | 2023-09-01 |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2023-09-01
Geneverse Energy Inc. | GVI-HS-6K-USM {240V} | Y | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac, Grid Support Utility Interactive Inverter | 6.1172 | 240 | 97 | SGS | [6/2/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-07-03 | 2023-09-01 |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2023-09-01
Geneverse Energy Inc. | GVI-HS-7K6-USM {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Grid Support Utility Interactive Inverter | 7.7647 | 240 | 97 | SGS | [6/2/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-07-03 | 2023-09-01 |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2023-09-01
Geneverse Energy Inc. | GVI-HS-8K-USM {240V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 240 Vac, Grid Support Utility Interactive Inverter | 8.0842 | 240 | 97.5 | SGS | [6/2/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-07-03 | 2023-09-01 |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2023-09-01
Geneverse Energy Inc. | GVI-HS-10K-USM {240V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 240 Vac, Grid Support Utility Interactive Inverter | 10.1767 | 240 | 97 | SGS | [6/2/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-07-03 | 2023-09-01 |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2023-09-01
Ginlong Technologies Co., Ltd. | S6-EH1P3.8K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 3.801 | 240 | 96.5 | CSA Group | [2/23/2024] | CSA Group | [1/13/2023] | [A2] | 2023-04-14 | [1/13/2023] | 2023-04-21 | CSA Group | 2023-01-28 | 2023-04-14 |  | N | N | 18.83 |  |  | 140 | 370 | 450 | 0.3801 | 0.7602 | 1.1403 | 1.9005 | 2.8507 | 3.801 | 96.5132 | 96.0087 | 96.4231 | 96.6237 | 96.6367 | 96.6709 | 96.5737 | 95.4944 | 96.0488 | 96.5134 | 96.4535 | 96.739 | 97.0521 | 96.5833 | 95.2959 | 95.8208 | 96.406 | 96.5264 | 96.7141 | 96.5462 | 96.528 | 2023-04-14 | 2025-06-11
Ginlong Technologies Co., Ltd. | S6-EH1P5K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 5.0017 | 240 | 96.5 | CSA Group | [2/23/2024] | CSA Group | [1/13/2023] | [A2] | 2023-04-14 | [1/13/2023] | 2023-04-21 | CSA Group | 2023-01-28 | 2023-04-14 |  | N | N | 18.83 |  |  | 140 | 370 | 450 | 0.50017 | 1.0003 | 1.5005 | 2.5008 | 3.7512 | 5.0017 | 94.2264 | 95.2572 | 96.6079 | 96.5986 | 96.7891 | 96.6855 | 96.5431 | 95.377 | 95.8168 | 96.542 | 96.5776 | 96.8363 | 96.978 | 96.6444 | 95.1057 | 95.5303 | 96.4585 | 96.5737 | 96.7108 | 96.7105 | 96.5285 | 2023-04-14 | 2025-06-11
Ginlong Technologies Co., Ltd. | RHI-1P5K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 5.003 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 115 | 330 | 450 | 0.5 | 1.001 | 1.501 | 2.501 | 3.752 | 5.003 | 95.12 | 96.18 | 96.94 | 97.37 | 97.18 | 96.63 | 97.03 | 95.66 | 97.24 | 97.42 | 97.55 | 97.7 | 96.96 | 97.49 | 95.38 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71 | 97.65 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | RHI-1P6K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 6.004 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 130 | 330 | 450 | 0.6 | 1.201 | 1.801 | 3.002 | 4.503 | 6.004 | 94.9 | 96.12 | 96.76 | 97.3 | 97.32 | 96.48 | 97.05 | 95.55 | 96.98 | 97.4 | 97.42 | 97.37 | 97.95 | 97.32 | 95.31 | 96.91 | 97.48 | 97.59 | 97.58 | 97.58 | 97.45 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | RHI-1P7K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 7.006 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 160 | 330 | 450 | 0.701 | 1.401 | 2.102 | 3.503 | 5.254 | 7.006 | 94.96 | 96.16 | 96.83 | 97.36 | 97.35 | 96.54 | 97.1 | 95.58 | 97.01 | 97.43 | 97.5 | 97.51 | 97.04 | 97.37 | 95.32 | 96.96 | 97.52 | 97.66 | 97.6 | 97.6 | 97.48 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | RHI-1P7.6K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 7.603 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 175 | 330 | 450 | 0.76 | 1.521 | 2.281 | 3.801 | 5.702 | 7.603 | 95.05 | 96.16 | 96.89 | 97.34 | 97.15 | 96.58 | 97 | 95.63 | 97.18 | 97.48 | 97.78 | 97.35 | 97.9 | 97.4 | 95.36 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71 | 97.66 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | S6-EH1P7.6K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.604 | 240 | 97 | CSA Group | [2/23/2024] | CSA Group | [8/5/2023] | [A2] | 2023-04-14 | [1/13/2023] | 2023-04-21 | CSA Group | 2023-04-19 | 2023-04-14 | Formerly S6-EH1P7.6K-H-L-US. | N | N | 16.33 |  |  | 175 | 380 | 450 | 0.76 | 1.521 | 2.281 | 3.802 | 5.703 | 7.604 | 95.78 | 96.57 | 97.14 | 97.12 | 97.27 | 97.32 | 97.13 | 95.02 | 96.11 | 97.17 | 97.26 | 97.29 | 97.63 | 97.13 | 94.73 | 96.14 | 96.95 | 97.09 | 97.15 | 97.33 | 96.97 | 2023-04-14 | 2025-06-11
Ginlong Technologies Co., Ltd. | RHI-1P8K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 8.006 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 185 | 330 | 450 | 0.801 | 1.601 | 2.402 | 4.003 | 6.004 | 8.006 | 95.12 | 96.18 | 96.94 | 97.37 | 97.18 | 96.63 | 97.03 | 95.66 | 97.24 | 97.42 | 97.55 | 97.7 | 96.96 | 97.49 | 95.38 | 96.75 | 97.61 | 97.82 | 97.85 | 97.71 | 97.65 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | RHI-1P9K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 9 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 9.006 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 210 | 330 | 450 | 0.901 | 1.801 | 2.702 | 4.503 | 6.754 | 9.006 | 95.14 | 96.75 | 97 | 97.49 | 97.37 | 97 | 97.21 | 95.72 | 97.27 | 97.45 | 97.61 | 97.75 | 97.11 | 97.55 | 95.58 | 96.74 | 97.66 | 97.82 | 97.82 | 97.71 | 97.65 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | S6-EH2P9.6K03-SV-YD-L-US {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 9.6471 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 27.1 |  |  | 240 | 370 | 425 | 0.965 | 1.929 | 2.894 | 4.824 | 7.235 | 9.647 | 93.18 | 94.41 | 95.47 | 96 | 95.5 | 95.52 | 95.46 | 93.21 | 94.44 | 95.48 | 96.01 | 95.51 | 95.53 | 95.47 | 92.36 | 94 | 95.48 | 96.01 | 95.54 | 95.59 | 95.43 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH1P9.9K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.9 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.99 | 240 | 97 | CSA Group | [2/23/2024] | CSA Group | [2/23/2024] | [A2] | 2024-05-21 | [2/23/2024] | 2024-05-21 | CSA Group | 2023-12-20 | 2024-05-21 |  | N | N | 16.38 |  |  | 230 | 380 | 450 | 0.999 | 1.998 | 2.997 | 4.995 | 7.493 | 9.99 | 93.57 | 96.11 | 97.39 | 97.27 | 97.33 | 97.21 | 97.11 | 93.52 | 95.74 | 97.27 | 97.32 | 97.21 | 97.39 | 97.03 | 92.78 | 95.46 | 97.38 | 97.33 | 97.28 | 97.6 | 97.05 | 2024-05-21 | 2025-06-11
Ginlong Technologies Co., Ltd. | S6-EH1P10K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 10.001 | 240 | 97 | CSA Group | [2/23/2024] | CSA Group | [8/5/2023] | [A2] | 2023-04-14 | [1/13/2023] | 2023-04-21 | CSA Group | 2023-04-19 | 2023-04-14 |  | N | N | 16.38 |  |  | 230 | 380 | 450 | 1 | 2 | 3 | 5 | 7.501 | 10.001 | 93.57 | 96.11 | 97.39 | 97.27 | 97.33 | 97.21 | 97.11 | 93.52 | 95.74 | 97.27 | 97.32 | 97.21 | 97.39 | 97.03 | 92.78 | 95.46 | 97.38 | 97.33 | 97.28 | 97.6 | 97.05 | 2023-04-14 | 2025-06-11
Ginlong Technologies Co., Ltd. | RHI-1P10K-HVES-5G {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 10.005 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2019] | [18] | 2020-04-13 | [08/30/2019] | 2020-10-01 | CSA Group | 2020-08-20 | 2020-04-13 |  | N | N | 1 |  |  | 230 | 330 | 450 | 1 | 2.001 | 3.001 | 5.002 | 7.504 | 10.005 | 95.18 | 96.78 | 97.08 | 97.55 | 97.61 | 97.06 | 97.37 | 95.3 | 96.32 | 97.58 | 97.66 | 97.73 | 97.21 | 97.5 | 95.6 | 96.8 | 97.68 | 97.79 | 97.81 | 97.71 | 97.65 | 2020-04-13 | 2020-10-01
Ginlong Technologies Co., Ltd. | S6-EH1P11.4K-H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.406 | 240 | 97 | CSA Group | [2/23/2024] | CSA Group | [8/5/2023] | [A2] | 2023-04-14 | [1/13/2023] | 2023-04-21 | CSA Group | 2023-04-19 | 2023-04-14 |  | N | N | 15.36 |  |  | 245 | 380 | 450 | 1.141 | 2.281 | 3.422 | 5.703 | 8.554 | 11.406 | 94.77 | 96.19 | 97.09 | 97.38 | 97.26 | 97.27 | 97.11 | 95.99 | 96.88 | 96.88 | 97.03 | 97.23 | 97.34 | 97.08 | 95.55 | 96.65 | 97.05 | 97.18 | 97.22 | 97.57 | 97.11 | 2023-04-14 | 2025-06-11
Ginlong Technologies Co., Ltd. | S6-EH2P11.4K03-SV-YD-L-US {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 11.41 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 26.79 |  |  | 160 | 380 | 450 | 1.141 | 2.282 | 3.423 | 5.705 | 8.557 | 11.41 | 92.32 | 93.96 | 95.46 | 96.01 | 95.53 | 95.58 | 95.42 | 93.44 | 94.45 | 95.44 | 96.01 | 95.54 | 95.53 | 95.49 | 93.46 | 94.48 | 95.45 | 96.01 | 95.52 | 95.54 | 95.48 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH2P12K03-SV-YD-L-US-E {240V} | Y | Y | N | N | N | N | Y* | Y | 11.9 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 11.939 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 26.72 |  |  | 160 | 380 | 450 | 1.194 | 2.388 | 3.582 | 5.97 | 8.954 | 11.939 | 93.17 | 93.91 | 95.49 | 96.01 | 95.48 | 95.59 | 95.42 | 93.58 | 94.37 | 95.27 | 96.02 | 95.52 | 95.58 | 95.47 | 93.32 | 94.31 | 95.48 | 96.01 | 95.51 | 95.51 | 95.46 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH2P12K03-SV-YD-L-US {240V} | Y | Y | N | N | N | N | Y* | Y | 11.9 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 11.94 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 27.02 |  |  | 160 | 380 | 450 | 1.194 | 2.388 | 3.582 | 5.97 | 8.955 | 11.94 | 92.21 | 93.23 | 95.54 | 96.02 | 95.56 | 95.57 | 95.4 | 93.54 | 94.56 | 95.45 | 96.02 | 95.52 | 95.53 | 95.49 | 93.5 | 94.52 | 95.43 | 96.01 | 95.53 | 95.55 | 95.49 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH2P14K03-SV-YD-L-US {240V} | Y | Y | N | N | N | N | Y* | Y | 13.9 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 13.96 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 26.98 |  |  | 186 | 380 | 450 | 1.396 | 2.792 | 4.188 | 6.98 | 10.47 | 13.96 | 92.12 | 93.89 | 95.24 | 96.02 | 95.57 | 95.6 | 95.4 | 93.45 | 94.5 | 95.54 | 96.02 | 95.57 | 95.53 | 95.52 | 93.55 | 94.45 | 95.52 | 96.02 | 95.55 | 95.57 | 95.51 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH2P16K03-SV-YD-L-US {240V} | Y | Y | N | N | N | N | Y* | Y | 15.9 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 15.911 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 27.07 |  |  | 186 | 380 | 450 | 1.591 | 3.182 | 4.773 | 7.955 | 11.933 | 15.911 | 92.15 | 94.13 | 95.17 | 95.99 | 95.51 | 95.53 | 95.37 | 93.9 | 95.25 | 95.35 | 96 | 95.47 | 95.53 | 95.5 | 93.98 | 95.26 | 95.47 | 96 | 95.45 | 95.5 | 95.5 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH2P16K03-SV-YD-L-US-E {240V} | Y | Y | N | N | N | N | Y* | Y | 15.9 kW, 240 Vac Grid Support Utility Interactive inverter with PCS functionality. | 15.94 | 240 | 95.5 | SGS | [4/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | 2025-06-23 |  | N | N | 23.07 |  |  | 186 | 380 | 450 | 1.594 | 3.188 | 4.782 | 7.97 | 11.955 | 15.94 | 92.21 | 93.89 | 95.52 | 96.01 | 95.58 | 95.6 | 95.45 | 93.27 | 94.3 | 95.48 | 96.02 | 95.51 | 95.53 | 95.47 | 93.28 | 94.31 | 95.52 | 96 | 95.57 | 95.58 | 95.5 | 2025-06-23 | 2026-03-23 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-LV-YD-H-US(21A) {208V} | Y | Y | N | N | N | N | Y* |  | 25.88 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality | 25.8835 | 208 | 97 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 57.3 |  |  | 500 | 675 | 850 | 2.5884 | 5.1767 | 7.7651 | 12.9418 | 19.4127 | 25.8835 | 93.9922 | 95.7952 | 96.926 | 96.8916 | 97.1284 | 97.2124 | 96.8665 | 95.8284 | 95.9332 | 96.6126 | 96.9374 | 97.4868 | 97.2454 | 97.1104 | 89.5538 | 94.454 | 95.935 | 96.8496 | 97.2484 | 97.382 | 96.5662 | 2026-03-11
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-LV-YD-H-US {208V} | Y | Y | N | N | N | N | Y* |  | 30 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 25.9 | 208 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 58 |  |  | 360 | 605 | 850 | 2.59 | 5.18 | 7.7699 | 12.9499 | 19.4248 | 25.8998 | 95.778 | 96.9618 | 97.2838 | 97.282 | 97.046 | 96.712 | 97.0525 | 96.054 | 97.146 | 97.5836 | 97.52 | 97.414 | 97.27 | 97.3816 | 95.75 | 97.158 | 97.54 | 97.574 | 97.478 | 97.406 | 97.4169 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-LV-YD-H-US {240V} | Y | Y | N | N | N | N | Y* |  | 30 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 29.705 | 240 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 61 |  |  | 360 | 605 | 850 | 2.971 | 5.941 | 8.912 | 14.853 | 22.279 | 29.705 | 96.02 | 97 | 97.32 | 97.28 | 97.01 | 96.69 | 97.05 | 95.99 | 97.26 | 97.56 | 97.58 | 97.44 | 97.31 | 97.41 | 95.71 | 97.22 | 97.57 | 97.63 | 97.53 | 97.4 | 97.46 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-LV-YD-H-US(21A) {240V} | Y | Y | N | N | N | N | Y* |  | 29.83 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality | 29.8342 | 240 | 97 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 70.7 |  |  | 500 | 675 | 850 | 2.9834 | 5.9668 | 8.9503 | 14.9171 | 22.3756 | 29.8342 | 94.1056 | 95.74 | 95.9364 | 96.9676 | 97.0914 | 97.208 | 96.7456 | 95.8062 | 95.9614 | 96.708 | 96.93 | 97.4686 | 97.4116 | 97.1195 | 89.631 | 95.7398 | 96.8554 | 97.2412 | 97.5684 | 97.5508 | 97.0043 | 2026-03-11
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-NV-YD-H-US(21A) {480V} | Y | Y | N | N | N | N | Y* |  | 29.88 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 29.8847 | 480 | 97 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 54.5 |  |  | 500 | 675 | 850 | 2.9885 | 5.9769 | 8.9654 | 14.9424 | 22.4135 | 29.8847 | 94.0686 | 95.8068 | 96.0994 | 97.282 | 97.2044 | 97.2516 | 96.8951 | 95.8456 | 96.0126 | 96.686 | 97.236 | 97.5746 | 97.4406 | 97.2429 | 89.6642 | 95.7374 | 96.8292 | 97.2394 | 97.57 | 97.6 | 97.0053 | 2026-03-11
Ginlong Technologies Co., Ltd. | S6-EH3P30K03-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 30 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 29.891 | 480 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 56 |  |  | 360 | 605 | 850 | 2.989 | 5.978 | 8.967 | 14.946 | 22.418 | 29.891 | 95.77 | 97.04 | 97.31 | 97.33 | 97.07 | 96.72 | 97.08 | 95.92 | 96.99 | 97.63 | 97.52 | 97.47 | 97.3 | 97.4 | 95.81 | 96.97 | 97.57 | 97.55 | 97.5 | 97.44 | 97.42 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | S6-EH3P40K04-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 40 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 39.8029 | 480 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 57 |  |  | 360 | 605 | 850 | 3.9803 | 7.9606 | 11.9409 | 19.9015 | 29.8522 | 39.8029 | 95.9044 | 96.9128 | 97.332 | 97.2852 | 97.0552 | 96.724 | 97.067 | 95.986 | 97.1218 | 97.5562 | 97.5342 | 97.4136 | 97.367 | 97.382 | 95.72 | 97.18 | 97.56 | 97.5722 | 97.5 | 97.4684 | 97.4336 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | S6-EH3P40K04-NV-YD-H-US(21A) {480V} | Y | Y | N | N | N | N | Y* |  | 39.84kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 39.844 | 480 | 97 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 70 |  |  | 500 | 675 | 850 | 3.9844 | 7.9688 | 11.9532 | 19.922 | 29.883 | 39.844 | 94.1092 | 95.8522 | 97.0008 | 97.3276 | 97.3346 | 97.4462 | 97.0955 | 96.0928 | 96.5924 | 96.914 | 97.447 | 97.4484 | 97.357 | 97.2824 | 94.472 | 96.3238 | 97.1636 | 97.5694 | 97.6026 | 97.3274 | 97.34 | 2026-03-11
Ginlong Technologies Co., Ltd. | S6-EH3P50K04-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 50 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 49.8003 | 480 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 52 |  |  | 450 | 650 | 850 | 4.98 | 9.9601 | 14.9401 | 24.9001 | 37.3502 | 49.8003 | 95.7862 | 96.9366 | 97.2908 | 97.3016 | 97.0498 | 96.686 | 97.0572 | 96.03 | 97.165 | 97.59 | 97.52 | 97.4236 | 97.3092 | 97.3894 | 95.714 | 97.195 | 97.5476 | 97.5848 | 97.5016 | 97.4614 | 97.4357 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | S6-EH3P50K04-NV-YD-H-US(21A) {480V} | Y | Y | N | N | N | N | Y* |  | 49.80 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 49.8034 | 480 | 97.5 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 76 |  |  | 600 | 725 | 850 | 4.9803 | 9.9607 | 14.941 | 24.9017 | 37.3526 | 49.8034 | 94.4062 | 96.4892 | 97.322 | 97.4496 | 97.3804 | 97.2358 | 97.2172 | 94.4798 | 96.4874 | 97.138 | 97.616 | 97.5676 | 97.5136 | 97.346 | 95.4054 | 96.9518 | 97.2974 | 97.5806 | 97.5812 | 97.4988 | 97.4244 | 2026-03-11
Ginlong Technologies Co., Ltd. | S6-EH3P60K04-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 60 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 59.7098 | 480 | 97.5 | TUV Rheinland of North America | [6/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland of North America | 2025-06-24 |  |  | N | N | 59 |  |  | 450 | 650 | 850 | 5.971 | 11.942 | 17.9129 | 29.8549 | 44.7823 | 59.7098 | 95.7718 | 96.9604 | 97.2936 | 97.2821 | 97.0418 | 96.7152 | 97.0513 | 96.0116 | 97.1956 | 97.5873 | 97.5413 | 97.4187 | 97.2794 | 97.3903 | 95.7391 | 97.1654 | 97.5485 | 97.6125 | 97.5087 | 97.3907 | 97.4414 | 2025-10-01 | 2025-11-12
Ginlong Technologies Co., Ltd. | S6-EH3P60K04-NV-YD-H-US(21A) {480V} | Y | Y | N | N | N | N | Y* |  | 59.76 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 59.763 | 480 | 97.5 | TUV Rheinland of North America | [12/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 76 |  |  | 600 | 725 | 850 | 5.976 | 11.953 | 17.929 | 29.882 | 44.822 | 59.763 | 96.01 | 97.2 | 97.59 | 97.54 | 97.42 | 97.28 | 97.39 | 95.84 | 96.83 | 97.37 | 97.65 | 97.49 | 97.31 | 97.4 | 95.74 | 97.17 | 97.55 | 97.61 | 97.51 | 97.39 | 97.44 | 2026-03-11
Ginlong Technologies Co., Ltd. | S6-EH3P75K10-LV-YD-H-US {208V} | Y | Y | N | N | N | N | Y* |  | 75 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 70.042 | 208 | 96 | CSA Group | [7/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-07-17 |  |  | N | N | 39.56 |  |  | 400 | 650 | 900 | 7.004 | 14.008 | 21.013 | 35.021 | 52.532 | 70.042 | 93.2 | 94.45 | 96 | 96.22 | 96.14 | 95.9 | 95.93 | 93.66 | 96.05 | 96.33 | 96.61 | 96.36 | 95.95 | 96.27 | 93.62 | 95.47 | 96.07 | 96.33 | 96.14 | 95.82 | 96.02 | 2026-09-01 |  | Y | N | N | N | N | N | Y | N | N
Ginlong Technologies Co., Ltd. | S6-EH3P75K10-LV-YD-H-US {240V} | Y | Y | N | N | N | N | Y* |  | 75 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 74.94 | 240 | 96 | CSA Group | [7/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-07-17 |  |  | N | N | 41.25 |  |  | 400 | 650 | 900 | 7.494 | 14.988 | 22.482 | 37.47 | 56.205 | 74.94 | 93.1 | 94.34 | 96.06 | 96.23 | 96.12 | 95.91 | 95.92 | 93.72 | 96.22 | 96.33 | 96.59 | 96.36 | 95.98 | 96.27 | 93.79 | 95.43 | 96.07 | 96.32 | 96.36 | 95.85 | 96.14 | 2026-09-01 |  | Y | N | N | N | N | N | Y | N | N
Ginlong Technologies Co., Ltd. | S6-EH3P100K10-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 100 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter | 99.945 | 480 | 97.5 | CSA Group | [7/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-07-17 |  |  | N | N | 40.78 |  |  | 550 | 725 | 900 | 9.994 | 19.989 | 29.983 | 49.972 | 74.958 | 99.945 | 95.92 | 96.72 | 97.1 | 97.32 | 97.54 | 97.52 | 97.33 | 94.98 | 96.22 | 96.71 | 96.85 | 97.29 | 97.29 | 96.98 | 95.41 | 96.63 | 97.27 | 97.43 | 97.72 | 97.7 | 97.46 | 2026-09-11 |  | Y | N | N | N | N | N | Y | N | N
Ginlong Technologies Co., Ltd. | S6-EH3P125K10-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 125 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter | 124.925 | 480 | 97.5 | CSA Group | [7/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-07-17 |  |  | N | N | 38.4 |  |  | 600 | 750 | 900 | 12.492 | 24.985 | 37.477 | 62.462 | 93.693 | 124.925 | 95.97 | 96.9 | 97.18 | 97.43 | 97.51 | 97.32 | 97.35 | 94.99 | 96.35 | 96.78 | 97.11 | 97.29 | 97.62 | 97.07 | 95.6 | 96.88 | 97.31 | 97.68 | 97.72 | 97.63 | 97.53 | 2026-09-11 |  | Y | N | N | N | N | N | Y | N | N
Ginlong Technologies Co., Ltd. | S6-EH3P150K10-NV-YD-H-US {480V} | Y | Y | N | N | N | N | Y* |  | 150 kW, 480 Vac Grid Support Utility Interactive Hybrid Inverter | 149.923 | 480 | 97.5 | CSA Group | [7/16/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-07-17 |  |  | N | N | 43.74 |  |  | 600 | 750 | 900 | 14.992 | 29.985 | 44.977 | 74.961 | 112.442 | 149.923 | 96.95 | 97.16 | 97.74 | 97.53 | 97.41 | 97.25 | 97.44 | 96.34 | 96.72 | 97.12 | 97.27 | 97.3 | 97.79 | 97.23 | 96.85 | 97.29 | 97.42 | 97.71 | 97.7 | 97.59 | 97.61 | 2026-09-11 |  | Y | N | N | N | N | N | Y | N | N
Global Tech China Ltd. | SSM-6.0-SPHYB-UL {208V} | Y | Y | N | N | N | N | N |  | 6 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 6.124 | 208 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.61237 | 1.2247 | 1.8371 | 3.0618 | 4.6 | 6.1 | 91.5 | 94.4 | 95.4 | 96.1 | 96.2 | 96 | 95.8 | 93.6 | 96 | 96.7 | 97.2 | 97.1 | 97 | 96.9 | 93 | 95.5 | 96.3 | 96.9 | 96.9 | 96.8 | 96.6 | 2025-11-12
Global Tech China Ltd. | SSM-6.0-SPHYB-UL {240V} | Y | Y | N | N | N | N | N |  | 6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 6.149 | 240 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.61493 | 1.2299 | 1.8448 | 3.0747 | 4.6 | 6.1 | 91.6 | 94.4 | 95.5 | 96.3 | 96.4 | 96.4 | 96 | 93.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.4 | 97.2 | 92.7 | 95.4 | 96.4 | 97.1 | 97.3 | 97.3 | 96.9 | 2025-11-12
Global Tech China Ltd. | SSM-7.6-SPHYB-UL {240V} | Y | Y | N | N | N | N | N |  | 7.6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 7.6472 | 240 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.76472 | 1.5294 | 2.2942 | 3.8236 | 5.7 | 7.6 | 93 | 95.6 | 96.2 | 96.7 | 96.5 | 96.2 | 96.3 | 89.7 | 96.1 | 96.8 | 97.2 | 97 | 96.8 | 96.6 | 94.1 | 96.2 | 96.8 | 97.1 | 96.9 | 96.6 | 96.8 | 2025-11-12
Global Tech China Ltd. | SSM-7.6-SPHYB-UL {208V} | Y | Y | N | N | N | N | N |  | 7.6 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 7.648 | 208 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.7 | 7.6 | 92.9 | 95.5 | 96.2 | 96.6 | 96.4 | 96.2 | 96.3 | 93.7 | 96.1 | 96.8 | 97.2 | 97 | 96.8 | 96.8 | 94.1 | 96.2 | 96.8 | 97.1 | 96.9 | 96.7 | 96.8 | 2025-11-12
Global Tech China Ltd. | SSM-11.4-SPHYB-UL {240V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 10.14 | 240 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.6 | 10.2 | 92.9 | 95.5 | 96.1 | 96.6 | 96.4 | 96.1 | 96.2 | 93.7 | 96 | 96.7 | 97.1 | 96.9 | 96.7 | 96.7 | 94.1 | 96.2 | 96.7 | 97 | 96.8 | 96.6 | 96.7 | 2025-11-12
Global Tech China Ltd. | SSM-11.4-SPHYB-UL {208V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 10.186 | 208 | 96.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.028 | 3.042 | 5.07 | 7.6 | 10.1 | 93.1 | 95.6 | 96.2 | 96.7 | 96.5 | 96.2 | 96.3 | 93.7 | 96.1 | 96.8 | 97.2 | 97 | 96.8 | 96.8 | 94.1 | 96.3 | 96.8 | 97.1 | 96.9 | 96.7 | 96.8 | 2025-11-12
Go Electric Inc. | 250-480-60-HLT {480V} | N | N | Y | Y | Y | Y | Y* | Y | 250 kW, 480 Vac Grid Support Multi-Mode Utility Interactive Inverter | 259.2 | 480 | 93 | No Information Submitted | No Information Submitted | UL | [04/14/2021] | [V21.01.6.1] | 2021-08-23 | [04/14/2021] | 2022-05-23 | PCTest | 2022-05-17 | 2022-05-23 |  | N | N | 748.7 |  |  | 540 | 700 | 780 | 25.92 | 51.84 | 77.76 | 129.6 | 194.4 | 259.2 | 80.3271 | 90.3414 | 93.4914 | 95.5014 | 95.0886 | 95.4071 | 94.1717 | 78.96 | 88.09 | 91.61 | 93.81 | 94.57 | 94.5 | 93.1 | 76.6614 | 86.5629 | 90.2743 | 92.8071 | 93.6429 | 93.7629 | 92.0359 | 2021-08-23 | 2022-05-23
GoodWe Technologies Co., Ltd. | GEC5.0-1U-US20 {240V} | N | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, with PCS functionality. | 4.9828 | 240 | 96 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.6 |  |  | 105 | 300 | 495 | 0.49828 | 0.99656 | 1.4948 | 2.4914 | 3.7371 | 4.9828 | 93.0286 | 95.1786 | 95.4186 | 95.81 | 95.61 | 94.3929 | 95.4433 | 94.29 | 95.9986 | 96.2543 | 96.4986 | 96.2243 | 96.6271 | 96.217 | 94.24 | 95.8229 | 96.3386 | 96.5929 | 96.5429 | 96.3671 | 96.3919 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW5000-SBP-US20 {240V} | N | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, with PCS functionality. | 4.9828 | 240 | 96 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.6 |  |  | 105 | 300 | 495 | 0.49828 | 0.99656 | 1.4948 | 2.4914 | 3.7371 | 4.9828 | 93.0286 | 95.1786 | 95.4186 | 95.81 | 95.61 | 94.3929 | 95.4433 | 94.29 | 95.9986 | 96.2543 | 96.4986 | 96.2243 | 96.6271 | 96.217 | 94.24 | 95.8229 | 96.3386 | 96.5929 | 96.5429 | 96.3671 | 96.3919 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW5000H-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, Bi-directional Grid Support Utility Interactive PV and Battery Inverter | 4.989 | 240 | 95.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 | Efficiency data includes external Isolation transformer GW5000G-TF effect. | N | N | 47.36 |  |  | 300 | 400 | 480 | 0.499 | 0.998 | 1.497 | 2.495 | 3.742 | 4.989 | 87.29 | 92.59 | 94.36 | 95.51 | 95.76 | 95.68 | 95.04 | 88.08 | 93.35 | 94.82 | 95.82 | 96.09 | 96.05 | 95.42 | 87.62 | 93.17 | 94.65 | 95.74 | 96.09 | 96.02 | 95.36 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEH5.0-1U-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 5.0047 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 235 | 390 | 500 | 0.50047 | 1.0009 | 1.5014 | 2.5023 | 3.7535 | 5.0047 | 93.8586 | 96.2286 | 96.6214 | 97.1629 | 97.0571 | 96.9514 | 96.8524 | 95.3457 | 96.8429 | 97.3786 | 97.6771 | 97.6357 | 97.4343 | 97.4722 | 95.3371 | 96.5929 | 97.0314 | 97.4057 | 97.4243 | 97.2571 | 97.2398 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW5000-ES-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 5.0047 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 235 | 390 | 500 | 0.50047 | 1.0009 | 1.5014 | 2.5023 | 3.7535 | 5.0047 | 93.8586 | 96.2286 | 96.6214 | 97.1629 | 97.0571 | 96.9514 | 96.8524 | 95.3457 | 96.8429 | 97.3786 | 97.6771 | 97.6357 | 97.4343 | 97.4722 | 95.3371 | 96.5929 | 97.0314 | 97.4057 | 97.4243 | 97.2571 | 97.2398 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEC5.0-1U-US10 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 5.031 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 11.16 |  |  | 200 | 350 | 495 | 0.5031 | 1.0062 | 1.5093 | 2.5155 | 3.7732 | 5.031 | 92.3455 | 95.0391 | 95.888 | 96.374 | 96.441 | 96.3321 | 96.1212 | 93.2413 | 95.834 | 96.4325 | 96.9776 | 97.1497 | 97.0738 | 96.8016 | 92.0083 | 95.2827 | 96.1894 | 96.8065 | 96.9577 | 96.9254 | 96.5504 | 2021-11-12 | 2023-12-11
GoodWe Technologies Co., Ltd. | GW5000A-BP {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 5.031 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 11.16 |  |  | 200 | 350 | 495 | 0.5031 | 1.0062 | 1.5093 | 2.5155 | 3.7732 | 5.031 | 92.3455 | 95.0391 | 95.888 | 96.374 | 96.441 | 96.3321 | 96.1212 | 93.2413 | 95.834 | 96.4325 | 96.9776 | 97.1497 | 97.0738 | 96.8016 | 92.0083 | 95.2827 | 96.1894 | 96.8065 | 96.9577 | 96.9254 | 96.5504 | 2021-01-21 | 2023-12-11
GoodWe Technologies Co., Ltd. | GEH5.0-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 5.0675 | 240 | 97.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 11.24 |  |  | 300 | 400 | 480 | 0.50675 | 1.0135 | 1.5202 | 2.5337 | 3.8006 | 5.0675 | 93.9925 | 96.2316 | 96.8797 | 97.2517 | 97.2643 | 97.1484 | 97.0272 | 94.9307 | 96.9459 | 97.4098 | 97.6103 | 97.5959 | 97.5021 | 97.4328 | 94.8782 | 96.5215 | 97.2181 | 97.7266 | 97.6607 | 97.5509 | 97.4477 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW5000A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 5.0675 | 240 | 97.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 11.24 |  |  | 300 | 400 | 480 | 0.50675 | 1.0135 | 1.5202 | 2.5337 | 3.8006 | 5.0675 | 93.9925 | 96.2316 | 96.8797 | 97.2517 | 97.2643 | 97.1484 | 97.0272 | 94.9307 | 96.9459 | 97.4098 | 97.6103 | 97.5959 | 97.5021 | 97.4328 | 94.8782 | 96.5215 | 97.2181 | 97.7266 | 97.6607 | 97.5509 | 97.4477 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEH6.0-1U-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 5.9973 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 285 | 390 | 500 | 0.59973 | 1.1995 | 1.7992 | 2.9987 | 4.498 | 5.9973 | 95.2243 | 95.7757 | 96.4657 | 96.9057 | 96.9414 | 96.8086 | 96.7432 | 95.5114 | 96.5143 | 97.1643 | 97.62 | 97.61 | 97.41 | 97.4099 | 95.26 | 96.0886 | 96.7686 | 97.3786 | 97.3714 | 97.2786 | 97.1473 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW6000-ES-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 5.9973 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 285 | 390 | 500 | 0.59973 | 1.1995 | 1.7992 | 2.9987 | 4.498 | 5.9973 | 95.2243 | 95.7757 | 96.4657 | 96.9057 | 96.9414 | 96.8086 | 96.7432 | 95.5114 | 96.5143 | 97.1643 | 97.62 | 97.61 | 97.41 | 97.4099 | 95.26 | 96.0886 | 96.7686 | 97.3786 | 97.3714 | 97.2786 | 97.1473 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEC6.0-1U-US20 {240V} | N | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, with PCS functionality. | 6.0097 | 240 | 96 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.6 |  |  | 125 | 300 | 495 | 0.60097 | 1.2019 | 1.8029 | 3.0048 | 4.5073 | 6.0097 | 92.7214 | 95.0743 | 95.43 | 95.7486 | 95.7086 | 94.3271 | 95.4633 | 94.6529 | 96.01 | 96.2829 | 96.3057 | 96.36 | 96.9286 | 96.282 | 95.6686 | 96.4657 | 96.78 | 96.7214 | 96.49 | 96.2014 | 96.5249 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW6000-SBP-US20 {240V} | N | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, with PCS functionality. | 6.0097 | 240 | 96 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.6 |  |  | 125 | 300 | 495 | 0.60097 | 1.2019 | 1.8029 | 3.0048 | 4.5073 | 6.0097 | 92.7214 | 95.0743 | 95.43 | 95.7486 | 95.7086 | 94.3271 | 95.4633 | 94.6529 | 96.01 | 96.2829 | 96.3057 | 96.36 | 96.9286 | 96.282 | 95.6686 | 96.4657 | 96.78 | 96.7214 | 96.49 | 96.2014 | 96.5249 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEC6.0-1U-US10 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 6.03 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 11.3 |  |  | 200 | 350 | 495 | 0.603 | 1.206 | 1.809 | 3.015 | 4.5225 | 6.03 | 93.1771 | 95.286 | 96.0561 | 96.4195 | 96.3466 | 96.1346 | 96.1366 | 93.9722 | 96.6306 | 96.6399 | 97.0392 | 97.0779 | 96.9108 | 96.8622 | 93.5715 | 95.7069 | 96.4745 | 96.8879 | 96.9108 | 96.8052 | 96.6546 | 2021-11-12 | 2023-12-11
GoodWe Technologies Co., Ltd. | GW6000A-BP {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 6.03 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 11.3 |  |  | 200 | 350 | 495 | 0.603 | 1.206 | 1.809 | 3.015 | 4.5225 | 6.03 | 93.1771 | 95.286 | 96.0561 | 96.4195 | 96.3466 | 96.1346 | 96.1366 | 93.9722 | 96.6306 | 96.6399 | 97.0392 | 97.0779 | 96.9108 | 96.8622 | 93.5715 | 95.7069 | 96.4745 | 96.8879 | 96.9108 | 96.8052 | 96.6546 | 2021-01-21 | 2023-12-11
GoodWe Technologies Co., Ltd. | GEH6.0-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 6.109 | 240 | 97.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.3 |  |  | 360 | 400 | 480 | 0.6109 | 1.2218 | 1.8327 | 3.0545 | 4.5817 | 6.109 | 95.1428 | 96.9138 | 97.2751 | 97.4472 | 97.3624 | 97.1646 | 97.2486 | 95.6917 | 97.2031 | 97.5713 | 97.6709 | 97.5587 | 97.3756 | 97.4822 | 95.3048 | 96.9647 | 97.385 | 97.593 | 97.4861 | 97.3196 | 97.3748 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW6000A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 6.109 | 240 | 97.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.3 |  |  | 360 | 400 | 480 | 0.6109 | 1.2218 | 1.8327 | 3.0545 | 4.5817 | 6.109 | 95.1428 | 96.9138 | 97.2751 | 97.4472 | 97.3624 | 97.1646 | 97.2486 | 95.6917 | 97.2031 | 97.5713 | 97.6709 | 97.5587 | 97.3756 | 97.4822 | 95.3048 | 96.9647 | 97.385 | 97.593 | 97.4861 | 97.3196 | 97.3748 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEH7.0-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.057 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.48 |  |  | 210 | 400 | 480 | 0.7057 | 1.4114 | 2.1171 | 3.5285 | 5.2927 | 7.057 | 94.3693 | 95.9144 | 96.3821 | 96.5425 | 96.3948 | 96.1519 | 96.3071 | 95.9384 | 97.2694 | 97.5935 | 97.666 | 97.5651 | 97.3232 | 97.4978 | 95.3006 | 96.8755 | 97.3229 | 97.7033 | 97.5711 | 97.3319 | 97.4315 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW7000A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.057 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.48 |  |  | 210 | 400 | 480 | 0.7057 | 1.4114 | 2.1171 | 3.5285 | 5.2927 | 7.057 | 94.3693 | 95.9144 | 96.3821 | 96.5425 | 96.3948 | 96.1519 | 96.3071 | 95.9384 | 97.2694 | 97.5935 | 97.666 | 97.5651 | 97.3232 | 97.4978 | 95.3006 | 96.8755 | 97.3229 | 97.7033 | 97.5711 | 97.3319 | 97.4315 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEC7.0-1U-US10 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 7.059 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.48 |  |  | 200 | 350 | 495 | 0.7059 | 1.4118 | 2.1177 | 3.5295 | 5.2942 | 7.059 | 94.1624 | 95.6808 | 96.2387 | 96.4556 | 96.2632 | 96.0229 | 96.1755 | 94.8837 | 96.3856 | 96.6968 | 96.9955 | 97.0411 | 96.7889 | 96.8585 | 93.4461 | 95.6865 | 96.4109 | 96.8452 | 96.8125 | 96.6488 | 96.572 | 2021-11-12 | 2023-12-11
GoodWe Technologies Co., Ltd. | GW7000A-BP {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 7.059 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.48 |  |  | 200 | 350 | 495 | 0.7059 | 1.4118 | 2.1177 | 3.5295 | 5.2942 | 7.059 | 94.1624 | 95.6808 | 96.2387 | 96.4556 | 96.2632 | 96.0229 | 96.1755 | 94.8837 | 96.3856 | 96.6968 | 96.9955 | 97.0411 | 96.7889 | 96.8585 | 93.4461 | 95.6865 | 96.4109 | 96.8452 | 96.8125 | 96.6488 | 96.572 | 2021-01-21 | 2023-12-11
GoodWe Technologies Co., Ltd. | GEC7.6-1U-US20 {240V} | N | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, with PCS functionality. | 7.5855 | 240 | 96 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.61 |  |  | 158 | 300 | 495 | 0.75855 | 1.5171 | 2.2756 | 3.7927 | 5.6891 | 7.5855 | 93.5571 | 95.2629 | 95.6457 | 96.3743 | 95.8329 | 94.9829 | 95.7621 | 94.7457 | 95.6714 | 96.3529 | 96.2671 | 96.5757 | 96.8329 | 96.3786 | 94.4143 | 95.3957 | 96.0771 | 96.15 | 95.9786 | 95.6943 | 95.9205 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW7600-SBP-US20 {240V} | N | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, with PCS functionality. | 7.5855 | 240 | 96 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.61 |  |  | 158 | 300 | 495 | 0.75855 | 1.5171 | 2.2756 | 3.7927 | 5.6891 | 7.5855 | 93.5571 | 95.2629 | 95.6457 | 96.3743 | 95.8329 | 94.9829 | 95.7621 | 94.7457 | 95.6714 | 96.3529 | 96.2671 | 96.5757 | 96.8329 | 96.3786 | 94.4143 | 95.3957 | 96.0771 | 96.15 | 95.9786 | 95.6943 | 95.9205 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEH7.6-1U-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 7.5882 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 180 | 390 | 500 | 0.75882 | 1.5176 | 2.2765 | 3.7941 | 5.6911 | 7.5882 | 94.8629 | 96.1257 | 96.6114 | 96.8586 | 96.7071 | 96.0729 | 96.5929 | 95.9643 | 97.0057 | 97.6957 | 97.6157 | 97.45 | 97.29 | 97.4246 | 95.6529 | 96.9743 | 97.35 | 97.3486 | 97.2 | 96.8929 | 97.1607 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW7600-ES-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 7.5882 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 180 | 390 | 500 | 0.75882 | 1.5176 | 2.2765 | 3.7941 | 5.6911 | 7.5882 | 94.8629 | 96.1257 | 96.6114 | 96.8586 | 96.7071 | 96.0729 | 96.5929 | 95.9643 | 97.0057 | 97.6957 | 97.6157 | 97.45 | 97.29 | 97.4246 | 95.6529 | 96.9743 | 97.35 | 97.3486 | 97.2 | 96.8929 | 97.1607 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEH7.6-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.644 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.44 |  |  | 230 | 400 | 480 | 0.7644 | 1.5288 | 2.2932 | 3.822 | 5.733 | 7.644 | 94.8643 | 96.15 | 96.5255 | 96.6841 | 96.4443 | 96.1981 | 96.4142 | 96.2197 | 97.3623 | 97.6532 | 97.6811 | 97.5297 | 97.2607 | 97.5021 | 95.6202 | 97.0112 | 97.3977 | 97.5881 | 97.4473 | 97.198 | 97.3636 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW7600A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.644 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.44 |  |  | 230 | 400 | 480 | 0.7644 | 1.5288 | 2.2932 | 3.822 | 5.733 | 7.644 | 94.8643 | 96.15 | 96.5255 | 96.6841 | 96.4443 | 96.1981 | 96.4142 | 96.2197 | 97.3623 | 97.6532 | 97.6811 | 97.5297 | 97.2607 | 97.5021 | 95.6202 | 97.0112 | 97.3977 | 97.5881 | 97.4473 | 97.198 | 97.3636 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEC7.6-1U-US10 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 7.648 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.48 |  |  | 200 | 350 | 495 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.736 | 7.648 | 94.2091 | 95.7971 | 96.2502 | 96.4508 | 96.086 | 95.8884 | 96.0829 | 95.3028 | 96.2388 | 96.7456 | 96.9702 | 96.8508 | 96.6381 | 96.7601 | 93.7819 | 95.8515 | 96.4641 | 96.8137 | 96.743 | 96.552 | 96.5518 | 2021-11-12 | 2023-12-11
GoodWe Technologies Co., Ltd. | GW7600A-BP {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 7.648 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.48 |  |  | 200 | 350 | 495 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.736 | 7.648 | 94.2091 | 95.7971 | 96.2502 | 96.4508 | 96.086 | 95.8884 | 96.0829 | 95.3028 | 96.2388 | 96.7456 | 96.9702 | 96.8508 | 96.6381 | 96.7601 | 93.7819 | 95.8515 | 96.4641 | 96.8137 | 96.743 | 96.552 | 96.5518 | 2021-01-21 | 2023-12-11
GoodWe Technologies Co., Ltd. | GEH8.6-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.614 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.54 |  |  | 260 | 400 | 480 | 0.8614 | 1.7228 | 2.5842 | 4.307 | 6.4605 | 8.614 | 95.3737 | 96.4874 | 96.7887 | 96.8743 | 96.5976 | 96.3068 | 96.6096 | 96.4937 | 97.4708 | 97.6603 | 97.6447 | 97.424 | 97.1058 | 97.4479 | 95.8593 | 97.1544 | 97.4506 | 97.5009 | 97.321 | 97.0125 | 97.2921 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW8600A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.614 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.54 |  |  | 260 | 400 | 480 | 0.8614 | 1.7228 | 2.5842 | 4.307 | 6.4605 | 8.614 | 95.3737 | 96.4874 | 96.7887 | 96.8743 | 96.5976 | 96.3068 | 96.6096 | 96.4937 | 97.4708 | 97.6603 | 97.6447 | 97.424 | 97.1058 | 97.4479 | 95.8593 | 97.1544 | 97.4506 | 97.5009 | 97.321 | 97.0125 | 97.2921 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEC8.6-1U-US10 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 8.68 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.47 |  |  | 200 | 350 | 495 | 0.868 | 1.736 | 2.604 | 4.34 | 6.51 | 8.68 | 94.6958 | 96.0043 | 96.3343 | 96.3371 | 96.0115 | 95.6796 | 96.049 | 95.7573 | 96.48 | 96.9605 | 97.0225 | 96.9106 | 96.6148 | 96.8576 | 94.6422 | 96.0768 | 96.4605 | 96.7395 | 96.7564 | 96.5087 | 96.5864 | 2021-11-12 | 2023-12-11
GoodWe Technologies Co., Ltd. | GW8600A-BP {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 8.68 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.47 |  |  | 200 | 350 | 495 | 0.868 | 1.736 | 2.604 | 4.34 | 6.51 | 8.68 | 94.6958 | 96.0043 | 96.3343 | 96.3371 | 96.0115 | 95.6796 | 96.049 | 95.7573 | 96.48 | 96.9605 | 97.0225 | 96.9106 | 96.6148 | 96.8576 | 94.6422 | 96.0768 | 96.4605 | 96.7395 | 96.7564 | 96.5087 | 96.5864 | 2021-01-21 | 2023-12-11
GoodWe Technologies Co., Ltd. | GEH9.6-1U-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 9.5862 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 225 | 390 | 500 | 0.95862 | 1.9172 | 2.8759 | 4.7931 | 7.1897 | 9.5862 | 95.3614 | 96.4043 | 96.9143 | 97.0186 | 96.8414 | 96.36 | 96.7822 | 96.0729 | 97.21 | 97.52 | 97.59 | 97.2314 | 97.05 | 97.2849 | 95.8657 | 97.0657 | 97.39 | 97.3929 | 97.0029 | 96.67 | 97.0722 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW9600-ES-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 9.5862 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 225 | 390 | 500 | 0.95862 | 1.9172 | 2.8759 | 4.7931 | 7.1897 | 9.5862 | 95.3614 | 96.4043 | 96.9143 | 97.0186 | 96.8414 | 96.36 | 96.7822 | 96.0729 | 97.21 | 97.52 | 97.59 | 97.2314 | 97.05 | 97.2849 | 95.8657 | 97.0657 | 97.39 | 97.3929 | 97.0029 | 96.67 | 97.0722 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEC9.6-1U-US20 {240V} | N | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, with PCS functionality. | 9.6031 | 240 | 96 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.61 |  |  | 200 | 300 | 495 | 0.96031 | 1.9206 | 2.8809 | 4.8015 | 7.2023 | 9.6031 | 93.6829 | 95.3486 | 95.6429 | 96.47 | 95.9143 | 95.2143 | 95.8459 | 94.49 | 95.9371 | 96.2043 | 96.16 | 96.8057 | 96.4157 | 96.4424 | 94.3943 | 96.0357 | 96.3371 | 96.3786 | 96.1443 | 96.5543 | 96.1617 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW9600-SBP-US20 {240V} | N | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, with PCS functionality. | 9.6031 | 240 | 96 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.61 |  |  | 200 | 300 | 495 | 0.96031 | 1.9206 | 2.8809 | 4.8015 | 7.2023 | 9.6031 | 93.6829 | 95.3486 | 95.6429 | 96.47 | 95.9143 | 95.2143 | 95.8459 | 94.49 | 95.9371 | 96.2043 | 96.16 | 96.8057 | 96.4157 | 96.4424 | 94.3943 | 96.0357 | 96.3371 | 96.3786 | 96.1443 | 96.5543 | 96.1617 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEC9.6-1U-US10 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 9.616 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.5 |  |  | 200 | 350 | 495 | 0.9616 | 1.9232 | 2.8848 | 4.808 | 7.212 | 9.616 | 95.0112 | 96.1034 | 96.3344 | 96.288 | 95.8601 | 95.4093 | 95.9626 | 95.7041 | 96.6346 | 96.9842 | 96.9505 | 96.7684 | 96.4098 | 96.7653 | 95.0504 | 96.1493 | 96.569 | 96.7048 | 96.6938 | 96.4008 | 96.5735 | 2021-11-12 | 2023-12-11
GoodWe Technologies Co., Ltd. | GW9600A-BP {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 9.616 | 240 | 96.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.5 |  |  | 200 | 350 | 495 | 0.9616 | 1.9232 | 2.8848 | 4.808 | 7.212 | 9.616 | 95.0112 | 96.1034 | 96.3344 | 96.288 | 95.8601 | 95.4093 | 95.9626 | 95.7041 | 96.6346 | 96.9842 | 96.9505 | 96.7684 | 96.4098 | 96.7653 | 95.0504 | 96.1493 | 96.569 | 96.7048 | 96.6938 | 96.4008 | 96.5735 | 2021-01-21 | 2023-12-11
GoodWe Technologies Co., Ltd. | GEH9.6-1U-US10 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 9.628 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-11-12 | [09/17/2021] | 2021-11-12 | CSA Group | 2021-11-01 | 2021-11-12 |  | N | N | 9.4 |  |  | 300 | 400 | 480 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7607 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 97.378 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369 | 97.2329 | 2021-11-12 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW9600A-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 9.628 | 240 | 97 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 |  | N | N | 9.4 |  |  | 300 | 400 | 480 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7607 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 97.378 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369 | 97.2329 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GW9600H-ES {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9.6 kW, 240 Vac, Bi-directional Grid Support Utility Interactive PV and Battery Inverter | 9.628 | 240 | 95.5 | CSA Group | [11/30/2021] | CSA Group | [09/17/2021] | [05] | 2021-01-21 | [09/17/2021] | 2021-01-21 | CSA Group | 2020-11-17 | 2021-01-21 | Efficiency data includes external Isolation transformer GW9600G-TF effect. | N | N | 45.22 |  |  | 300 | 400 | 480 | 0.9519 | 1.9038 | 2.8557 | 4.7595 | 7.1393 | 9.519 | 92.2072 | 94.7398 | 95.3899 | 95.5471 | 95.1557 | 94.5552 | 95.0973 | 93.0285 | 95.4529 | 96.0211 | 96.1062 | 95.7384 | 95.1732 | 95.6986 | 92.6051 | 95.1829 | 95.7232 | 95.9558 | 95.6413 | 94.9918 | 95.5403 | 2021-01-21 | 2023-02-13
GoodWe Technologies Co., Ltd. | GEH11.4-1U-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 11.3793 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 270 | 390 | 500 | 1.1379 | 2.2759 | 3.4138 | 5.6896 | 8.5345 | 11.3793 | 95.6314 | 96.44 | 96.7957 | 97.0514 | 96.98 | 96.7171 | 96.8788 | 96.49 | 97.4429 | 97.5329 | 97.4414 | 97.2029 | 96.98 | 97.2649 | 96.2414 | 97.1871 | 97.2243 | 97.1386 | 96.99 | 96.3657 | 96.998 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW11K4-ES-US20 {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter, with PCS functionality. | 11.3793 | 240 | 97 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.62 |  |  | 270 | 390 | 500 | 1.1379 | 2.2759 | 3.4138 | 5.6896 | 8.5345 | 11.3793 | 95.6314 | 96.44 | 96.7957 | 97.0514 | 96.98 | 96.7171 | 96.8788 | 96.49 | 97.4429 | 97.5329 | 97.4414 | 97.2029 | 96.98 | 97.2649 | 96.2414 | 97.1871 | 97.2243 | 97.1386 | 96.99 | 96.3657 | 96.998 | 2023-01-23
GoodWe Technologies Co., Ltd. | GEC11.4-1U-US20 {240V} | N | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, with PCS functionality. | 11.3919 | 240 | 96 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.61 |  |  | 235 | 300 | 495 | 1.1392 | 2.2784 | 3.4176 | 5.6959 | 8.5439 | 11.3919 | 94.32 | 95.6357 | 95.7729 | 96.4757 | 95.7914 | 95.1371 | 95.8335 | 95.15 | 96.1857 | 96.27 | 96.0443 | 96.5486 | 96.0214 | 96.3088 | 94.5386 | 96.0657 | 96.2914 | 96.2114 | 95.8529 | 96.2186 | 95.9571 | 2023-01-23
GoodWe Technologies Co., Ltd. | GW11K4-SBP-US20 {240V} | N | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, with PCS functionality. | 11.3919 | 240 | 96 | CSA Group | [7/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2022-08-26 | 2023-01-23 |  | N | N | 5.61 |  |  | 235 | 300 | 495 | 1.1392 | 2.2784 | 3.4176 | 5.6959 | 8.5439 | 11.3919 | 94.32 | 95.6357 | 95.7729 | 96.4757 | 95.7914 | 95.1371 | 95.8335 | 95.15 | 96.1857 | 96.27 | 96.0443 | 96.5486 | 96.0214 | 96.3088 | 94.5386 | 96.0657 | 96.2914 | 96.2114 | 95.8529 | 96.2186 | 95.9571 | 2023-01-23
Green Solutions (Chengdu) Co., Ltd | H12K-US {208V} | Y | Y | N | N | N | N | N | N | 12 kW, 208 Vac Grid Support Interactive Hybrid Inverter | 10.49 | 208 | 96.5 | Intertek | [3/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.05 | 2.1 | 3.15 | 5.25 | 7.875 | 10.499 | 93.48 | 95.27 | 95.93 | 95.85 | 95.61 | 95.29 | 95.58 | 95.07 | 96.66 | 97.03 | 97.31 | 97.1 | 96.41 | 96.99 | 94.29 | 96.71 | 97.16 | 96.95 | 96.77 | 96.47 | 96.74 | 2024-05-21
Green Solutions (Chengdu) Co., Ltd | H12K-US {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Interactive Hybrid Inverter | 11.93 | 240 | 97 | Intertek | [3/4/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.193 | 2.387 | 3.58 | 5.966 | 8.949 | 11.933 | 95.02 | 96.1 | 96.54 | 96.5 | 96.13 | 95.9 | 96.2 | 96.59 | 97.19 | 97.51 | 97.34 | 97.24 | 97.1 | 97.26 | 95.82 | 97.01 | 97.42 | 97.26 | 97.14 | 97.04 | 97.13 | 2024-05-21
Gridwiz Co., Ltd | Gridwiz-PCS 300 {380V} | N | Y | N | N | N | N | N |  | 300.42 kW, 380 Vac Grid Support Utility Interactive Inverter | 300.42 | 380 | 97.5 | TUV SUD | [9/20/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 16.7 |  |  | 640 | 870 | 1100 | 30.042 | 60.084 | 90.126 | 150.21 | 225.315 | 300.42 | 95.17 | 97.07 | 97.62 | 97.43 | 97.53 | 97.48 | 97.4 | 89.01 | 93.65 | 95.37 | 96.51 | 96.9 | 96.93 | 96.16 | 90.37 | 94.36 | 95.71 | 96.68 | 97.02 | 97.07 | 96.39 | 2025-12-01
Guangzhou Sanjing Electric Co., Ltd. | H2-5K-LS3-US {208V} | Y | Y | N | N | N | N | N | N | 4.4 kW, 208Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 4.363 | 208 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N |  |  |  | 190 | 380 | 510 | 0.436 | 0.873 | 1.309 | 2.181 | 3.272 | 4.363 | 89.13 | 93.12 | 95.34 | 96.49 | 96.89 | 96.68 | 96.11 | 90.68 | 93.87 | 96 | 96.7 | 97.28 | 96.45 | 96.53 | 88.88 | 93.04 | 95.55 | 96.82 | 97.13 | 97.08 | 96.34 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-5K-LS3-US {240V} | Y | Y | N | N | N | N | N | N | 5.0 kW, 240Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 5.067 | 240 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N |  |  |  | 190 | 380 | 510 | 0.507 | 1.013 | 1.52 | 2.534 | 3.8 | 5.067 | 89.8 | 93.15 | 95.17 | 96.61 | 96.96 | 97.01 | 96.2 | 90.59 | 94.59 | 96.74 | 96.99 | 97.27 | 97.23 | 96.75 | 89.47 | 93 | 95.78 | 96.73 | 97.18 | 97.13 | 96.4 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-7.6K-S3-US {208V} | Y | Y | N | N | N | N | N | N | 6.6 kW, 208 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 6.605 | 208 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.1 |  |  | 200 | 380 | 550 | 0.66054 | 1.3211 | 1.9816 | 3.3027 | 4.954 | 6.6054 | 91.2646 | 94.8961 | 96.1247 | 96.9883 | 97.1549 | 96.7701 | 96.6285 | 92.3867 | 96.0621 | 97.2134 | 97.6384 | 97.5579 | 97.5114 | 97.2495 | 90.7261 | 94.6534 | 96.0471 | 96.9029 | 97.328 | 97.3169 | 96.6867 | 2023-03-13
Guangzhou Sanjing Electric Co., Ltd. | H2-7.6K-LS3-US {208V} | Y | Y | N | N | N | N | N | N | 6.6 kW, 208Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 6.609 | 208 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N |  |  |  | 190 | 380 | 510 | 0.661 | 1.322 | 1.983 | 3.305 | 4.957 | 6.609 | 90.83 | 93.44 | 95.36 | 96.26 | 96.98 | 96.91 | 96.21 | 91.46 | 94.71 | 96.1 | 97.02 | 97.33 | 97.32 | 96.75 | 90.1 | 93.69 | 95.46 | 96.43 | 97.13 | 97.14 | 96.33 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-7.6K-S3-US {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 7.606 | 240 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.1 |  |  | 200 | 380 | 550 | 0.76061 | 1.5212 | 2.2818 | 3.803 | 5.7046 | 7.6061 | 91.6757 | 95.0333 | 96.06 | 96.9014 | 97.0114 | 96.8343 | 96.553 | 93.3129 | 96.5629 | 96.8173 | 97.5543 | 97.7557 | 97.6629 | 97.3588 | 89.9229 | 94.5157 | 95.957 | 96.9959 | 97.4427 | 97.3929 | 96.721 | 2023-03-13
Guangzhou Sanjing Electric Co., Ltd. | H2-7.6K-LS3-US {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 7.61 | 240 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N |  |  |  | 190 | 380 | 510 | 0.761 | 1.522 | 2.283 | 3.805 | 5.708 | 7.61 | 90.19 | 93.39 | 95.24 | 95.94 | 96.48 | 96.51 | 95.82 | 91.29 | 95.55 | 96.58 | 97.22 | 97.41 | 97.24 | 96.92 | 91.16 | 94.6 | 96.13 | 96.79 | 97.35 | 97.19 | 96.69 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-9.6K-LS4-US {208V} | Y | Y | N | N | N | N | N | N | 8.3 kW, 208Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 8.316 | 208 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N |  |  |  | 190 | 380 | 510 | 0.832 | 1.663 | 2.495 | 4.158 | 6.237 | 8.316 | 90.63 | 93.84 | 95.22 | 96.21 | 96.23 | 96.19 | 95.76 | 91.43 | 94.79 | 96.31 | 97.12 | 97.29 | 97.28 | 96.78 | 89.48 | 93.84 | 95.64 | 96.44 | 97.09 | 97.12 | 96.32 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-10K-S4-US {208V} | Y | Y | N | N | N | N | N | N | 8.8 kW, 208 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 8.798 | 208 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.9 |  |  | 200 | 380 | 550 | 0.87978 | 1.7596 | 2.6394 | 4.3989 | 6.5984 | 8.7978 | 91.9266 | 94.9857 | 95.9901 | 96.6531 | 96.7526 | 96.5514 | 96.3488 | 93.3406 | 96.2684 | 97.2293 | 97.7784 | 97.8737 | 97.7571 | 97.509 | 90.1603 | 94.3034 | 95.8667 | 96.8204 | 97.1063 | 97.1454 | 96.4815 | 2023-03-13
Guangzhou Sanjing Electric Co., Ltd. | H2-9.6K-LS4-US {240V} | Y | Y | N | N | N | N | N | N | 9.6 kW, 240Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 9.605 | 240 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N |  |  |  | 190 | 380 | 510 | 0.96 | 1.921 | 2.881 | 4.802 | 7.204 | 9.605 | 90.78 | 94.02 | 94.95 | 96.2 | 96.55 | 96.62 | 95.93 | 91.87 | 95.28 | 96.52 | 97.45 | 97.38 | 97.25 | 96.96 | 89.9 | 94.28 | 95.82 | 97.23 | 97.04 | 97.03 | 96.51 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-11.4K-LS4-US {208V} | Y | Y | N | N | N | N | N | N | 9.9 kW, 208Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 9.881 | 208 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N |  |  |  | 190 | 380 | 510 | 0.988 | 1.976 | 2.964 | 4.94 | 7.411 | 9.881 | 91.26 | 94.37 | 95.55 | 96.31 | 96.34 | 96 | 95.92 | 92.71 | 95.49 | 96.99 | 97.27 | 97.31 | 97.15 | 96.98 | 90.94 | 94.23 | 96.38 | 97.13 | 97.29 | 97.2 | 96.74 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-10K-S4-US {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 10.089 | 240 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3 |  |  | 200 | 380 | 550 | 1.0089 | 2.0179 | 3.0268 | 5.0447 | 7.5671 | 10.0894 | 92.505 | 95.285 | 96.1289 | 96.6833 | 96.757 | 96.5369 | 96.4115 | 93.3783 | 96.0274 | 96.8706 | 97.488 | 97.6233 | 97.8881 | 97.2682 | 91.7759 | 95.115 | 96.252 | 97.1056 | 97.3409 | 97.2843 | 96.8241 | 2023-03-13
Guangzhou Sanjing Electric Co., Ltd. | H2-12K-S4-US {208V} | Y | Y | N | N | N | N | N | N | 10.4 kW, 208 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 10.417 | 208 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.8 |  |  | 200 | 380 | 550 | 1.0417 | 2.0833 | 3.125 | 5.2084 | 7.8126 | 10.4167 | 92.9157 | 95.6341 | 96.2164 | 96.654 | 96.3786 | 96.1233 | 96.2285 | 94.2331 | 96.697 | 97.4084 | 97.7706 | 97.7253 | 97.5054 | 97.4947 | 91.3866 | 95.1003 | 96.1777 | 96.8868 | 97.0123 | 96.3247 | 96.5308 | 2023-03-13
Guangzhou Sanjing Electric Co., Ltd. | H2-11.4K-LS4-US {240V} | Y | Y | N | N | N | N | N | N | 11.3 kW, 240Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 11.298 | 240 | 96.5 | Intertek | [9/10/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N |  |  |  | 190 | 380 | 510 | 1.13 | 2.26 | 3.389 | 5.649 | 8.474 | 11.298 | 92.02 | 94.77 | 95.72 | 96.39 | 96.3 | 96.18 | 95.99 | 93.01 | 95.73 | 96.74 | 97.43 | 97.37 | 97.36 | 97.05 | 91.95 | 95.01 | 96.59 | 97.29 | 97.19 | 97.21 | 96.82 | 2025-03-21
Guangzhou Sanjing Electric Co., Ltd. | H2-12K-S4-US {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Bi-directional Transformerless Hybrid Grid Support Utility Interactive Inverter | 12.034 | 240 | 97 | CSA Group | [12/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.2 |  |  | 200 | 380 | 550 | 1.2034 | 2.4068 | 3.6103 | 6.0171 | 9.0257 | 12.0342 | 93.1914 | 95.6541 | 96.3079 | 96.6811 | 96.526 | 96.1971 | 96.339 | 93.908 | 96.3353 | 97.0489 | 97.4993 | 97.4757 | 97.2611 | 97.219 | 92.4186 | 95.4427 | 96.5387 | 97.1697 | 97.2534 | 97.11 | 96.859 | 2023-03-13
Hangzhou Boco Electronics Co., Ltd. | P115SJ240-2001FT-00 {240V} | N | Y | N | N | N | N | N |  | 2.20 kW, 240 Vac Grid Support Utility Interactive Inverter | 2.198 | 240 | 94.5 | CSA Group | [7/9/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 4.11 |  |  | 105 | 115 | 128 | 0.22 | 0.44 | 0.66 | 1.099 | 1.649 | 2.198 | 88.2 | 92.34 | 93.73 | 95.12 | 95.49 | 95.22 | 94.74 | 86.99 | 91.8 | 93.39 | 94.8 | 95.34 | 95.35 | 94.48 | 85.42 | 91.01 | 92.9 | 94.24 | 95.13 | 95.34 | 94.09 | 2026-09-01 |  | N | N | Y | N | N | N | Y | N | N
Hitachi Energy Power Conversion Solutions S.L.U | MP2Ms2.3BsWD3-V850 {850V} | Y | Y | N | N | N | N | N |  | 1304.52 kW, 850 Vac Grid Support Utility Interactive Inverter with external transformer. (made up of two 1MsWD3-V850 installed together rated max output power = 2,609kW) | 1304.52 | 850 | 98.5 | SGS | [4/6/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | Y | N | 181.5592 |  |  | 1216 | 1310 | 1500 | 130.452 | 260.904 | 391.356 | 652.26 | 978.39 | 1304.52 | 97.4306 | 98.241 | 98.5415 | 98.5348 | 98.2694 | 98.0394 | 98.3113 | 97.3156 | 98.2211 | 98.5166 | 98.4941 | 98.2684 | 97.9794 | 98.2906 | 97.1603 | 98.0934 | 98.498 | 98.4325 | 98.2143 | 97.9187 | 98.2312 | 2026-10-12 |  | Y | N | N | N | N | N | Y | N | No Information Submitted
Holu Hou Energy LLC | HH9600H-HI {240V} | Y | N | Y | Y | Y | N | N | N | 9.6 KW, 240 Vac Non-isolated Grid Support Utility Interactive Hybrid Inverter | 9.628 | 240 | 97 | No Information Submitted | No Information Submitted | CSA Group | [5/20/2020] | [00, 13] | 2023-03-13 | [5/20/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | This model number can also be configured as an Isolated Inverter with Isolation Transformer HH9600H-IT which changes the overal weighted efficiency to 95.5% and night tare loss to 45.22 W. | Y | N | 9.4 |  |  | 300 | 400 | 480 | 0.9628 | 1.9256 | 2.8884 | 4.814 | 7.221 | 9.628 | 95.8361 | 96.8121 | 97.0582 | 97.004 | 96.7022 | 96.3329 | 96.7607 | 96.7134 | 97.5372 | 97.6589 | 97.5753 | 97.3115 | 96.9524 | 97.378 | 96.1531 | 97.2748 | 97.5216 | 97.4456 | 97.1983 | 96.8369 | 97.2329 | 2023-03-13
Hongyibo New Energy Technology (Shenzhen) Co., Ltd. | PCSR5KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac, Grid Support Utility Inverter with PCS functionality. | 5.0897 | 240 | 97 | SGS | [2/24/2025] | SGS | [2/24/2025] | [V1.04.06(DSP), V1.03.03(ARM)] | 2025-06-11 | [2/24/2025] | 2025-06-11 | SGS | 2025-03-14 | 2025-06-11 |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2025-06-11
Hongyibo New Energy Technology (Shenzhen) Co., Ltd. | PCSR6KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac, Grid Support Utility Inverter with PCS functionality. | 6.1172 | 240 | 97 | SGS | [2/24/2025] | SGS | [2/24/2025] | [V1.04.06(DSP), V1.03.03(ARM)] | 2025-06-11 | [2/24/2025] | 2025-06-11 | SGS | 2025-03-14 | 2025-06-11 |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2025-06-11
Hongyibo New Energy Technology (Shenzhen) Co., Ltd. | PCSR7K6LNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Grid Support Utility Inverter with PCS functionality. | 7.7647 | 240 | 97 | SGS | [2/24/2025] | SGS | [2/24/2025] | [V1.04.06(DSP), V1.03.03(ARM)] | 2025-06-11 | [2/24/2025] | 2025-06-11 | SGS | 2025-03-14 | 2025-06-11 |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2025-06-11
Hongyibo New Energy Technology (Shenzhen) Co., Ltd. | PCSR8KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.0 kW, 240 Vac, Grid Support Utility Inverter with PCS functionality. | 8.0842 | 240 | 97.5 | SGS | [2/24/2025] | SGS | [2/24/2025] | [V1.04.06(DSP), V1.03.03(ARM)] | 2025-06-11 | [2/24/2025] | 2025-06-11 | SGS | 2025-03-14 | 2025-06-11 |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2025-06-11
Hongyibo New Energy Technology (Shenzhen) Co., Ltd. | PCSR10KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.0 kW, 240 Vac, Grid Support Utility Inverter with PCS functionality. | 10.1767 | 240 | 97 | SGS | [2/24/2025] | SGS | [2/24/2025] | [V1.04.06(DSP), V1.03.03(ARM)] | 2025-06-11 | [2/24/2025] | 2025-06-11 | SGS | 2025-03-14 | 2025-06-11 |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2025-06-11
Hoymiles Power Electronics Inc. | HAS-3.8LV-USG1 {240V} | N | Y | N | N | N | N | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 3.646 | 240 | 93.5 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 5.9865 |  |  | 50 | 55 | 60 | 0.36458 | 0.72917 | 1.0938 | 1.8229 | 2.7344 | 3.6458 | 86.5163 | 91.2176 | 92.49 | 93.4093 | 94.3077 | 94.3895 | 93.4389 | 86.7334 | 91.3865 | 92.5999 | 93.4714 | 94.6891 | 94.9028 | 93.71 | 86.382 | 90.9812 | 92.3206 | 93.1604 | 94.4387 | 95.0493 | 93.4515 | 2024-02-01 | 2024-08-12
Hoymiles Power Electronics Inc. | HYS-3.8LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 3.796 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 6.0401 |  |  | 300 | 380 | 480 | 0.37958 | 0.75916 | 1.1387 | 1.8979 | 2.8468 | 3.7958 | 92.5517 | 95.5966 | 96.419 | 96.9105 | 97.0723 | 97.0287 | 96.7032 | 93.2466 | 96.7006 | 97.2174 | 97.4939 | 97.5869 | 97.5544 | 97.3035 | 93.268 | 96.0331 | 96.8384 | 97.1796 | 97.3381 | 97.3158 | 97.0157 | 2024-02-01 | 2025-08-01
Hoymiles Power Electronics Inc. | HAS-4.8LV-USG1 {240V} | N | Y | N | N | N | N | Y* | Y | 4.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.559 | 240 | 94 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 5.9872 |  |  | 50 | 55 | 60 | 0.45589 | 0.91177 | 1.3677 | 2.2794 | 3.4191 | 4.5589 | 88.3212 | 92.0282 | 92.8887 | 93.8461 | 94.3405 | 93.9889 | 93.6885 | 88.7536 | 92.1459 | 93.0233 | 93.8138 | 94.894 | 94.7936 | 94.0546 | 88.4121 | 91.8474 | 92.7843 | 93.486 | 94.9956 | 95.0424 | 93.9948 | 2024-02-01 | 2024-08-12
Hoymiles Power Electronics Inc. | HAS-6.0LV-USG1 {240V} | N | Y | N | N | N | N | Y* | Y | 6.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.559 | 240 | 94 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 5.9872 |  |  | 50 | 55 | 60 | 0.45589 | 0.91177 | 1.3677 | 2.2794 | 3.4191 | 4.5589 | 88.3212 | 92.0282 | 92.8887 | 93.8461 | 94.3405 | 93.9889 | 93.6885 | 88.7536 | 92.1459 | 93.0233 | 93.8138 | 94.894 | 94.7936 | 94.0546 | 88.4121 | 91.8474 | 92.7843 | 93.486 | 94.9956 | 95.0424 | 93.9948 | 2024-02-01 | 2024-08-12
Hoymiles Power Electronics Inc. | HYS-4.8LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 4.8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 4.793 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 5.7606 |  |  | 300 | 380 | 480 | 0.47929 | 0.95858 | 1.4379 | 2.3964 | 3.5947 | 4.7929 | 94.0767 | 96.1362 | 96.6912 | 97.0212 | 97.0575 | 96.9337 | 96.8344 | 95.4316 | 97.1034 | 97.3546 | 97.5695 | 97.5695 | 97.4739 | 97.4301 | 94.3738 | 96.5934 | 96.9723 | 97.2727 | 97.3154 | 97.2367 | 97.1075 | 2024-02-01 | 2025-08-01
Hoymiles Power Electronics Inc. | HYS-6.0LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 6.0 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 5.995 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 5.8237 |  |  | 300 | 380 | 480 | 0.59951 | 1.199 | 1.7985 | 2.9976 | 4.4963 | 5.9951 | 94.8234 | 96.5478 | 96.8698 | 97.0713 | 96.9873 | 96.7883 | 96.8723 | 96.0891 | 97.2705 | 97.4671 | 97.5855 | 97.504 | 97.3496 | 97.4407 | 95.3019 | 96.89 | 97.1313 | 97.3238 | 97.2572 | 97.1052 | 97.1519 | 2024-02-01 | 2025-08-01
Hoymiles Power Electronics Inc. | HAS-7.6LV-USG1 {240V} | N | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.417 | 240 | 94 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 6.6685 |  |  | 50 | 55 | 60 | 0.7417 | 1.4834 | 2.2251 | 3.7085 | 5.5627 | 7.417 | 89.5505 | 92.2808 | 93.1499 | 93.7139 | 94.2128 | 94.1368 | 93.6936 | 89.9118 | 92.676 | 93.3696 | 93.9571 | 94.7302 | 94.8552 | 94.1154 | 89.3113 | 92.0912 | 92.9419 | 93.3646 | 94.391 | 94.8099 | 93.7043 | 2024-02-01 | 2024-08-12
Hoymiles Power Electronics Inc. | HYS-7.6LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 7.708 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 6.1397 |  |  | 300 | 380 | 480 | 0.77079 | 1.5416 | 2.3124 | 3.8539 | 5.7809 | 7.7079 | 94.8322 | 96.4779 | 96.907 | 97.1091 | 97.0333 | 96.6304 | 96.8981 | 96.482 | 97.3997 | 97.6208 | 97.6611 | 97.5217 | 97.3094 | 97.5045 | 95.5348 | 96.8788 | 97.1848 | 97.3224 | 97.2171 | 97.0689 | 97.1437 | 2024-02-01 | 2025-08-01
Hoymiles Power Electronics Inc. | HAS-11.5LV-USG1 {240V} | N | Y | N | N | N | N | Y* | Y | 11.5 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.153 | 240 | 94 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 6.6 |  |  | 50 | 55 | 60 | 0.91525 | 1.8305 | 2.7458 | 4.5763 | 6.8644 | 9.1525 | 90.4351 | 92.6478 | 93.3604 | 93.7836 | 94.0257 | 93.4137 | 93.6519 | 90.6645 | 92.8724 | 93.4875 | 94.0118 | 94.5607 | 94.227 | 94.0597 | 90.0627 | 92.4067 | 93.0712 | 93.4128 | 94.7249 | 94.5805 | 93.9413 | 2024-02-01 | 2024-08-12
Hoymiles Power Electronics Inc. | HAS-9.6LV-USG1 {240V} | N | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.153 | 240 | 94 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 6.6 |  |  | 50 | 55 | 60 | 0.91525 | 1.8305 | 2.7458 | 4.5763 | 6.8644 | 9.1525 | 90.4351 | 92.6478 | 93.3604 | 93.7836 | 94.0257 | 93.4137 | 93.6519 | 90.6645 | 92.8724 | 93.4875 | 94.0118 | 94.5607 | 94.227 | 94.0597 | 90.0627 | 92.4067 | 93.0712 | 93.4128 | 94.7249 | 94.5805 | 93.9413 | 2024-02-01 | 2024-08-12
Hoymiles Power Electronics Inc. | HYS-9.6LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 9.641 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 6.8588 |  |  | 300 | 380 | 480 | 0.96413 | 1.9283 | 2.8924 | 4.8206 | 7.231 | 9.6413 | 95.7062 | 96.8422 | 97.1011 | 97.1182 | 96.9178 | 96.4094 | 96.9042 | 96.6936 | 97.4649 | 97.6066 | 97.5483 | 97.3476 | 97.0572 | 97.386 | 96.301 | 97.1806 | 97.3628 | 97.3361 | 97.1168 | 96.8368 | 97.149 | 2024-02-01 | 2025-08-01
Hoymiles Power Electronics Inc. | HYS-11.5LV-USG1 {240V} | Y | Y | N | N | N | N | Y* | Y | 11.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 11.575 | 240 | 97 | CSA Group | [10/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-05-10 | 2024-08-12 |  | N | N | 6.6304 |  |  | 300 | 380 | 480 | 1.1575 | 2.3151 | 3.4726 | 5.7877 | 8.6815 | 11.5754 | 95.9907 | 97.1161 | 97.298 | 97.2213 | 96.8983 | 96.5184 | 96.9697 | 97.1958 | 97.7715 | 97.7755 | 97.4974 | 97.2422 | 96.8577 | 97.3652 | 96.6169 | 97.42 | 97.5383 | 97.4007 | 97.0634 | 96.7187 | 97.174 | 2024-02-01 | 2025-08-01
Huizhou Roypow Technology Co., Ltd | SUN10000S-U {240V} | Y | Y | N | N | N | N | Y* | Y | 10.111 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.111 | 240 | 95.5 | CSA Group | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-10-17 | 2025-01-02 |  | N | N | 36.53 |  |  | 200 | 300 | 440 | 1.011 | 2.022 | 3.033 | 5.055 | 7.583 | 10.111 | 90.13 | 93.91 | 95.02 | 95.42 | 95.26 | 94.75 | 94.97 | 90.3 | 94.11 | 95.3 | 96.04 | 95.95 | 95.76 | 95.56 | 89.9 | 94.14 | 95.42 | 96.26 | 96.36 | 96.21 | 95.85 | 2024-08-01 | 2025-01-02
Huizhou Roypow Technology Co., Ltd | SUN12000S-U {240V} | Y | Y | N | N | N | N | Y* | Y | 12.079 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.079 | 240 | 95.5 | CSA Group | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-10-17 | 2025-01-02 |  | N | N | 36.44 |  |  | 200 | 300 | 440 | 1.208 | 2.416 | 3.624 | 6.039 | 9.059 | 12.079 | 90.6 | 94.4 | 95.16 | 95.39 | 94.99 | 94.49 | 94.87 | 91.02 | 94.65 | 95.66 | 96.13 | 95.9 | 95.58 | 95.65 | 90.95 | 94.82 | 95.86 | 96.36 | 96.29 | 96.16 | 95.96 | 2024-08-01 | 2025-01-02
Huizhou Roypow Technology Co., Ltd | SUN15000S-U {240V} | Y | Y | N | N | N | N | Y* | Y | 14.987 kW, 240 Vac Grid Support Utility Interactive Inverter | 14.987 | 240 | 95.5 | CSA Group | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-10-17 | 2025-01-02 |  | N | N | 35.81 |  |  | 200 | 300 | 440 | 1.499 | 2.997 | 4.496 | 7.493 | 11.24 | 14.987 | 92.8 | 94.52 | 95.48 | 95.57 | 94.76 | 94.12 | 94.9 | 93.5 | 94.74 | 95.41 | 96.14 | 95.86 | 95.53 | 95.7 | 93.63 | 95.21 | 95.59 | 96.03 | 96.19 | 96.05 | 95.93 | 2024-08-01 | 2025-01-02
Hyperian Energy Inc. | ST2-76i {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter Power Conversion System | 7.581 | 240 | 97 | Intertek | [11/9/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.758 | 1.516 | 2.274 | 3.791 | 5.686 | 7.581 | 94.27 | 95.22 | 96.16 | 96.92 | 97.11 | 97.06 | 96.75 | 95.22 | 96.18 | 96.79 | 97.36 | 97.6 | 97.53 | 97.29 | 94.82 | 95.83 | 96.55 | 97.2 | 97.42 | 97.35 | 97.09 | 2024-05-13
Hyperian Energy Inc. | ST2-96i {240V} | Y | Y | N | N | N | N | N | N | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter Power Conversion System | 9.573 | 240 | 97 | Intertek | [11/9/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.957 | 1.915 | 2.872 | 4.787 | 7.18 | 9.573 | 94.32 | 95.43 | 96.47 | 97.01 | 97.09 | 97.01 | 96.8 | 95.76 | 96.41 | 97.04 | 97.48 | 97.57 | 97.4 | 97.35 | 94.89 | 95.98 | 96.84 | 97.31 | 97.39 | 97.23 | 97.13 | 2024-05-13
Hyperian Energy Inc. | ST2-100i {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive Inverter Power Conversion System | 9.956 | 240 | 97 | Intertek | [11/9/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.996 | 1.991 | 2.987 | 4.978 | 7.467 | 9.956 | 94.33 | 95.61 | 96.51 | 97.03 | 97.07 | 96.98 | 96.81 | 95.79 | 96.48 | 97.07 | 97.5 | 97.54 | 97.37 | 97.35 | 95.18 | 96.08 | 96.88 | 97.34 | 97.37 | 97.21 | 97.14 | 2024-05-13
Hyperian Energy Inc. | ST2-114i {240V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter Power Conversion System | 11.371 | 240 | 97 | Intertek | [11/9/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.137 | 2.274 | 3.411 | 5.685 | 8.528 | 11.371 | 94.36 | 96.06 | 96.91 | 97.1 | 97.04 | 96.9 | 96.88 | 95.81 | 96.79 | 97.34 | 97.6 | 97.47 | 97.26 | 97.37 | 95.28 | 96.55 | 97.16 | 97.41 | 97.3 | 97.08 | 97.18 | 2024-05-13
Hyperian Energy Inc. | ST2-120i {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Utility Interactive Inverter Power Conversion System | 11.968 | 240 | 97 | Intertek | [11/9/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.197 | 2.394 | 3.59 | 5.984 | 8.976 | 11.968 | 94.38 | 96.06 | 96.92 | 97.12 | 97.01 | 96.87 | 96.87 | 95.83 | 96.81 | 97.34 | 97.62 | 97.45 | 97.22 | 97.37 | 95.32 | 96.57 | 97.18 | 97.44 | 97.28 | 97.04 | 97.18 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 610TL U B220 {220V} | Y | N | Y | Y | Y | N | N | N | 610 kW, 220 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 610 | 220 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 440 | 590 | 740 | 61 | 122 | 183 | 305 | 457.5 | 610 | 97.11 | 98.06 | 98.25 | 98.17 | 97.74 | 97.1 | 97.85 | 96.37 | 97.64 | 98.01 | 97.9 | 97.48 | 96.73 | 97.56 | 95.53 | 97.29 | 97.68 | 97.72 | 97.45 | 96.53 | 97.41 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 830TL U B300 {300V} | Y | N | Y | Y | Y | N | N | N | 830 kW, 300 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 830 | 300 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 440 | 590 | 740 | 83 | 166 | 249 | 415 | 622.5 | 830 | 97.21 | 98.13 | 98.27 | 98.16 | 97.74 | 97.18 | 97.86 | 96.5 | 97.77 | 97.96 | 97.92 | 97.55 | 97.06 | 97.62 | 95.7 | 97.41 | 97.7 | 97.66 | 97.36 | 96.88 | 97.38 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 915TL U B330 {330V} | Y | N | Y | Y | Y | N | N | N | 915 kW, 330 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 915 | 330 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 485 | 613 | 740 | 91.5 | 183 | 274.5 | 457.5 | 686.25 | 915 | 97.17 | 98.13 | 98.33 | 98.22 | 97.86 | 97.27 | 97.95 | 96.5 | 97.84 | 98.09 | 98.05 | 97.69 | 97.15 | 97.75 | 95.82 | 97.49 | 97.82 | 97.81 | 97.51 | 97.17 | 97.53 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1000TL U B360 {360V} | Y | N | Y | Y | Y | N | N | N | 1000 kW, 360 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1000 | 360 | 98 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 524 | 632 | 740 | 100 | 200 | 300 | 500 | 750 | 1000 | 97.34 | 98.14 | 98.33 | 98.21 | 97.83 | 97.31 | 97.94 | 96.84 | 97.92 | 98.13 | 98.08 | 97.7 | 97.09 | 97.78 | 96.36 | 97.64 | 97.97 | 97.94 | 97.55 | 96.97 | 97.61 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1140TL U B410 {410V} | Y | N | Y | Y | Y | N | N | N | 1136 kVA, 410 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1027.752 | 410 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 2550.2775 |  |  | 595 | 668 | 800 | 102.7752 | 205.5504 | 308.3256 | 513.876 | 770.814 | 1027.752 | 95.8625 | 97.4417 | 97.8113 | 97.8912 | 97.7441 | 97.3829 | 97.6746 | 95.6736 | 97.3781 | 97.7557 | 97.8606 | 97.7193 | 97.3781 | 97.6374 | 95.14 | 97.0801 | 97.524 | 97.6897 | 97.5561 | 97.213 | 97.4427 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1245TL U B480 {480V} | Y | N | Y | Y | Y | N | N | N | 1247 kVA, 480 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1042.22 | 480 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 697 | 949 | 1200 | 104.222 | 208.444 | 312.666 | 521.11 | 781.665 | 1042.22 | 96.9037 | 97.6188 | 97.803 | 97.7395 | 97.5015 | 97.1174 | 97.5504 | 96.4047 | 97.431 | 97.5993 | 97.4719 | 97.2822 | 96.859 | 97.3113 | 96.026 | 97.0747 | 97.3979 | 97.2268 | 96.9903 | 96.5138 | 97.0307 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1190TL U B430 {430V} | Y | N | Y | Y | Y | N | N | N | 1192 kVA, 430 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1048.594 | 430 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 2550.2775 |  |  | 624 | 682 | 800 | 104.8594 | 209.7188 | 314.5782 | 524.297 | 786.4455 | 1048.594 | 96.0041 | 97.4811 | 97.8373 | 97.9231 | 97.7893 | 97.4138 | 97.7176 | 95.8692 | 97.4303 | 97.7966 | 97.9039 | 97.781 | 97.4506 | 97.6982 | 95.3825 | 97.1832 | 97.5935 | 97.7411 | 97.6496 | 97.3174 | 97.5314 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1220TL U B440 {440V} | Y | N | Y | Y | Y | N | N | N | 1217 kVA, 440 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1099.306 | 440 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 2550.2775 |  |  | 638 | 689 | 800 | 109.9306 | 219.8612 | 329.7918 | 549.653 | 824.4795 | 1099.306 | 95.932 | 97.4927 | 97.868 | 97.9487 | 97.8105 | 97.4537 | 97.7375 | 95.8363 | 97.4652 | 97.8509 | 97.9442 | 97.8039 | 97.4677 | 97.7266 | 95.4261 | 97.2395 | 97.6478 | 97.8037 | 97.6832 | 97.3514 | 97.5752 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1110TL U B400 {400V} | Y | N | Y | Y | Y | N | N | N | 1110 kW, 400 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1110 | 400 | 98 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 580 | 660 | 740 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 97.16 | 98.08 | 98.29 | 98.27 | 97.94 | 97.39 | 98 | 96.8 | 97.93 | 98.19 | 98.25 | 97.8 | 97.32 | 97.89 | 96.54 | 97.71 | 98.06 | 98.12 | 97.67 | 97.35 | 97.75 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1250TL U B450 {450V} | Y | N | Y | Y | Y | N | N | N | 1247 kVA, 450 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1114.104 | 450 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 2550.2775 |  |  | 652 | 696 | 800 | 111.4104 | 222.8208 | 334.2312 | 557.052 | 835.578 | 1114.104 | 95.9706 | 97.5016 | 97.8688 | 97.9364 | 97.8103 | 97.4968 | 97.7391 | 95.9001 | 97.4837 | 97.855 | 97.9743 | 97.8316 | 97.5204 | 97.7542 | 95.5073 | 97.2604 | 97.6982 | 97.8443 | 97.7172 | 97.4132 | 97.6152 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1275TL U B460 {460V} | Y | N | Y | Y | Y | N | N | N | 1275 kVA, 460 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1128.476 | 460 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 2550.2775 |  |  | 666 | 703 | 800 | 112.8476 | 225.6952 | 338.5428 | 564.238 | 846.357 | 1128.476 | 95.9938 | 97.508 | 97.8617 | 97.9706 | 97.8442 | 97.6278 | 97.7712 | 95.8888 | 97.4823 | 97.8709 | 97.9916 | 97.8671 | 97.5597 | 97.7799 | 95.5429 | 97.3202 | 97.7334 | 97.9123 | 97.7635 | 97.4905 | 97.6665 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1165TL U B420 {420V} | Y | N | Y | Y | Y | N | N | N | 1165 kW, 420 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1165 | 420 | 98 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 80 |  |  | 610 | 675 | 740 | 116.5 | 233 | 349.5 | 582.5 | 873.75 | 1165 | 97.28 | 98.08 | 98.28 | 98.26 | 98.01 | 97.47 | 98.04 | 96.99 | 97.92 | 98.18 | 98.24 | 97.91 | 97.53 | 97.95 | 96.74 | 97.75 | 98.03 | 98.15 | 97.85 | 97.42 | 97.87 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1740TL U B670 {670V} | Y | N | Y | Y | Y | N | N | N | 1741 kVA, 670 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1272.412 | 670 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 962 | 1081 | 1200 | 127.2412 | 254.4824 | 381.7236 | 636.206 | 954.309 | 1272.412 | 95.9646 | 97.3748 | 97.6902 | 97.7604 | 97.6287 | 97.348 | 97.5704 | 95.7313 | 97.2879 | 97.5573 | 97.697 | 97.5442 | 97.223 | 97.4764 | 95.3778 | 97.1365 | 97.419 | 97.506 | 97.402 | 97.144 | 97.3188 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1800TL U B690 {690V} | Y | N | Y | Y | Y | N | N | N | 1793 kVA, 690 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1300.644 | 690 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 962 | 1081 | 1200 | 130.0644 | 260.1288 | 390.1932 | 650.322 | 975.483 | 1300.644 | 96.6717 | 97.6652 | 97.8788 | 97.9021 | 97.7538 | 97.399 | 97.7345 | 96.4722 | 97.5961 | 97.804 | 97.828 | 97.6778 | 97.3356 | 97.6551 | 96.3335 | 97.5145 | 97.7082 | 97.7346 | 97.5625 | 97.2579 | 97.5493 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1665TL U B640 {640V} | Y | N | Y | Y | Y | N | N | N | 1663 kVA, 640 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1367.076 | 640 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 919 | 1060 | 1200 | 136.7076 | 273.4152 | 410.1228 | 683.538 | 1025.307 | 1367.076 | 96.2495 | 97.4423 | 97.7204 | 97.755 | 97.6184 | 97.3123 | 97.5805 | 95.9772 | 97.3141 | 97.5906 | 97.6697 | 97.5061 | 97.1929 | 97.4642 | 95.5155 | 97.1401 | 97.4064 | 97.4529 | 97.3426 | 97.0371 | 97.2749 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1690TL U B650 {650V} | Y | N | Y | Y | Y | N | N | N | 1689 kVA, 650 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1375.282 | 650 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 933 | 1067 | 1200 | 137.5282 | 275.0564 | 412.5846 | 687.641 | 1031.4615 | 1375.282 | 96.2881 | 97.5051 | 97.7757 | 97.8183 | 97.6619 | 97.3581 | 97.6304 | 96.0008 | 97.4016 | 97.6638 | 97.7405 | 97.5736 | 97.2501 | 97.5318 | 95.6676 | 97.2627 | 97.5419 | 97.5575 | 97.4238 | 97.0851 | 97.3708 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 1715TL U B660 {660V} | Y | N | Y | Y | Y | N | N | N | 1715 kVA, 660 Vac Grid Support Utility Interactive Inverter for PV and Battery Applications. | 1390.614 | 660 | 97.5 | No Information Submitted | No Information Submitted | SGS | [5/5/2018] | [ABK1000] | 2019-05-01 | [5/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Overall efficiency includes Ingeteam transformer packaged with product. Per SGS, revision I of ABK 1 was tested per UL 1741 SA. Revisions J, K, and L were considered with no influence regarding grid support compliance. | N | N | 459.0724 |  |  | 948 | 1074 | 1200 | 139.0614 | 278.1228 | 417.1842 | 695.307 | 1042.9605 | 1390.614 | 96.0622 | 97.4034 | 97.6863 | 97.7536 | 97.622 | 97.3392 | 97.5699 | 95.8419 | 97.2707 | 97.5502 | 97.7009 | 97.5384 | 97.2305 | 97.4773 | 95.3647 | 97.1092 | 97.4005 | 97.5253 | 97.4034 | 97.0865 | 97.3166 | 2019-05-01
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3660TL U C450 {450V} | N | Y | N | N | N | N | N | N | 2306 kW, 450 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter with External Transformer | 2306 | 450 | 97 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2700.1098 |  |  | 650 | 1088 | 1300 | 230.6 | 461.2 | 691.8 | 1153 | 1729.5 | 2306 | 96.3459 | 97.4866 | 97.7995 | 97.6073 | 97.5158 | 97.1673 | 97.5034 | 94.1835 | 96.1096 | 96.6986 | 96.9223 | 96.8165 | 96.4983 | 96.668 | 93.7406 | 95.5656 | 96.2525 | 96.6212 | 96.4455 | 96.1577 | 96.2926 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3660TL U C480 {480V} | N | Y | N | N | N | N | N | N | 2467 kW, 480 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter with External Transformer | 2467.62 | 480 | 97 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2700.1098 |  |  | 670 | 1088 | 1300 | 246.762 | 493.524 | 740.286 | 1233.81 | 1850.715 | 2467.62 | 96.3108 | 97.5063 | 97.8628 | 97.856 | 97.5264 | 97.0899 | 97.5645 | 94.4756 | 96.2677 | 96.7661 | 97.0602 | 96.9566 | 96.642 | 96.8061 | 94.0549 | 95.7886 | 96.3946 | 96.7805 | 96.6486 | 96.3652 | 96.4849 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3930TL U HV C600 {600V} | N | Y | N | N | N | N | N |  | 2582 kW, 600 Vac Grid Support Utility Interactive Inverter | 2582 | 600 | 97.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Efficiency data includes external transformer Ingecon Sun Storage Power Station FSK C Series HV UL - Step-Up effect. | N | N | 7080 |  |  | 938 | 1200 | 1500 | 258.2 | 516.4 | 774.6 | 1291 | 1936.5 | 2582 | 95.523 | 97.4881 | 98.0466 | 98.3333 | 98.1699 | 97.9318 | 98.0376 | 94.3441 | 96.8954 | 97.2841 | 97.9507 | 97.9396 | 97.6593 | 97.6532 | 93.3247 | 95.6741 | 96.8993 | 97.4217 | 97.5653 | 97.2998 | 97.1778 | 2026-03-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3930TL U HV C650 {650V} | N | Y | N | N | N | N | N |  | 2762.4 kW, 650 Vac Grid Support Utility Interactive Inverter | 2762.4 | 650 | 97.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Efficiency data includes external transformer Ingecon Sun Storage Power Station FSK C Series HV UL - Step-Up effect. | N | N | 7080 |  |  | 1010 | 1200 | 1500 | 276.24 | 552.48 | 828.72 | 1381.2 | 2071.8 | 2762.4 | 95.1745 | 97.3036 | 97.9621 | 98.2809 | 98.124 | 97.8947 | 97.9671 | 94.3425 | 97.0049 | 97.5545 | 97.9097 | 97.875 | 97.6609 | 97.6483 | 93.3218 | 95.6339 | 96.9263 | 97.4342 | 97.5778 | 97.3884 | 97.1925 | 2026-03-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3660TL U C578 {578V} | N | Y | N | N | N | N | N | N | 2881 kW, 578 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter with External Transformer | 2881.48 | 578 | 97.5 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2892.5248 |  |  | 826 | 1088 | 1300 | 288.148 | 576.296 | 864.444 | 1440.74 | 2161.11 | 2881.48 | 96.2086 | 97.5316 | 97.8756 | 98.1134 | 98.0193 | 97.7432 | 97.9112 | 95.4419 | 96.9928 | 97.4037 | 97.5915 | 97.4986 | 97.2261 | 97.3855 | 95.017 | 96.5863 | 96.9983 | 97.1796 | 97.2314 | 96.8158 | 97.0509 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3930TL U HV C690 {690V} | N | Y | N | N | N | N | N |  | 2983.4 kW, 690 Vac Grid Support Utility Interactive Inverter | 2983.4 | 690 | 98 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Efficiency data includes external transformer Ingecon Sun Storage Power Station FSK C Series HV UL - Step-Up effect. | N | N | 7080 |  |  | 1085 | 1250 | 1500 | 298.34 | 596.68 | 895.02 | 1491.7 | 2237.55 | 2983.4 | 95.8227 | 97.7083 | 98.2536 | 98.4992 | 98.3672 | 98.2799 | 98.2422 | 95.1789 | 97.4431 | 97.9753 | 98.1543 | 98.1685 | 98.1113 | 97.9836 | 94.2145 | 96.3563 | 97.2868 | 97.8993 | 97.8748 | 97.8361 | 97.5851 | 2026-03-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3660TL U C600 {600V} | N | Y | N | N | N | N | N | N | 3095 kW, 600 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter with External Transformer | 3095.3 | 600 | 98 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2892.5248 |  |  | 857 | 1170 | 1300 | 309.53 | 619.06 | 928.59 | 1547.65 | 2321.475 | 3095.3 | 96.2926 | 98.06 | 98.5052 | 98.6678 | 98.5782 | 98.3062 | 98.4573 | 95.348 | 96.9302 | 97.2423 | 97.496 | 97.4826 | 97.2891 | 97.3339 | 95.6043 | 97.1607 | 97.5987 | 97.7736 | 97.6878 | 97.4161 | 97.5718 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3930TL U HV C730 {730V} | N | Y | N | N | N | N | N |  | 3102.8 kW, 730 Vac Grid Support Utility Interactive Inverter | 3102.8 | 730 | 98.5 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Efficiency data includes external transformer Ingecon Sun Storage Power Station FSK C Series HV UL - Step-Up effect. | N | N | 7080 |  |  | 1136 | 1300 | 1500 | 310.28 | 620.56 | 930.84 | 1551.4 | 2327.1 | 3102.8 | 95.8102 | 97.8526 | 98.458 | 98.6975 | 98.6887 | 98.5364 | 98.4983 | 95.3152 | 97.6697 | 98.2835 | 98.4032 | 98.5422 | 98.3799 | 98.3011 | 94.4465 | 96.9296 | 97.59 | 98.2297 | 98.3489 | 98.127 | 97.9947 | 2026-03-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3930TL U HV C750 {750V} | N | Y | N | N | N | N | N |  | 3237.1 kW, 750 Vac Grid Support Utility Interactive Inverter | 3237.1 | 750 | 98 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Efficiency data includes external transformer Ingecon Sun Storage Power Station FSK C Series HV UL - Step-Up effect. | N | N | 7080 |  |  | 1165 | 1300 | 1500 | 323.71 | 647.42 | 971.13 | 1618.55 | 2427.825 | 3237.1 | 95.6107 | 97.6212 | 98.1763 | 98.4596 | 98.4489 | 98.2883 | 98.2555 | 95.1108 | 97.4166 | 98.0803 | 98.1965 | 98.3962 | 98.1696 | 98.1246 | 94.2861 | 96.927 | 97.3727 | 97.9906 | 98.15 | 97.9537 | 97.7977 | 2026-03-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3660TL U C630 {630V} | N | Y | N | N | N | N | N | N | 3239 kW, 630 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter with External Transformer | 3239.42 | 630 | 98 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2892.5248 |  |  | 894 | 1185 | 1300 | 323.942 | 647.884 | 971.826 | 1619.71 | 2429.565 | 3239.42 | 96.3132 | 97.7784 | 98.2173 | 98.2564 | 98.3094 | 98.0308 | 98.1669 | 95.6961 | 97.2402 | 97.68 | 97.851 | 97.7616 | 97.4875 | 97.6482 | 95.4573 | 96.982 | 97.4165 | 97.5909 | 97.5044 | 97.2301 | 97.3903 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3930TL U HV C760 {760V} | N | Y | N | N | N | N | N |  | 3240 kW, 760 Vac Grid Support Utility Interactive Inverter | 3240 | 760 | 98 | SGS | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Efficiency data includes external transformer Ingecon Sun Storage Power Station FSK C Series HV UL - Step-Up effect. | N | N | 7080 |  |  | 1180 | 1350 | 1500 | 324 | 648 | 972 | 1620 | 2430 | 3240 | 95.8181 | 97.7226 | 98.1845 | 98.5283 | 98.4398 | 98.4031 | 98.2852 | 95.1786 | 97.4659 | 98.0286 | 98.2236 | 98.3096 | 98.271 | 98.0885 | 94.5753 | 97.1015 | 97.3632 | 98.0642 | 98.1772 | 98.0974 | 97.8539 | 2026-03-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3660TL U C645 {645V} | N | Y | N | N | N | N | N | N | 3304 kW, 645 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter with External Transformer | 3304.62 | 645 | 98 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2892.5248 |  |  | 919 | 1198 | 1300 | 330.462 | 660.924 | 991.386 | 1652.31 | 2478.465 | 3304.62 | 96.3192 | 97.8824 | 98.4026 | 98.5932 | 98.6717 | 98.5557 | 98.4836 | 95.8697 | 97.4188 | 97.8578 | 98.0277 | 97.9363 | 97.6628 | 97.8239 | 95.6571 | 97.225 | 97.6635 | 97.8343 | 97.7396 | 97.4636 | 97.6275 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3660TL U C660 {660V} | N | Y | N | N | N | N | N | N | 3377 kW, 660 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter with External Transformer | 3377.6 | 660 | 98 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2804.839 |  |  | 940 | 1198 | 1300 | 337.76 | 675.52 | 1013.28 | 1688.8 | 2533.2 | 3377.6 | 96.5514 | 98.0805 | 98.5257 | 98.7028 | 98.6109 | 98.3376 | 98.4974 | 96.0119 | 97.5767 | 97.9957 | 98.1794 | 98.0856 | 97.8138 | 97.9725 | 95.816 | 97.3667 | 97.8067 | 97.9771 | 97.8876 | 97.5713 | 97.772 | 2024-05-13
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN STORAGE 3660TL U C690 {690V} | N | Y | N | N | N | N | N | N | 3535 kW, 690 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter with External Transformer | 3535.56 | 690 | 98.5 | SGS | [9/27/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2804.839 |  |  | 981 | 1200 | 1300 | 353.556 | 707.112 | 1060.668 | 1767.78 | 2651.67 | 3535.56 | 96.8472 | 98.3894 | 98.8191 | 98.9899 | 98.9407 | 98.6271 | 98.8095 | 96.4248 | 97.9781 | 98.4038 | 98.5799 | 98.49 | 98.2174 | 98.3767 | 96.103 | 97.6667 | 98.1004 | 98.2761 | 98.1845 | 97.9132 | 98.0709 | 2024-05-13
Jackery Inc. | GVI-HR-7K6-USG {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.394 | 240 | 97 | CSA Group | [9/8/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-23 | 2025-02-21 |  | N | N | 16.33 |  |  | 175 | 380 | 450 | 0.739 | 1.479 | 2.218 | 3.697 | 5.545 | 7.394 | 95.78 | 96.57 | 97.14 | 97.12 | 97.27 | 97.32 | 97.13 | 95.02 | 96.11 | 97.17 | 97.26 | 97.29 | 97.63 | 97.13 | 94.73 | 96.14 | 96.95 | 97.09 | 97.15 | 97.33 | 96.97 | 2025-02-21
Jackery Inc. | GVI-HR-11K4-USG {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.084 | 240 | 97 | CSA Group | [9/8/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-09-23 | 2025-02-21 |  | N | N | 15.36 |  |  | 245 | 380 | 450 | 1.108 | 2.217 | 3.325 | 5.542 | 8.313 | 11.084 | 94.77 | 96.19 | 97.09 | 97.38 | 97.26 | 97.27 | 97.11 | 95.99 | 96.88 | 96.88 | 97.03 | 97.23 | 97.34 | 97.08 | 95.55 | 96.65 | 97.05 | 97.18 | 97.22 | 97.63 | 97.11 | 2025-02-21
Jiangsu RCT Power Energy Technology Co., Ltd | Power Storage DC US-8.0 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.015 | 208 | 97 | CSA Group | [4/29/2024] | CSA Group | [3/30/2022];[4/29/2024] | [V54];[V127(2.27.0104-1.44)] | 2022-05-11 | [3/30/2022] | 2022-05-11 | CSA Group | 2022-03-17 | 2022-05-11 |  | N | N | 0.3 |  |  | 220 | 360 | 420 | 0.701 | 1.403 | 2.104 | 3.507 | 5.261 | 7.015 | 93.43 | 95.62 | 96.35 | 96.74 | 96.65 | 96.23 | 96.43 | 93.5 | 96.2 | 96.79 | 97.21 | 97.18 | 96.89 | 96.93 | 93.92 | 96.44 | 97.09 | 97.42 | 97.35 | 97.01 | 97.13 | 2022-05-11 | 2024-08-01
Jiangsu RCT Power Energy Technology Co., Ltd | Power Storage DC US-8.0 PRO {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.015 | 208 | 97 | CSA Group | [4/29/2024] | CSA Group | [3/30/2022];[4/29/2024] | [V54];[V127(2.27.0104-1.44)] | 2024-08-01 | [4/29/2024] | 2024-08-01 | CSA Group | 2024-06-01 | 2024-08-01 |  | N | N | 0.3 |  |  | 220 | 360 | 420 | 0.701 | 1.403 | 2.104 | 3.507 | 5.261 | 7.015 | 93.4321 | 95.6214 | 96.3503 | 96.7391 | 96.6452 | 96.2338 | 96.4293 | 93.4986 | 96.2026 | 96.7947 | 97.209 | 97.1825 | 96.889 | 96.9305 | 93.9173 | 96.445 | 97.0889 | 97.4174 | 97.3475 | 97.0142 | 97.1321 | 2024-08-01
Jiangsu RCT Power Energy Technology Co., Ltd | Power Storage DC US-8.0 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.0322 | 240 | 97 | CSA Group | [4/29/2024] | CSA Group | [3/30/2022];[4/29/2024] | [V54];[V127(2.27.0104-1.44)] | 2022-05-11 | [3/30/2022] | 2022-05-11 | CSA Group | 2022-03-17 | 2022-05-11 |  | N | N | 0.4025 |  |  | 220 | 360 | 420 | 0.80322 | 1.6064 | 2.4097 | 4.0161 | 6.0241 | 8.0322 | 94.4835 | 96.2889 | 96.8676 | 97.1353 | 96.9831 | 96.5638 | 96.8456 | 94.8035 | 96.8257 | 97.2969 | 97.5898 | 97.5257 | 97.2299 | 97.353 | 94.7472 | 96.886 | 97.455 | 97.7157 | 97.636 | 97.3371 | 97.463 | 2022-05-11 | 2024-08-01
Jiangsu RCT Power Energy Technology Co., Ltd | Power Storage DC US-8.0 PRO {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.0322 | 240 | 97 | CSA Group | [4/29/2024] | CSA Group | [3/30/2022];[4/29/2024] | [V54];[V127(2.27.0104-1.44)] | 2024-08-01 | [4/29/2024] | 2024-08-01 | CSA Group | 2024-06-01 | 2024-08-01 |  | N | N | 0.4025 |  |  | 220 | 360 | 420 | 0.80322 | 1.6064 | 2.4097 | 4.0161 | 6.0241 | 8.0322 | 94.4835 | 96.2889 | 96.8676 | 97.1353 | 96.9831 | 96.5638 | 96.8456 | 94.8035 | 96.8257 | 97.2969 | 97.5898 | 97.5257 | 97.2299 | 97.353 | 94.7472 | 96.886 | 97.455 | 97.7157 | 97.636 | 97.3371 | 97.463 | 2024-08-01
Jiangsu Weiheng Intelligent Technology Co., Ltd. | SHD-7.6kW {240V} | Y | Y | N | N | N | N | N | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.572 | 240 | 97 | Intertek | [7/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-08-21 |  | N | N | 10.938 |  |  | 144 | 410 | 550 | 0.757 | 1.514 | 2.271 | 3.786 | 5.679 | 7.572 | 92.67 | 93.99 | 96.25 | 96.74 | 97.23 | 97.29 | 96.67 | 93.45 | 95.89 | 96.63 | 97.13 | 97.44 | 97.17 | 97.03 | 92.88 | 93.74 | 95.81 | 96.67 | 97.51 | 97.41 | 96.75 | 2025-08-21
Jiangsu Weiheng Intelligent Technology Co., Ltd. | SHD-9.6kW {240V} | Y | Y | N | N | N | N | N | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.66 | 240 | 97 | Intertek | [7/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-08-21 |  | N | N | 11.042 |  |  | 180 | 410 | 550 | 0.966 | 1.932 | 2.898 | 4.83 | 7.245 | 9.66 | 95.02 | 95.73 | 96.33 | 97.12 | 97.43 | 96.86 | 97.02 | 94.7 | 96.34 | 96.9 | 97.25 | 97.43 | 97.04 | 97.15 | 93.23 | 95.17 | 96.29 | 97.24 | 97.54 | 97.15 | 97.02 | 2025-08-21
Jiangsu Weiheng Intelligent Technology Co., Ltd. | SHD-11.4kW {240V} | Y | Y | N | N | N | N | N | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.257 | 240 | 97 | Intertek | [7/9/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-08-21 |  | N | N | 10.379 |  |  | 210 | 410 | 550 | 1.126 | 2.251 | 3.377 | 5.628 | 8.443 | 11.257 | 95.48 | 96.28 | 96.64 | 97.26 | 97.49 | 96.36 | 97.14 | 95.03 | 96.63 | 97.11 | 97.59 | 97.3 | 96.87 | 97.19 | 93.32 | 95.8 | 96.63 | 97.54 | 97.36 | 96.48 | 97.03 | 2025-08-21
JingTsing Technology Ltd. | JTES-PCS125K-1000/480-L03C1 {480V} | N | Y | N | N | N | N | Y* | Y | 125 kW, 480 Vac Grid Support Utility Interactive Energy Storage Inverter | 127.819 | 480 | 98 | CSA Group | [11/29/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-15 | 2025-01-21 |  | N | N | 8.34 |  |  | 700 | 832 | 950 | 12.782 | 25.564 | 38.346 | 63.909 | 95.864 | 127.819 | 97.35 | 98.28 | 98.44 | 98.6 | 98.45 | 98.22 | 98.42 | 95.9 | 97.65 | 98.15 | 98.36 | 98.21 | 98.01 | 98.1 | 94.83 | 97.15 | 97.71 | 97.98 | 97.97 | 97.81 | 97.77 | 2025-01-21
JingTsing Technology Ltd. | JTES-PCS125K-1000/480-L03L1 {480V} | N | Y | N | N | N | N | Y* | Y | 125 kW, 480 Vac Grid Support Utility Interactive Energy Storage Inverter | 127.819 | 480 | 98 | CSA Group | [11/29/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-15 | 2025-01-21 |  | N | N | 8.34 |  |  | 700 | 832 | 950 | 12.782 | 25.564 | 38.346 | 63.909 | 95.864 | 127.819 | 97.35 | 98.28 | 98.44 | 98.6 | 98.45 | 98.22 | 98.42 | 95.9 | 97.65 | 98.15 | 98.36 | 98.21 | 98.01 | 98.1 | 94.83 | 97.15 | 97.71 | 97.98 | 97.97 | 97.81 | 97.77 | 2025-01-21
JingTsing Technology Ltd. | JTES-PCS450K-1600/740-L03C1 {740V} | N | Y | N | N | N | N | Y* | Y | 450 kW, 740 Vac Grid Support Utility Interactive Energy Storage Inverter | 459.563 | 740 | 98.5 | CSA Group | [11/29/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-06-21 | 2025-01-21 |  | N | N | 3.57 |  |  | 1100 | 1400 | 1600 | 45.956 | 91.913 | 137.869 | 229.782 | 344.672 | 459.563 | 97.35 | 98.43 | 98.68 | 98.8 | 98.75 | 98.64 | 98.68 | 96.51 | 97.99 | 98.36 | 98.57 | 98.57 | 98.47 | 98.43 | 96.05 | 97.75 | 98.18 | 98.44 | 98.47 | 98.39 | 98.29 | 2025-01-21
Jinko Solar Co., Ltd | JKS-R-7P12-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.604 | 240 | 97 | CSA Group | [5/30/2023] | CSA Group | [5/30/2023] | [A2] | 2023-12-01 | [5/30/2023] | 2023-12-01 | CSA Group | 2023-09-25 | 2023-11-27 |  | N | N | 16.33 |  |  | 175 | 380 | 450 | 0.76 | 1.521 | 2.281 | 3.802 | 5.703 | 7.604 | 95.78 | 96.57 | 97.14 | 97.12 | 97.27 | 97.32 | 97.13 | 95.02 | 96.11 | 97.17 | 97.26 | 97.29 | 97.63 | 97.13 | 94.73 | 96.14 | 96.95 | 97.09 | 97.15 | 97.33 | 96.97 | 2023-12-01 | 2024-01-22
Jinko Solar Co., Ltd | JKS-R-11P12-US {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.406 | 240 | 97 | CSA Group | [5/30/2023] | CSA Group | [5/30/2023] | [A2] | 2023-12-01 | [5/30/2023] | 2023-12-01 | CSA Group | 2023-09-25 | 2023-11-27 |  | N | N | 15.36 |  |  | 245 | 380 | 450 | 1.141 | 2.281 | 3.422 | 5.703 | 8.554 | 11.406 | 94.77 | 96.19 | 97.09 | 97.38 | 97.26 | 97.27 | 97.11 | 95.99 | 96.88 | 96.88 | 97.03 | 97.23 | 97.34 | 97.08 | 95.55 | 96.65 | 97.05 | 97.18 | 97.22 | 97.57 | 97.11 | 2023-12-01 | 2024-01-22
Kora Power, Inc. | KP-INV-380-01 {240V} | Y | Y | Y | Y | Y | Y | N |  | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 3.7972 | 240 | 96 | CSA Group | [8/17/2026] | CSA Group | [8/17/2026] | [V1.08, V1.02] | 2026-10-01 | [8/17/2026] | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 13.35 |  |  | 204 | 380 | 500 | 0.37972 | 0.75944 | 1.1392 | 1.8986 | 2.8479 | 3.7972 | 89.6627 | 93.2292 | 94.5681 | 95.9692 | 96.4301 | 96.5483 | 95.685 | 91.725 | 94.6987 | 95.7083 | 96.7501 | 96.9842 | 97.1693 | 96.4665 | 88.9624 | 93.5492 | 95.5387 | 97.0122 | 97.3598 | 97.5206 | 96.5499 | 2026-10-01 |  | N | Y | N | N | N | Y | N | N | N
Kora Power, Inc. | KP-INV-570-01 {240V} | Y | Y | Y | Y | Y | Y | N |  | 5.7 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.6866 | 240 | 97 | CSA Group | [8/17/2026] | CSA Group | [8/17/2026] | [V1.08, V1.02] | 2026-10-01 | [8/17/2026] | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 13.35 |  |  | 204 | 380 | 500 | 0.56866 | 1.1373 | 1.706 | 2.8433 | 4.265 | 5.6866 | 90.9696 | 94.7434 | 95.8003 | 96.4201 | 96.6721 | 96.5359 | 96.1832 | 91.1194 | 95.495 | 96.9717 | 97.7104 | 97.7396 | 97.8212 | 97.2684 | 91.0574 | 96.0199 | 96.4362 | 96.7768 | 97.6862 | 97.512 | 96.9881 | 2026-10-01 |  | N | Y | N | N | N | Y | N | N | N
Kora Power, Inc. | KP-INV-760-01 {240V} | Y | Y | Y | Y | Y | Y | N |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.5857 | 240 | 97.5 | CSA Group | [8/17/2026] | CSA Group | [8/17/2026] | [V1.08, V1.02] | 2026-10-01 | [8/17/2026] | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 13.35 |  |  | 271 | 380 | 500 | 0.75857 | 1.5171 | 2.2757 | 3.7928 | 5.6893 | 7.5857 | 95.214 | 96.6078 | 97.1112 | 97.4349 | 97.5337 | 97.4987 | 97.3214 | 95.8601 | 97.1947 | 97.6786 | 97.8404 | 97.7797 | 97.7298 | 97.6718 | 95.0767 | 96.615 | 97.41 | 97.5037 | 97.6476 | 97.3909 | 97.4216 | 2026-10-01 |  | N | Y | N | N | N | Y | N | N | N
Kora Power, Inc. | KP-INV-960-01 {240V} | Y | Y | Y | Y | Y | Y | N |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.5752 | 240 | 97.5 | CSA Group | [8/17/2026] | CSA Group | [8/17/2026] | [V1.08, V1.02] | 2026-10-01 | [8/17/2026] | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 13.35 |  |  | 257 | 380 | 500 | 0.95752 | 1.915 | 2.8726 | 4.7876 | 7.1814 | 9.5752 | 95.5716 | 96.9652 | 97.2989 | 97.5667 | 97.3513 | 97.0646 | 97.2854 | 96.4655 | 97.5565 | 97.7877 | 97.8147 | 97.7869 | 97.5106 | 97.7147 | 95.5032 | 96.9894 | 97.3765 | 97.569 | 97.4942 | 97.2838 | 97.3804 | 2026-10-01 |  | N | Y | N | N | N | Y | N | N | N
Kora Power, Inc. | KP-INV-114-01 {240V} | Y | Y | Y | Y | Y | Y | N |  | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.3612 | 240 | 97.5 | CSA Group | [8/17/2026] | CSA Group | [8/17/2026] | [V1.08, V1.02] | 2026-10-01 | [8/17/2026] | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 13.35 |  |  | 305 | 380 | 500 | 1.1361 | 2.2722 | 3.4084 | 5.6806 | 8.5209 | 11.3612 | 95.4936 | 97.0984 | 97.3469 | 97.5337 | 97.2494 | 96.9259 | 97.2268 | 96.3704 | 97.3767 | 97.7788 | 97.5807 | 97.5045 | 97.4531 | 97.4991 | 95.4259 | 97.3169 | 97.5648 | 97.6753 | 97.5094 | 97.1914 | 97.442 | 2026-10-01 |  | N | Y | N | N | N | Y | N | N | N
Kowint Energy (Shenzhen) Co., Ltd. | KSL-8KU-A {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 8.111 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 20.205 |  |  | 150 | 360 | 430 | 0.8111 | 1.6222 | 2.4333 | 4.0555 | 6.0832 | 8.111 | 93.836 | 95.318 | 95.642 | 95.8 | 95.492 | 95.582 | 95.5042 | 94.262 | 96.192 | 96.604 | 96.92 | 96.6 | 96.288 | 96.5382 | 94.044 | 96.13 | 96.518 | 96.864 | 96.724 | 96.4 | 96.5756 | 2025-02-03
Kowint Energy (Shenzhen) Co., Ltd. | KSL-8KU-B {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 8.1809 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 19.254 |  |  | 150 | 360 | 430 | 0.81809 | 1.6362 | 2.4543 | 4.0905 | 6.1357 | 8.1809 | 93.944 | 95.376 | 95.752 | 95.916 | 95.522 | 95.56 | 95.5638 | 94.308 | 96.218 | 96.68 | 96.842 | 96.584 | 96.23 | 96.5227 | 93.938 | 96.068 | 96.616 | 96.926 | 96.772 | 96.24 | 96.6105 | 2025-02-03
Kowint Energy (Shenzhen) Co., Ltd. | KSL-12KU-A {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 12.1371 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 19.85 |  |  | 200 | 360 | 430 | 1.2137 | 2.4274 | 3.6411 | 6.0686 | 9.1028 | 12.1371 | 93.694 | 95.54 | 95.7 | 95.864 | 95.498 | 95.304 | 95.5193 | 94.212 | 96.206 | 96.618 | 96.8 | 96.544 | 96.338 | 96.4862 | 94.07 | 96.028 | 96.604 | 96.908 | 96.662 | 96.216 | 96.549 | 2025-02-03
Kowint Energy (Shenzhen) Co., Ltd. | KSL-12KU-B {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 12.2135 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 13.202 |  |  | 200 | 360 | 430 | 1.2214 | 2.4427 | 3.6641 | 6.1068 | 9.1601 | 12.2135 | 93.588 | 95.318 | 95.52 | 95.804 | 95.494 | 95.612 | 95.4831 | 94.262 | 96.132 | 96.662 | 96.872 | 96.622 | 96.294 | 96.544 | 94.002 | 96.18 | 96.74 | 96.876 | 96.678 | 96.362 | 96.5793 | 2025-02-03
Kowint Energy (Shenzhen) Co., Ltd. | KSL-16KU-A {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 16 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 16.1309 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 19.23 |  |  | 220 | 360 | 430 | 1.6131 | 3.2262 | 4.8393 | 8.0655 | 12.0982 | 16.1309 | 93.788 | 95.264 | 95.68 | 95.82 | 95.856 | 95.46 | 95.6952 | 94.188 | 96.134 | 96.65 | 96.838 | 96.602 | 96.238 | 96.5192 | 94.13 | 96.028 | 96.604 | 96.836 | 96.6 | 96.354 | 96.5103 | 2025-02-03
Kowint Energy (Shenzhen) Co., Ltd. | KSL-16KU-B {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 16 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 16.1988 | 240 | 96 | SGS | [10/17/2024] | SGS | [10/17/2024] | [1.0406(DSP), V2.0306(ARM)] | 2025-02-03 | [10/17/2024] | 2025-02-03 | SGS | 2024-10-10 | 2025-02-03 |  | N | N | 20.465 |  |  | 220 | 360 | 430 | 1.6199 | 3.2398 | 4.8596 | 8.0994 | 12.1491 | 16.1988 | 93.662 | 95.358 | 95.802 | 95.93 | 95.51 | 96.18 | 95.5852 | 94.188 | 96.06 | 96.548 | 96.876 | 96.636 | 96.35 | 96.5348 | 94.088 | 95.998 | 96.536 | 96.946 | 96.692 | 96.25 | 96.5657 | 2025-02-03
Kowint Energy (Shenzhen) Co., Ltd. | K-PH125-B-US03 {480V} | N | Y | N | N | N | N | N | N | 125 kW, 480 Vac Grid Support Utility Interactive Inverter | 125.015 | 480 | 98.5 | Intertek | [9/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 60 |  |  | 720.015 | 1010.1 | 1300.1 | 12.5015 | 25.003 | 37.5045 | 62.5075 | 93.7613 | 125.015 | 98.374 | 98.636 | 98.8 | 98.65 | 98.538 | 98.468 | 98.5878 | 98.286 | 98.536 | 98.7 | 98.536 | 98.468 | 98.378 | 98.5017 | 97.876 | 98.444 | 98.64 | 98.442 | 98.4 | 98.274 | 98.4126 | 2025-02-03
LG Electronics Inc. | A005KEEN261 {208V} | N | N | Y | Y | Y | Y | Y* | Y | 5000 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter | 5 | 208 | 98 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2018] | [1.4.1] | 2018-10-15 | [08/30/2018] | 2020-05-11 | CSA Group | 2020-03-26 | 2020-05-11 |  | Y | N | 1.85 |  |  | 350 | 400 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.3576 | 97.7104 | 98.1201 | 98.2082 | 98.0337 | 97.6876 | 97.9802 | 95.6974 | 97.377 | 97.8682 | 98.0571 | 97.92 | 97.611 | 97.8111 | 95.112 | 97.0074 | 97.61 | 97.87 | 97.8014 | 97.5053 | 97.6308 | 2018-10-01 | 2020-05-11
LG Electronics Inc. | A005KEEN261 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5000 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode, Grid Support Utility Interactive Energy Storage Inverter | 5 | 240 | 98 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2018] | [1.4.1] | 2018-10-15 | [08/30/2018] | 2020-05-11 | CSA Group | 2020-03-26 | 2020-05-11 |  | Y | N | 2.05 |  |  | 350 | 400 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.4809 | 97.5846 | 98.1167 | 98.4736 | 98.3238 | 97.9351 | 98.2003 | 95.8938 | 97.5508 | 98.0084 | 98.4507 | 98.3503 | 98.1238 | 98.1808 | 95.244 | 97.1576 | 97.7531 | 98.2952 | 98.2453 | 98.0333 | 98.0117 | 2018-10-01 | 2020-05-11
LG Electronics Inc. | D007KEEN261 {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 6656W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 6.656 | 208 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2018] | [1.4.1] | 2018-10-15 | [08/30/2018] | 2020-05-11 | CSA Group | 2020-03-26 | 2020-05-11 |  | Y | N | 1.15 |  |  | 270 | 380 | 450 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 94.5771 | 96.3015 | 96.9963 | 97.3878 | 97.2948 | 96.929 | 97.1019 | 95.9053 | 97.3314 | 97.7633 | 97.8619 | 97.5862 | 97.2138 | 97.5667 | 95.0392 | 96.9541 | 97.466 | 97.7308 | 97.5103 | 97.1462 | 97.4064 | 2018-10-01 | 2020-05-11
LG Electronics Inc. | D007KEEN261 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 7.68 | 240 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [08/30/2018] | [1.4.1] | 2018-10-15 | [08/30/2018] | 2020-05-11 | CSA Group | 2020-03-26 | 2020-05-11 |  | Y | N | 1.19 |  |  | 270 | 380 | 450 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.1418 | 96.5566 | 97.3325 | 97.5972 | 97.5104 | 97.1304 | 97.3459 | 96.4957 | 97.6782 | 98.0328 | 98.0644 | 97.7762 | 97.4311 | 97.7942 | 95.7683 | 97.3217 | 97.8155 | 97.9581 | 97.748 | 97.4471 | 97.6847 | 2018-10-01 | 2020-05-11
LG Electronics Inc. | P250KH53231 {480V} | N | N | Y | Y | Y | Y | Y | N | 250 kW, 480 Vac, Bi-directional, 3 phase Grid Support Utility Interactive Battery Inverter | 250.425 | 480 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [06/03/2021] | [01.00] | 2021-10-21 | [06/03/2021] | 2021-10-21 | SunSpec Alliance | 2020-07-03 | No Information Submitted | Efficiency data inclusive of transformer effect based on 300 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE2016. | N | N | 4.21 |  |  | 750 | 881 | 1000 | 25.0425 | 50.085 | 75.1276 | 125.2126 | 187.8189 | 250.4252 | 95.4281 | 96.528 | 96.9446 | 97.2414 | 97.3147 | 97.29 | 97.1389 | 94.908 | 96.2014 | 96.6189 | 96.9729 | 97.0742 | 97.0491 | 96.8668 | 94.3188 | 95.8647 | 96.3501 | 96.7377 | 96.8651 | 96.8152 | 96.6222 | 2021-10-21
LG Energy Solution, Ltd. | SHB-G1-050-US {240V} | N | Y | N | N | N | N | Y* | N | 5 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 4.9828 | 240 | 96 | CSA Group | [7/13/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-07-13 | No Information Submitted |  | N | N | 5.6 |  |  | 105 | 300 | 495 | 0.49828 | 0.99656 | 1.4948 | 2.4914 | 3.7371 | 4.9828 | 93.0286 | 95.1786 | 95.4186 | 95.81 | 95.61 | 94.3929 | 95.4433 | 94.29 | 95.9986 | 96.2543 | 96.4986 | 96.2243 | 96.6271 | 96.217 | 94.24 | 95.8229 | 96.3386 | 96.5929 | 96.5429 | 96.3671 | 96.3919 | 2024-04-22
LG Energy Solution, Ltd. | SHB-G1-060-US {240V} | N | Y | N | N | N | N | Y* | N | 6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 6.0097 | 240 | 96 | CSA Group | [7/13/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-07-13 | No Information Submitted |  | N | N | 5.6 |  |  | 125 | 300 | 495 | 0.60097 | 1.2019 | 1.8029 | 3.0048 | 4.5073 | 6.0097 | 92.7214 | 95.0743 | 95.43 | 95.7486 | 95.7086 | 94.3271 | 95.4633 | 94.6529 | 96.01 | 96.2829 | 96.3057 | 96.36 | 96.9286 | 96.282 | 95.6686 | 96.4657 | 96.78 | 96.7214 | 96.49 | 96.2014 | 96.5249 | 2024-04-22
LG Energy Solution, Ltd. | SHB-G1-076-US {240V} | N | Y | N | N | N | N | Y* | N | 7.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 7.5855 | 240 | 96 | CSA Group | [7/13/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-07-13 | No Information Submitted |  | N | N | 5.61 |  |  | 158 | 300 | 495 | 0.75855 | 1.5171 | 2.2756 | 3.7927 | 5.6891 | 7.5855 | 93.5571 | 95.2629 | 95.6457 | 96.3743 | 95.8329 | 94.9829 | 95.7621 | 94.7457 | 95.6714 | 96.3529 | 96.2671 | 96.5757 | 96.8329 | 96.3786 | 94.4143 | 95.3957 | 96.0771 | 96.15 | 95.9786 | 95.6943 | 95.9205 | 2024-04-22
LG Energy Solution, Ltd. | SHB-G1-096-US {240V} | N | Y | N | N | N | N | Y* | N | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter with PCS functionality. | 9.6031 | 240 | 96 | CSA Group | [7/13/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-07-13 | No Information Submitted |  | N | N | 5.61 |  |  | 200 | 300 | 495 | 0.96031 | 1.9206 | 2.8809 | 4.8015 | 7.2023 | 9.6031 | 93.6829 | 95.3486 | 95.6429 | 96.47 | 95.9143 | 95.2143 | 95.8459 | 94.49 | 95.9371 | 96.2043 | 96.16 | 96.8057 | 96.4157 | 96.4424 | 94.3943 | 96.0357 | 96.3371 | 96.3786 | 96.1443 | 96.5543 | 96.1617 | 2024-04-22 | 2025-01-13
LG Energy Solution, Ltd. | SHB-G1-114-US {240V} | N | Y | N | N | N | N | Y* | N | 11.4 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 11.3919 | 240 | 96 | CSA Group | [7/13/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-07-13 | No Information Submitted |  | N | N | 5.61 |  |  | 235 | 300 | 495 | 1.1392 | 2.2784 | 3.4176 | 5.6959 | 8.5439 | 11.3919 | 94.32 | 95.6357 | 95.7729 | 96.4757 | 95.7914 | 95.1371 | 95.8335 | 95.15 | 96.1857 | 96.27 | 96.0443 | 96.5486 | 96.0214 | 96.3088 | 94.5386 | 96.0657 | 96.2914 | 96.2114 | 95.8529 | 96.2186 | 95.9571 | 2024-04-22
Liniotech Energy Inc. | LNT5K0228UL {208V} | Y | Y | N | N | N | N | N | N | 5 kW, 208Vac Grid Support Utility Interactive PV and Battery Inverter | 5.02 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 92.68 | 95.27 | 95.93 | 96.35 | 96.16 | 95.99 | 95.98 | 93.57 | 95.86 | 96.53 | 97.03 | 97.08 | 96.97 | 96.8 | 93.73 | 95.93 | 96.5 | 96.81 | 96.9 | 96.81 | 96.65 | 2024-09-11
Liniotech Energy Inc. | LNT5K0228UL {240V} | Y | Y | N | N | N | N | N | N | 5 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 5.04 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.504 | 1.008 | 1.512 | 2.52 | 3.78 | 5.04 | 92.99 | 95.51 | 96.13 | 96.56 | 96.34 | 96.22 | 96.18 | 93.67 | 95.99 | 96.75 | 97.31 | 97.43 | 97.38 | 97.1 | 93.79 | 96.14 | 96.61 | 96.98 | 97.24 | 97.24 | 96.92 | 2024-09-11
Liniotech Energy Inc. | LNT6K0228UL {208V} | Y | Y | N | N | N | N | N | N | 6 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 6.124 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.612 | 1.225 | 1.837 | 3.062 | 4.593 | 6.124 | 91.51 | 94.38 | 95.44 | 96.15 | 96.2 | 96.02 | 95.81 | 93.61 | 95.95 | 96.7 | 97.16 | 97.14 | 97.02 | 96.88 | 93.01 | 95.45 | 96.32 | 96.9 | 96.93 | 96.76 | 96.61 | 2024-09-11
Liniotech Energy Inc. | LNT6K0228UL {240V} | Y | Y | N | N | N | N | N | N | 6 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 6.149 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.615 | 1.23 | 1.845 | 3.075 | 4.612 | 6.149 | 91.6 | 94.45 | 95.46 | 96.26 | 96.41 | 96.35 | 95.97 | 93.87 | 96.14 | 96.88 | 97.38 | 97.49 | 97.42 | 97.18 | 92.69 | 95.45 | 96.41 | 97.1 | 97.3 | 97.27 | 96.87 | 2024-09-11
Liniotech Energy Inc. | LNT7K0228UL {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 7.647 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.529 | 2.294 | 3.824 | 5.735 | 7.647 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 89.75 | 96.08 | 96.79 | 97.16 | 96.97 | 96.77 | 96.65 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2024-09-11
Liniotech Energy Inc. | LNT7K0228UL {208V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 7.648 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.53 | 2.294 | 3.824 | 5.736 | 7.648 | 92.95 | 95.54 | 96.21 | 96.65 | 96.45 | 96.19 | 96.26 | 93.74 | 96.07 | 96.79 | 97.16 | 96.97 | 96.77 | 96.8 | 94.06 | 96.23 | 96.77 | 97.12 | 96.91 | 96.7 | 96.78 | 2024-09-11
Liniotech Energy Inc. | LNT8K0228UL {240V} | Y | Y | N | N | N | N | N | N | 8 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 8.047 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.805 | 1.609 | 2.414 | 4.024 | 6.035 | 8.047 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 93.75 | 96.08 | 96.8 | 97.17 | 96.97 | 96.77 | 96.81 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2024-09-11
Liniotech Energy Inc. | LNT8K0228UL {208V} | Y | Y | N | N | N | N | N | N | 8 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 8.06 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 17.78 |  |  | 200 | 360 | 480 | 0.806 | 1.612 | 2.418 | 4.03 | 6.045 | 8.06 | 92.85 | 95.45 | 96.11 | 96.55 | 96.35 | 96.09 | 96.17 | 93.65 | 95.98 | 96.69 | 97.06 | 96.87 | 96.67 | 96.71 | 93.97 | 96.14 | 96.67 | 97.02 | 96.81 | 96.55 | 96.68 | 2024-09-11
Liniotech Energy Inc. | LNT12K0228UL {240V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 10.14 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.028 | 3.042 | 5.07 | 7.605 | 10.14 | 93.05 | 95.58 | 96.24 | 96.66 | 96.45 | 96.2 | 96.28 | 93.72 | 96.07 | 96.82 | 97.15 | 96.96 | 96.78 | 96.8 | 94.05 | 96.25 | 96.79 | 97.12 | 96.92 | 96.66 | 96.79 | 2024-09-11
Liniotech Energy Inc. | LNT10K0228UL {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 10.147 | 240 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.015 | 2.029 | 3.044 | 5.074 | 7.61 | 10.147 | 93 | 95.58 | 96.22 | 96.66 | 96.46 | 96.2 | 96.28 | 93.79 | 96.1 | 96.81 | 97.16 | 96.97 | 96.77 | 96.81 | 94.11 | 96.27 | 96.78 | 97.13 | 96.92 | 96.66 | 96.79 | 2024-09-11
Liniotech Energy Inc. | LNT10K0228UL {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 10.186 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.89 | 95.48 | 96.13 | 96.56 | 96.36 | 96.1 | 96.18 | 93.7 | 96.01 | 96.71 | 97.07 | 96.88 | 96.67 | 96.72 | 94.02 | 96.16 | 96.68 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-09-11
Liniotech Energy Inc. | LNT12K0228UL {208V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 10.186 | 208 | 96.5 | SGS | [5/30/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.91 | 95.48 | 96.12 | 96.56 | 96.36 | 96.1 | 96.18 | 93.66 | 96.02 | 96.72 | 97.07 | 96.88 | 96.68 | 96.72 | 94.07 | 96.17 | 96.67 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-09-11
Lion Energy | #50170167 Sanctuary 8K {208V} | Y | Y | Y | Y | Y | N | N | N | 8 kW, 208 Vac, Grid Support Utility Interactive Inverter | 7.827 | 208 | 94.5 | SGS | [3/2/2023] | SGS | [5/27/2021] | [COMM: f23b; MCU: Ver1585] | 2022-07-21 | [5/27/2021] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 14.2 |  |  | 240 | 370 | 425 | 0.78272 | 1.5654 | 2.3482 | 3.9136 | 5.8704 | 7.8272 | 91.5935 | 94.5306 | 94.7008 | 94.8172 | 94.2661 | 93.7306 | 94.3136 | 92.4554 | 95.1969 | 95.3682 | 95.4678 | 94.995 | 94.4074 | 95.0182 | 91.4596 | 94.7987 | 94.9704 | 95.2764 | 94.8404 | 94.2929 | 94.7828 | 2022-07-21 | 2023-04-03
Lion Energy | #50170167 Sanctuary 8K {240V} | Y | Y | Y | Y | Y | N | N | N | 8 kW, 240 Vac, Grid Support Utility Interactive Inverter | 7.898 | 240 | 95 | SGS | [3/2/2023] | SGS | [5/27/2021] | [COMM: f23b; MCU: Ver1585] | 2022-07-21 | [5/27/2021] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 18.8 |  |  | 240 | 370 | 425 | 0.7898 | 1.5796 | 2.3694 | 3.949 | 5.9235 | 7.898 | 91.6179 | 94.6876 | 94.7932 | 95.0759 | 94.5989 | 94.128 | 94.584 | 92.6051 | 95.3425 | 95.4495 | 95.7148 | 95.3412 | 94.8314 | 95.2978 | 91.4912 | 94.8318 | 95.0468 | 95.5105 | 95.268 | 94.8354 | 95.0979 | 2022-07-21 | 2023-04-03
Lion Energy | #50170168 {240V} | Y | Y | Y | Y | Y | Y | N | N | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 8.084 | 240 | 97.5 | SGS | [3/30/2023] | SGS | [3/30/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-05-21 | [3/29/2024] | 2024-05-21 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2023-06-01 | 2024-05-21
Lion Energy | Lion Hybrid Inverter 12kW {240V} | Y | Y | Y | Y | Y | N | N |  | 12 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 8.084 | 240 | 97.5 | SGS | [7/17/2024] | SGS | [6/27/2024] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-22 | [7/17/2024] | 2025-09-22 | CSA Group | 2024-12-16 |  |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.808 | 1.617 | 2.425 | 4.042 | 6.063 | 8.084 | 93.98 | 95.42 | 96.35 | 97.36 | 97.92 | 96.85 | 97.27 | 93.95 | 95.64 | 96.59 | 97.27 | 97.93 | 97.01 | 97.31 | 94.07 | 95.49 | 96.43 | 97.32 | 97.69 | 96.99 | 97.17 | 2025-09-22 | 2026-08-11 | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 12kW {208V} | Y | Y | Y | Y | Y | Y | N |  | 12 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter | 8.138 | 208 | 96.5 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2026-10-01 | 2026-06-24 | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 0.002 |  |  | 150 | 360 | 430 | 0.814 | 1.628 | 2.441 | 4.069 | 6.103 | 8.138 | 94.07 | 95.83 | 96.51 | 96.74 | 96.59 | 96.06 | 96.45 | 94.22 | 96.05 | 96.58 | 96.83 | 96.63 | 96.32 | 96.52 | 94.26 | 96.4 | 96.64 | 96.8 | 96.71 | 96.4 | 96.59 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 12kW {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 12 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 8.181 | 240 | 96 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2025-12-11 | 2025-05-09 | 2025-12-11 | CSA Group | 2025-05-10 |  |  | N | N | 19.254 |  |  | 150 | 360 | 430 | 0.818 | 1.636 | 2.454 | 4.09 | 6.136 | 8.181 | 93.94 | 95.38 | 95.75 | 95.92 | 95.52 | 95.56 | 95.56 | 94.31 | 96.22 | 96.68 | 96.84 | 96.58 | 96.23 | 96.52 | 93.94 | 96.07 | 96.62 | 96.93 | 96.77 | 96.24 | 96.61 | 2025-12-11 | 2026-10-01 | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Lion Hybrid Inverter 15kW {240V} | Y | Y | Y | Y | Y | N | N |  | 15 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality | 10.177 | 240 | 97 | SGS | [7/17/2024] | SGS | [6/27/2024] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-22 | [7/17/2024] | 2025-09-22 | CSA Group | 2024-12-16 |  |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.018 | 2.035 | 3.053 | 5.088 | 7.632 | 10.177 | 94.69 | 95.94 | 96.4 | 96.8 | 97.34 | 96.75 | 96.91 | 95.39 | 96.33 | 96.85 | 97.45 | 97.97 | 97.37 | 97.51 | 94.93 | 95.96 | 96.65 | 97.01 | 97.56 | 97.03 | 97.12 | 2025-09-22 | 2026-08-11 | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 18kW {208V} | Y | Y | Y | Y | Y | Y | N |  | 18 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter | 12.185 | 208 | 96 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2026-10-01 | 2026-06-24 | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 0.002 |  |  | 200 | 360 | 430 | 1.218 | 2.437 | 3.655 | 6.092 | 9.139 | 12.185 | 93.6 | 95.32 | 95.65 | 95.89 | 95.5 | 95.59 | 95.52 | 94.53 | 96.35 | 96.63 | 96.81 | 96.5 | 96.61 | 96.5 | 94.51 | 96.12 | 96.6 | 96.89 | 96.7 | 96.46 | 96.6 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 18kW {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 18 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 12.214 | 240 | 96 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2025-12-11 | 2025-05-09 | 2025-12-11 | CSA Group | 2025-05-10 |  |  | N | N | 13.202 |  |  | 200 | 360 | 430 | 1.221 | 2.443 | 3.664 | 6.107 | 9.16 | 12.214 | 93.59 | 95.32 | 95.52 | 95.8 | 95.49 | 95.61 | 95.48 | 94.26 | 96.13 | 96.66 | 96.87 | 96.62 | 96.29 | 96.54 | 94 | 96.18 | 96.74 | 96.88 | 96.68 | 96.36 | 96.58 | 2025-12-11 | 2026-10-01 | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 24kW {208V} | Y | Y | Y | Y | Y | Y | N |  | 24 kW, 208 Vac Grid Support Hybrid Utility Interactive Inverter | 16.178 | 208 | 96 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2026-10-01 | 2026-06-24 | 2026-10-01 | No Information Submitted | No Information Submitted |  |  | N | N | 0.002 |  |  | 220 | 360 | 430 | 1.618 | 3.236 | 4.854 | 8.089 | 12.134 | 16.178 | 93.95 | 95.2 | 95.77 | 95.85 | 95.48 | 95.39 | 95.51 | 94.47 | 96.42 | 96.58 | 96.83 | 96.53 | 96.55 | 96.51 | 94.28 | 96.29 | 96.57 | 96.81 | 96.74 | 96.43 | 96.6 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lion Energy | Sanctuary 3 Inverter 24kW {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 24 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 16.199 | 240 | 96 | SGS | [7/8/2026] | SGS | [7/8/2026] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2025-12-11 | 2025-05-09 | 2025-12-11 | CSA Group | 2025-05-10 |  |  | N | N | 20.465 |  |  | 220 | 360 | 430 | 1.62 | 3.24 | 4.86 | 8.099 | 12.149 | 16.199 | 93.66 | 95.36 | 95.8 | 95.93 | 95.51 | 96.18 | 95.59 | 94.19 | 96.06 | 96.55 | 96.88 | 96.64 | 96.35 | 96.53 | 94.09 | 96 | 96.54 | 96.95 | 96.69 | 96.25 | 96.57 | 2025-12-11 | 2026-10-01 | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Lite-On Technology Corporation | IN-HP5123US {120V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 120 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.0186 | 120 | 95.5 | Intertek | [12/27/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-11-01 | [9/10/2024] | 2024-11-01 | CSA Group | 2025-04-08 | 2025-04-21 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.846 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.218 | 95.95 | 95.686 | 95.0375 | 2024-11-01 | 2025-04-21
Lite-On Technology Corporation | IN-HP5123US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 9.0186 | 240 | 95.5 | Intertek | [12/27/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2025-01-02 | [9/10/2024] | 2025-01-02 | CSA Group | 2025-04-08 | 2025-04-21 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.846 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.218 | 95.95 | 95.686 | 95.0375 | 2025-01-02 | 2025-04-21
Lite-On Technology Corporation | IN-HP5113US {240V} | Y | Y | N | N | N | N | Y* |  | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality | 11.361 | 240 | 97.5 | CSA Group | [6/30/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-06-30 |  |  | N | N | 13.3488 |  |  | 257 | 380 | 500 | 1.136 | 2.272 | 3.408 | 5.681 | 8.521 | 11.361 | 95.49 | 97.1 | 97.35 | 97.53 | 97.25 | 96.93 | 97.23 | 96.37 | 97.38 | 97.78 | 97.58 | 97.5 | 97.45 | 97.5 | 95.43 | 97.32 | 97.56 | 97.68 | 97.51 | 97.19 | 97.44 | 2025-09-02
LS ELECTRIC Co Ltd | LSPB-BB-0150-48-2T {480V} | N | Y | Y | Y | Y | Y | Y* |  | 151.403 kW, 480 Vac Grid Support Utility Interactive Battery Inverter | 151.403 | 480 | 98 | UL | [9/26/2025] | UL | [9/26/2025] | [1.3.1] | 2026-09-01 | [9/26/2025] | 2026-09-01 | UL | 2026-07-01 |  |  | N | N | 0 |  |  | 800 | 1300 | 1500 | 15.14 | 30.281 | 45.421 | 75.702 | 113.552 | 151.403 | 98.62 | 99.03 | 99.09 | 99.01 | 98.8 | 98.54 | 98.87 | 95.61 | 97.26 | 97.76 | 98.02 | 97.96 | 97.8 | 97.81 | 94.13 | 96.33 | 97.06 | 97.5 | 97.52 | 97.38 | 97.26 | 2026-09-01 |  | N | Y | N | N | N | N | Y | N | No Information Submitted
LS ELECTRIC Co Ltd | LSPB-BB-0190-60-2T {600V} | N | Y | Y | Y | Y | Y | Y* |  | 191.856 kW, 600 Vac Grid Support Utility Interactive Battery Inverter | 191.856 | 600 | 98.5 | UL | [9/26/2025] | UL | [9/26/2025] | [1.3.1] | 2026-09-01 | [9/26/2025] | 2026-09-01 | UL | 2026-07-01 |  |  | N | N | 0 |  |  | 990 | 1300 | 1500 | 19.186 | 38.371 | 57.557 | 95.928 | 143.892 | 191.856 | 98.49 | 98.98 | 99.09 | 99.06 | 98.91 | 98.67 | 98.94 | 97 | 98.1 | 98.44 | 98.58 | 98.5 | 98.32 | 98.42 | 95.76 | 97.39 | 97.9 | 98.18 | 98.14 | 98 | 97.98 | 2026-09-01 |  | N | Y | N | N | N | N | Y | N | No Information Submitted
LS ELECTRIC Co Ltd | LSPB-BB-0220-69-2T {690V} | N | Y | Y | Y | Y | Y | Y* |  | 222.17 kW, 690 Vac Grid Support Utility Interactive Battery Inverter | 222.17 | 690 | 98.5 | UL | [9/26/2025] | UL | [9/26/2025] | [1.3.1] | 2026-09-01 | [9/26/2025] | 2026-09-01 | UL | 2026-07-01 |  |  | N | N | 0 |  |  | 1125 | 1300 | 1500 | 22.217 | 44.434 | 66.651 | 111.085 | 166.628 | 222.17 | 98.43 | 98.96 | 99.09 | 99.09 | 98.9 | 98.75 | 98.94 | 97.71 | 98.53 | 98.77 | 98.85 | 98.75 | 98.55 | 98.71 | 96.61 | 97.93 | 98.33 | 98.53 | 98.48 | 98.33 | 98.36 | 2026-09-01 |  | N | Y | N | N | N | N | Y | N | No Information Submitted
LS Energy Solutions LLC | PBE-6140-R61-1A0-1000 {600V} | N | N | Y | Y | Y | Y | Y* | Y | 140 kVA, 600 Vac, Bi-directional Grid Support Utility Interactive Energy Storage Inverter | 139.449 | 600 | 98 | No Information Submitted | No Information Submitted | Intertek | [06/18/2021] | [2.0] | 2020-08-11 | [06/18/2021] | 2021-08-02 | Intertek | 2021-07-08 | 2021-08-02 |  | N | N | 1.58 |  |  | 900 | 1125 | 1350 | 13.9449 | 27.8898 | 41.8346 | 69.7244 | 104.5866 | 139.4488 | 97.4036 | 98.309 | 98.4912 | 98.7182 | 98.6138 | 98.533 | 98.5533 | 96.7152 | 97.8982 | 98.2252 | 98.3488 | 98.378 | 98.282 | 98.2582 | 96.0238 | 97.3794 | 97.74 | 98.0456 | 98.0902 | 98.0034 | 97.9163 | 2020-08-11 | 2021-08-02
LS Energy Solutions LLC | PBE-5140-R61-1A0-1000 {480V} | N | N | Y | Y | Y | Y | Y* | Y | 140 kVA, 480 Vac, Bi-directional Grid Support Utility Interactive Energy Storage Inverter | 140.485 | 480 | 98 | No Information Submitted | No Information Submitted | Intertek | [06/18/2021] | [2.0] | 2020-08-11 | [06/18/2021] | 2021-08-02 | Intertek | 2021-07-08 | 2021-08-02 |  | N | N | 1.5 |  |  | 720 | 935 | 1150 | 14.0485 | 28.097 | 42.1455 | 70.2425 | 105.3638 | 140.485 | 97.5 | 98.3658 | 98.4438 | 98.5204 | 98.4466 | 98.3362 | 98.4143 | 96.596 | 97.653 | 97.9814 | 98.1558 | 98.0944 | 97.9973 | 98.0069 | 95.592 | 97.1282 | 97.6164 | 97.7772 | 97.8094 | 97.6214 | 97.6473 | 2020-08-11 | 2021-08-02
Lunar Energy, Inc. | 10-005025 {240V} | Y | Y | N | N | N | N | Y* | N | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 9.675 | 240 | 95.5 | CSA Group | [1/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-10-23 | No Information Submitted |  | N | N | 29.61 |  |  | 380 | 415 | 450 | 0.967 | 1.935 | 2.902 | 4.837 | 7.256 | 9.675 | 90.73 | 94.46 | 95.73 | 96.51 | 96.64 | 96.43 | 96.15 | 89.53 | 93.61 | 95.12 | 96.09 | 96.32 | 96.16 | 95.71 | 87.44 | 92.74 | 94.32 | 95.59 | 95.91 | 95.83 | 95.15 | 2024-11-21 | 2025-10-21
MANGO POWER TECH INC. | M Hybrid Inverter 12kW {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.499 | 208 | 96.5 | Intertek | [9/13/2024] | Intertek | [9/13/2024] | [fA1.0] | 2024-12-11 | [8/26/2024] | 2024-12-11 | Intertek | 2022-07-26 | 2024-12-11 |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.05 | 2.1 | 3.15 | 5.25 | 7.875 | 10.499 | 93.48 | 95.27 | 95.93 | 95.85 | 95.61 | 95.29 | 95.58 | 95.07 | 96.66 | 97.03 | 97.31 | 97.1 | 96.41 | 96.99 | 94.29 | 96.71 | 97.16 | 96.95 | 96.77 | 96.47 | 96.74 | 2024-12-11
MANGO POWER TECH INC. | M Hybrid Inverter 12kW {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 11.933 | 240 | 97 | Intertek | [9/13/2024] | Intertek | [9/13/2024] | [fA1.0] | 2024-12-11 | [8/26/2024] | 2024-12-11 | Intertek | 2022-07-26 | 2024-12-11 |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.193 | 2.387 | 3.58 | 5.966 | 8.949 | 11.933 | 95.02 | 96.1 | 96.54 | 96.5 | 96.13 | 95.9 | 96.2 | 96.59 | 97.19 | 97.51 | 97.34 | 97.24 | 97.1 | 97.26 | 95.82 | 97.01 | 97.42 | 97.26 | 97.14 | 97.04 | 97.13 | 2024-12-11
MidNite Power Inc. | MN 15-12KW-AIO {240V} | Y | Y | N | N | N | N | Y* |  | 10.135 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 10.135 | 240 | 96.5 | SGS | [7/28/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-07-15 |  |  | N | N | 19.44 |  |  | 200 | 360 | 480 | 1.014 | 2.027 | 3.041 | 5.068 | 7.601 | 10.135 | 93.07 | 95.57 | 96.3 | 96.64 | 96.44 | 96.21 | 96.28 | 93.68 | 96.04 | 96.8 | 97.14 | 96.95 | 96.78 | 96.79 | 94.05 | 96.32 | 96.82 | 97.12 | 96.93 | 96.65 | 96.8 | 2025-12-22
MidNite Power Inc. | MN 15-12KW-AIO {208V} | Y | Y | N | N | N | N | Y* |  | 10.193 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 10.193 | 208 | 96.5 | SGS | [7/28/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-07-15 |  |  | N | N | 18.56 |  |  | 200 | 360 | 480 | 1.019 | 2.039 | 3.058 | 5.097 | 7.645 | 10.193 | 92.89 | 95.49 | 96.11 | 96.57 | 96.35 | 96.1 | 96.18 | 93.64 | 96.03 | 96.72 | 97.06 | 96.88 | 96.68 | 96.72 | 94.1 | 96.17 | 96.67 | 97 | 96.82 | 96.56 | 96.69 | 2025-12-22
MidNite Solar, Inc. | MN 15-12KW-AIO {240V} | Y | Y | N | N | N | N | Y* | N | 15 kW, 240 Vac Grid Support Interactive Hybrid Inverter with PCS functionality. | 10.135 | 240 | 96.6 | SGS | [5/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2025-04-23 | No Information Submitted |  | N | N | 19.44 |  |  | 200 | 360 | 480 | 1.014 | 2.027 | 3.041 | 5.068 | 7.601 | 10.135 | 93.07 | 95.57 | 96.3 | 96.64 | 96.44 | 96.21 | 96.28 | 93.68 | 96.04 | 96.8 | 97.14 | 96.95 | 96.78 | 96.79 | 94.05 | 96.32 | 96.82 | 97.12 | 96.93 | 96.65 | 96.8 | 2024-07-11 | 2025-10-01
MPP SOLAR INC | LVX 12KW WP {120V} | Y | Y | N | N | N | N | N | N | 10 kW, 120 Vac Grid Support Utility Interactive Inverter | 9.0186 | 120 | 95.5 | Intertek | [2/6/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-10-01
MPP SOLAR INC | LVX 12KW WP {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.0186 | 240 | 95.5 | Intertek | [2/6/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-10-01
NeoVolta Inc. | NV7600 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7680 W, 208 Vac, 1-phase hybrid Grid Support Utility Interactive Inverter that works with PV and energy storage. Inverter is capable of PCS functionality. | 7.4473 | 208 | 96.5 | SGS | [7/14/2022] | SGS | [02/18/2019] | [Ver1585] | 2019-03-15 | [02/18/2019] | 2020-08-11 | CSA Group | 2020-06-22 | 2020-08-11 | The NV7600 inverter and batteries are components of the NV14 Energy Storage System. | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.74473 | 1.4895 | 2.2342 | 3.7237 | 5.5855 | 7.4473 | 91.4863 | 94.7602 | 95.3527 | 97.2963 | 97.1851 | 96.8599 | 96.6231 | 91.7 | 94.9639 | 95.4957 | 97.4288 | 97.2316 | 96.9297 | 96.715 | 91.9073 | 94.929 | 95.3698 | 97.3187 | 96.9256 | 97.0631 | 96.5278 | 2019-03-15 | 2022-12-01
NeoVolta Inc. | NV7600 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7680W, 240 Vac, 1-phase hybrid Grid Support Utility Interactive Inverter that works with PV and energy storage. Inverter is capable of PCS functionality. | 7.657 | 240 | 96.5 | SGS | [7/14/2022] | SGS | [02/18/2019] | [Ver1585] | 2019-03-15 | [02/18/2019] | 2020-08-11 | CSA Group | 2020-06-22 | 2020-08-11 | The NV7600 inverter and batteries are components of the NV14 Energy Storage System. | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.76571 | 1.5314 | 2.2971 | 3.8286 | 5.7428 | 7.6571 | 91.8196 | 94.911 | 95.5205 | 97.0796 | 96.988 | 97.1305 | 96.5277 | 91.6709 | 95.0008 | 95.7077 | 97.5465 | 97.4459 | 97.0835 | 96.8871 | 91.5513 | 95.0717 | 95.8584 | 97.6006 | 97.274 | 97.0868 | 96.8243 | 2019-03-15 | 2022-12-01
NeoVolta Inc. | NV12KAC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 12.0 kW, 240Vac, 1-Phase & 3-Phase Grid Support Utility Interactive Hybrid Inverter that works with PV and energy storage | 12.2135 | 240 | 96 | SGS | [8/18/2025] | SGS | [8/18/2025] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2025-11-21 | [8/18/2025] | 2025-11-21 | SGS | 2025-08-18 |  |  | N | N | 13.2 |  |  | 200 | 360 | 430 | 1.2214 | 2.4427 | 3.6641 | 6.1068 | 9.1601 | 12.2135 | 93.588 | 95.318 | 95.52 | 95.804 | 95.494 | 95.612 | 95.4831 | 94.262 | 96.132 | 96.662 | 96.872 | 96.622 | 96.294 | 96.544 | 94.002 | 96.18 | 96.74 | 96.876 | 96.678 | 96.362 | 96.5793 | 2025-11-21
NeoVolta Inc. | NV16KAC {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 16.0 kW, 240Vac, 1-Phase & 3-Phase Grid Support Utility Interactive Hybrid Inverter that works with PV and energy storage | 16.199 | 240 | 96 | SGS | [8/18/2025] | SGS | [8/18/2025] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2025-11-21 | [8/18/2025] | 2025-11-21 | SGS | 2025-08-18 |  |  | N | N | 20.47 |  |  | 220 | 360 | 430 | 1.62 | 3.24 | 4.86 | 8.099 | 12.149 | 16.199 | 93.66 | 95.36 | 95.8 | 95.93 | 95.51 | 96.18 | 95.59 | 94.19 | 96.06 | 96.55 | 96.88 | 96.64 | 96.35 | 96.53 | 94.09 | 96 | 96.54 | 96.95 | 96.69 | 96.25 | 96.57 | 2025-11-21
NEXTRACKER LLC | NXPCS800K-HUD {800V} | Y | Y | N | N | N | N | N | N | 800 kW, 800 Vac Grid Support Power Conversion System with a 800 kVA liquid-immersed distribution transformer. | 801.42 | 800 | 98 | Intertek | [11/4/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 222.84 |  |  | 1200 | 1350 | 1500 | 80.142 | 160.284 | 240.426 | 400.71 | 601.065 | 801.42 | 96.8652 | 98.0112 | 98.3614 | 98.3467 | 98.2464 | 97.9889 | 98.2014 | 96.7678 | 97.9399 | 98.2903 | 98.3257 | 98.1778 | 97.9753 | 98.1439 | 96.6558 | 97.8785 | 98.2331 | 98.2773 | 98.1877 | 97.9314 | 98.1224 | 2023-05-11
NEXTRACKER LLC | NXPCS1670K-HUD {800V} | Y | Y | N | N | N | N | N | N | 1670 kW, 800 Vac Grid Support Power Conversion System with a 1670 kVA liquid-immersed distribution transformer | 1673.4 | 800 | 98.5 | Intertek | [11/4/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 223.1 |  |  | 1200 | 1350 | 1500 | 167.34 | 334.68 | 502.02 | 836.7 | 1255.05 | 1673.4 | 97.1002 | 98.1991 | 98.4358 | 98.4485 | 98.3052 | 98.1498 | 98.2897 | 96.9903 | 98.1322 | 98.3783 | 98.4244 | 98.2715 | 98.1189 | 98.2506 | 96.8708 | 98.0743 | 98.3233 | 98.3951 | 98.2361 | 98.0867 | 98.2098 | 2023-05-11
NEXTRACKER LLC | NXPCS3340K-HUD {800V} | Y | Y | N | N | N | N | N | N | 3340 kW, 800 Vac Grid Support Power Conversion System with a 3340 kVA liquid-immersed distribution transformer | 3347.8 | 800 | 98.5 | Intertek | [11/4/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 443.65 |  |  | 1200 | 1350 | 1500 | 334.78 | 669.56 | 1004.34 | 1673.9 | 2510.85 | 3347.8 | 97.3162 | 98.2973 | 98.567 | 98.5482 | 98.4398 | 98.2414 | 98.4158 | 97.1663 | 98.2314 | 98.5122 | 98.5619 | 98.4077 | 98.1954 | 98.3835 | 97.0754 | 98.1596 | 98.4893 | 98.4686 | 98.3606 | 98.1888 | 98.3287 | 2023-05-11
NEXTRACKER LLC | NXPCS5000K-HUD {800V} | Y | Y | N | N | N | N | N | N | 5000 kW, 800 Vac Grid Support Power Conversion System a 5000 kVA liquid-immersed distribution transformer | 5004.9 | 800 | 98.5 | Intertek | [11/4/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 638.04 |  |  | 1200 | 1350 | 1500 | 500.49 | 1000.98 | 1501.47 | 2502.45 | 3753.675 | 5004.9 | 97.3771 | 98.3426 | 98.6085 | 98.6082 | 98.4969 | 98.2626 | 98.4695 | 97.2268 | 98.269 | 98.5468 | 98.5963 | 98.4512 | 98.2467 | 98.4248 | 97.1517 | 98.2154 | 98.507 | 98.5246 | 98.4233 | 98.2089 | 98.3826 | 2023-05-11
Northern Electric & Power Co. Ltd | BDHX-2000T-208 {208V} | Y | Y | N | N | N | N | Y* |  | 2.078 kW, 208 Vac Grid Support Utility Interactive Microinverter | 2.078 | 208 | 95.5 | Intertek | [4/3/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2026-03-19 |  |  | N | Y | 0.54 |  |  | 22 | 37 | 55 | 0.208 | 0.416 | 0.624 | 1.039 | 1.559 | 2.078 | 95.48 | 95.55 | 95.36 | 95.92 | 95.57 | 95.7 | 95.62 | 95.59 | 95.51 | 95.67 | 95.92 | 95.57 | 95.69 | 95.66 | 95.59 | 95.81 | 95.7 | 95.92 | 95.57 | 95.78 | 95.68 | 2026-07-21 |  | Y | N | N | N | N | N | Y | N | N
Northern Electric & Power Co. Ltd | BDH-8KSP-LB {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 8 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 6.9318 | 208 | 96.5 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.26 |  |  | 220 | 360 | 500 | 0.69318 | 1.3864 | 2.0795 | 3.4659 | 5.1989 | 6.9318 | 94.8824 | 95.1559 | 96.3164 | 96.1494 | 95.5083 | 95.3277 | 95.6882 | 95.5148 | 96.247 | 97.1412 | 96.7237 | 96.2569 | 96.1172 | 96.4239 | 96.9461 | 97.549 | 98.4544 | 98.0507 | 97.2182 | 97.2592 | 97.5491 | 2025-10-13
Northern Electric & Power Co. Ltd | BDH-8KSP-LB {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 8 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.99 | 240 | 97 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.56 |  |  | 220 | 360 | 500 | 0.799 | 1.598 | 2.397 | 3.995 | 5.993 | 7.99 | 95.48 | 96.12 | 96.98 | 96.71 | 96.05 | 95.48 | 96.25 | 95.99 | 97.25 | 98.05 | 97.46 | 96.95 | 96.48 | 97.14 | 96.37 | 97.29 | 98.33 | 98.08 | 97.88 | 97.11 | 97.85 | 2025-10-13
Northern Electric & Power Co. Ltd | BDH-10KSP-LB {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 8.671 | 208 | 96.5 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.22 |  |  | 220 | 360 | 500 | 0.867 | 1.734 | 2.601 | 4.336 | 6.503 | 8.671 | 94.64 | 95.52 | 96.33 | 95.96 | 95.58 | 95.35 | 95.7 | 95.54 | 96.3 | 97.06 | 96.86 | 96.55 | 96.2 | 96.61 | 96.16 | 97.09 | 97.88 | 97.5 | 97.52 | 96.94 | 97.45 | 2025-10-13
Northern Electric & Power Co. Ltd | BDH-10KSP-LB {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.9914 | 240 | 97 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.53 |  |  | 220 | 360 | 500 | 0.99914 | 1.9983 | 2.9974 | 4.9957 | 7.4936 | 9.9914 | 95.4308 | 96.2429 | 97.1609 | 96.681 | 96.131 | 95.6355 | 96.3229 | 96.0699 | 96.9269 | 97.9414 | 97.4965 | 97.0743 | 96.7243 | 97.202 | 96.7257 | 97.6788 | 98.5843 | 98.2362 | 97.8247 | 97.2475 | 97.9222 | 2025-10-13
Northern Electric & Power Co. Ltd | BDH-12KSP-LB {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 12 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.517 | 208 | 96.5 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.25 |  |  | 220 | 360 | 500 | 1.1517 | 2.3034 | 3.4551 | 5.7585 | 8.6378 | 11.517 | 94.5637 | 95.0747 | 96.2219 | 95.9651 | 95.651 | 95.6393 | 95.7126 | 95.8105 | 96.2916 | 97.011 | 96.9717 | 96.4131 | 96.0207 | 96.5523 | 96.2546 | 96.9778 | 98.424 | 97.2969 | 97.1415 | 96.943 | 97.2745 | 2025-10-13
Northern Electric & Power Co. Ltd | BDH-12KSP-LB {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 12 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.969 | 240 | 97 | Intertek | [3/21/2025] | Intertek | [3/21/2025] | [V0.1] | 2025-10-13 | [3/21/2025] | 2025-10-13 | Intertek | 2025-03-18 |  |  | N | N | 16.48 |  |  | 220 | 360 | 500 | 1.1969 | 2.3938 | 3.5907 | 5.9845 | 8.9767 | 11.969 | 95.5377 | 96.4105 | 97.2613 | 96.6277 | 96.3047 | 95.9192 | 96.4427 | 96.1402 | 97.3142 | 97.9948 | 97.5526 | 96.9976 | 96.7655 | 97.2038 | 96.9953 | 97.7455 | 98.6046 | 98.4266 | 97.9344 | 97.2686 | 98.0379 | 2025-10-13
OutBack Power | FXR3048A {120V} | N | N | Y | Y | Y | N | N | N | 2.5 kW, 120 VAC Grid Support Utility Interactive Inverter with external battery backup | 2.56 | 120 | 91 | No Information Submitted | No Information Submitted | Intertek | [11/7/2017] | [001.006.063] | 2018-10-15 | [11/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0 |  |  | 40 | 52 | 60 | 0.26 | 0.51 | 0.77 | 1.28 | 1.92 | 2.56 | 83.7 | 90.2 | 92.2 | 93.3 | 92.6 | 91.6 | 92.2 | 79.8 | 87.1 | 90 | 92 | 92 | 91.2 | 91 | 77.3 | 85.1 | 88.1 | 90.6 | 91 | 90.7 | 89.7 | 2017-12-15 | 2018-10-15
OutBack Power | VFXR3524A {120V} | N | N | Y | Y | Y | N | N | N | 3 kW, 120 VAC Grid Support Utility Interactive Inverter with external battery backup | 2.96 | 120 | 90.5 | No Information Submitted | No Information Submitted | Intertek | [11/7/2017] | [001.006.063] | 2018-10-15 | [11/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0 |  |  | 22 | 24 | 28 | 0.3 | 0.59 | 0.89 | 1.48 | 2.22 | 2.96 | 88.3 | 91.9 | 92.9 | 93 | 91.3 | 88.7 | 91.6 | 87.2 | 90.8 | 92.1 | 92.1 | 91 | 88.6 | 91.1 | 83.7 | 87.1 | 89.1 | 90.6 | 90 | 87.8 | 89.5 | 2017-12-15 | 2018-10-15
OutBack Power | VFXR3648A {120V} | N | N | Y | Y | Y | N | N | N | 4 kW, 120 VAC Grid Support Utility Interactive Inverter with external battery backup | 3.037 | 120 | 91 | No Information Submitted | No Information Submitted | Intertek | [11/7/2017] | [001.006.063] | 2018-10-15 | [11/7/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | Y | N | 0 |  |  | 40 | 51.2 | 60 | 0.3 | 0.61 | 0.91 | 1.52 | 2.28 | 3.04 | 88 | 92.2 | 93.5 | 94 | 93 | 91.2 | 92.9 | 82.2 | 88.5 | 90.7 | 91.8 | 91.6 | 89.7 | 90.9 | 80.3 | 86.1 | 87.9 | 90.3 | 90.4 | 88.3 | 89.4 | 2017-12-15 | 2018-10-15
OutBack Power | GS4048A {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with external battery backup and accessible neutral to allow 120 VAC loads to be backed up. Inverter is capable of PCS functionality | 3.6 | 240 | 92.5 | No Information Submitted | No Information Submitted | Intertek | [11/7/2017] | [001.006.063] | 2018-10-15 | [11/7/2017] | 2020-10-01 | PCTEST Engineering Laboratory | 2020-01-24 | 2020-05-01 |  | Y | N | 0.1 |  |  | 44 | 48 | 56 | 0.72 | 1.44 | 2.16 | 3.6 | 5.4 | 7.2 | 92.6 | 94.4 | 93.7 | 94.4 | 93 | 90.4 | 93.3 | 91.5 | 93.4 | 93 | 93.3 | 92.7 | 90.8 | 92.7 | 89 | 91.6 | 92.2 | 92.1 | 91.5 | 89.9 | 91.5 | 2017-12-15 | 2020-12-01
OutBack Power | SBX5048-120/240 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac, Multimode Grid Support Utility Interactive PV and Battery Inverter with PCS Functionality | 4.985 | 240 | 94 | No Information Submitted | No Information Submitted | UL | [08/08/2018];[08/08/2018];[01/28/2021] | [NPC:0.0.0.2.2.0.9352,PBM:0.3.1.0.0.0.9359];[NPC:0.0.0.3.0.2.10015,PBM:0.3.1.0.0.6.10006];[NPC:0.0.0.3.0.2.10164,PMB:0.3.1.0.0.6.10482] | 2019-04-02 | [08/08/2018];[08/08/2018];[01/28/2021] | 2021-03-11 | SunSpec Alliance | 2020-01-28 | 2020-03-23 |  | Y | N | 24.85 |  |  | 250 | 420 | 550 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 85.9112 | 91.8786 | 93.404 | 94.206 | 94.0833 | 93.7751 | 93.575 | 87.0418 | 92.4308 | 94.1918 | 94.8976 | 95.0953 | 94.8942 | 94.4799 | 85.3624 | 91.926 | 93.5091 | 94.4779 | 94.7418 | 94.6173 | 94.0163 | 2018-09-17 | 2021-03-11
OutBack Power | GS8048A {240V} | N | N | Y | Y | Y | Y | Y* | Y | 7.2 kW, 240 Vac Grid Support Utility Interactive Inverter with external battery backup and accessible neutral to allow 120 VAC loads to be backed up. Inverter is capable of PCS functionality | 7.2 | 240 | 92.5 | No Information Submitted | No Information Submitted | Intertek | [11/7/2017] | [001.006.063] | 2018-10-15 | [11/7/2017] | 2020-10-01 | PCTEST Engineering Laboratory | 2020-01-24 | 2020-04-21 |  | Y | N | 0.1 |  |  | 44 | 48 | 56 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 88.3 | 92.6 | 94.1 | 94.4 | 93.2 | 91.2 | 93.3 | 87.1 | 91.5 | 92.9 | 93.3 | 93 | 90.8 | 92.6 | 84 | 89 | 90.9 | 92.1 | 91.9 | 90.2 | 91.3 | 2017-12-15 | 2020-12-01
OutBack Power | OGHI8048A {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.2 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.638 | 240 | 93 | UL | [4/21/2023] | UL | [7/21/2022];[4/21/2023] | [DSP 0x6EE0] | 2023-04-21 | [7/21/2022];[4/21/2023] | 2022-09-12 | SunSpec Alliance | 2023-02-13 | No Information Submitted |  | Y | N | 146.4 |  |  | 44 | 48 | 52 | 0.76382 | 1.5276 | 2.2914 | 3.8191 | 5.7286 | 7.6382 | 89.6183 | 93.5227 | 94.1192 | 94.5133 | 92.5863 | 89.0209 | 92.9247 | 88.4117 | 93.3675 | 94.539 | 94.3368 | 92.7159 | 90.3307 | 93.0162 | 87.1721 | 92.8471 | 94.3599 | 94.6092 | 93.4428 | 91.8098 | 93.4355 | 2022-09-12 | 2023-10-11
Oxford Intelligent Energy Co., Ltd. | OE 5KHS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 5.02 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 92.68 | 95.27 | 95.93 | 96.35 | 96.16 | 95.99 | 95.98 | 93.57 | 95.86 | 96.53 | 97.03 | 97.08 | 96.97 | 96.8 | 93.73 | 95.93 | 96.5 | 96.81 | 96.9 | 96.81 | 96.65 | 2024-03-11 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 5KHS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 5.04 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.504 | 1.008 | 1.512 | 2.52 | 3.78 | 5.04 | 92.99 | 95.51 | 96.13 | 96.56 | 96.34 | 96.22 | 96.18 | 93.67 | 95.99 | 96.75 | 97.31 | 97.43 | 97.38 | 97.1 | 93.79 | 96.14 | 96.61 | 96.98 | 97.24 | 97.24 | 96.92 | 2024-03-11 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 6KHS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 6.124 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.612 | 1.225 | 1.837 | 3.062 | 4.593 | 6.124 | 91.51 | 94.38 | 95.44 | 96.15 | 96.2 | 96.02 | 95.81 | 93.61 | 95.95 | 96.7 | 97.16 | 97.14 | 97.02 | 96.88 | 93.01 | 95.45 | 96.32 | 96.9 | 96.93 | 96.76 | 96.61 | 2024-03-11 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 6KHS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 6.149 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.615 | 1.23 | 1.845 | 3.075 | 4.612 | 6.149 | 91.6 | 94.45 | 95.46 | 96.26 | 96.41 | 96.35 | 95.97 | 93.87 | 96.14 | 96.88 | 97.38 | 97.49 | 97.42 | 97.18 | 92.69 | 95.45 | 96.41 | 97.1 | 97.3 | 97.27 | 96.87 | 2024-03-11 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 7K6HS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 7.647 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.529 | 2.294 | 3.824 | 5.735 | 7.647 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 89.75 | 96.08 | 96.79 | 97.16 | 96.97 | 96.77 | 96.65 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2023-12-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 7K6HS-T2/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 7.647 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.529 | 2.294 | 3.824 | 5.735 | 7.647 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 89.75 | 96.08 | 96.79 | 97.16 | 96.97 | 96.77 | 96.65 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2024-11-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 7K6HS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 7.648 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.53 | 2.294 | 3.824 | 5.736 | 7.648 | 92.95 | 95.54 | 96.21 | 96.65 | 96.45 | 96.19 | 96.26 | 93.74 | 96.07 | 96.79 | 97.16 | 96.97 | 96.77 | 96.8 | 94.06 | 96.23 | 96.77 | 97.12 | 96.91 | 96.7 | 96.78 | 2024-03-11 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 7K6HS-T2/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 7.648 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.53 | 2.294 | 3.824 | 5.736 | 7.648 | 92.95 | 95.54 | 96.21 | 96.65 | 96.45 | 96.19 | 96.26 | 93.74 | 96.07 | 96.79 | 97.16 | 96.97 | 96.77 | 96.8 | 94.06 | 96.23 | 96.77 | 97.12 | 96.91 | 96.7 | 96.78 | 2024-11-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 8KHS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 8.047 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.805 | 1.609 | 2.414 | 4.024 | 6.035 | 8.047 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 93.75 | 96.08 | 96.8 | 97.17 | 96.97 | 96.77 | 96.81 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2023-12-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 8KHS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 8.06 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 17.78 |  |  | 200 | 360 | 480 | 0.806 | 1.612 | 2.418 | 4.03 | 6.045 | 8.06 | 92.85 | 95.45 | 96.11 | 96.55 | 96.35 | 96.09 | 96.17 | 93.65 | 95.98 | 96.69 | 97.06 | 96.87 | 96.67 | 96.71 | 93.97 | 96.14 | 96.67 | 97.02 | 96.81 | 96.55 | 96.68 | 2023-12-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 11K4HS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 10.14 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.028 | 3.042 | 5.07 | 7.605 | 10.14 | 93.05 | 95.58 | 96.24 | 96.66 | 96.45 | 96.2 | 96.28 | 93.72 | 96.07 | 96.82 | 97.15 | 96.96 | 96.78 | 96.8 | 94.05 | 96.25 | 96.79 | 97.12 | 96.92 | 96.66 | 96.79 | 2024-11-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 10KHS/LV {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 10.147 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.015 | 2.029 | 3.044 | 5.074 | 7.61 | 10.147 | 93 | 95.58 | 96.22 | 96.66 | 96.46 | 96.2 | 96.28 | 93.79 | 96.1 | 96.81 | 97.16 | 96.97 | 96.77 | 96.81 | 94.11 | 96.27 | 96.78 | 97.13 | 96.92 | 96.66 | 96.79 | 2023-12-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 10KHS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 10.186 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.89 | 95.48 | 96.13 | 96.56 | 96.36 | 96.1 | 96.18 | 93.7 | 96.01 | 96.71 | 97.07 | 96.88 | 96.67 | 96.72 | 94.02 | 96.16 | 96.68 | 96.99 | 96.82 | 96.56 | 96.68 | 2023-12-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
Oxford Intelligent Energy Co., Ltd. | OE 11K4HS/LV {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 10.186 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-03-21 | [1/10/2025] | 2025-03-21 | SGS | 2024-08-06 | 2024-12-23 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.91 | 95.48 | 96.12 | 96.56 | 96.36 | 96.1 | 96.18 | 93.66 | 96.02 | 96.72 | 97.07 | 96.88 | 96.68 | 96.72 | 94.07 | 96.17 | 96.67 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-11-01 | 2026-05-21 | Y | N | N | N | N | N | N | N | No Information Submitted
PANASONIC CORPORATION OF NORTH AMERICA | EVHB-I7 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid support utility-interactive Power Conversion System. Capable of PCS functionality. | 7.6082 | 240 | 96.5 | CSA Group | [5/30/2024] | CSA Group | [5/30/2024] | [V1.05, V1.03, V1.10] | 2023-07-21 | [5/10/2023] | 2023-07-21 | Intertek | 2023-05-22 | 2023-07-21 |  | N | N | 7.3 |  |  | 234.1 | 365.5 | 498.4 | 0.756 | 1.512 | 2.267 | 3.779 | 5.668 | 7.558 | 95.53 | 96.94 | 97.21 | 97.32 | 96.95 | 96.71 | 96.99 | 96.67 | 97.84 | 97.97 | 97.94 | 97.77 | 97.53 | 97.78 | 96.06 | 97.25 | 97.82 | 97.87 | 97.75 | 97.62 | 97.68 | 2023-07-21 | 2025-02-03
PhaseGreen Technology Inc. | PhG-P5K0LNA-M {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 5.0897 | 240 | 97 | SGS | [10/23/2023] | SGS | [10/23/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-01-02 | [10/23/2023] | 2024-01-02 | SGS | 2023-10-20 | 2024-01-02 |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2023-05-11 | 2026-03-11 | N | N | N | N | N | N | Y | N | No Information Submitted
PhaseGreen Technology Inc. | PhG-P6K0LNA-M {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 6.117 | 240 | 97 | SGS | [10/23/2023] | SGS | [10/23/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-01-02 | [10/23/2023] | 2024-01-02 | SGS | 2023-10-20 | 2024-01-02 |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2023-05-11 | 2026-03-11 | N | N | N | N | N | N | Y | N | No Information Submitted
PhaseGreen Technology Inc. | PhG-P7K6LNA-M {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 7.765 | 240 | 97 | SGS | [10/23/2023] | SGS | [10/23/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-01-02 | [10/23/2023] | 2024-01-02 | SGS | 2023-10-20 | 2024-01-02 |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2023-05-11 | 2026-03-11 | N | N | N | N | N | N | Y | N | No Information Submitted
PhaseGreen Technology Inc. | PhG-P8K0LNA-M {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 8.084 | 240 | 97.5 | SGS | [10/23/2023] | SGS | [10/23/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-01-02 | [10/23/2023] | 2024-01-02 | SGS | 2023-10-20 | 2024-01-02 |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2023-05-11 | 2026-03-11 | N | N | N | N | N | N | Y | N | No Information Submitted
PhaseGreen Technology Inc. | PhG-P10K0LNA-M {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 10.177 | 240 | 97 | SGS | [10/23/2023] | SGS | [10/23/2023] | [V1.04.06(DSP), V1.03.06(ARM)] | 2024-01-02 | [10/23/2023] | 2024-01-02 | SGS | 2023-10-20 | 2024-01-02 |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2023-05-11 | 2026-03-11 | N | N | N | N | N | N | Y | N | No Information Submitted
Pika Energy | X7602 {240V} | Y | N | Y | Y | Y | Y | Y | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.587 | 240 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [11/11/2019] | [12982] | 2018-10-15 | [11/11/2019] | 2020-03-23 | SunSpec Alliance | 2019-11-26 | 2020-03-23 |  | N | N | 1.29 |  |  | 390 | 400 | 420 | 0.759 | 1.517 | 2.276 | 3.793 | 5.689 | 7.586 | 91.67 | 95.89 | 96.62 | 97.26 | 97.24 | 97.04 | 96.87 | 91.01 | 95.4 | 96.52 | 97.26 | 97.15 | 97.01 | 96.75 | 90.48 | 95.21 | 96.33 | 96.86 | 97.02 | 96.91 | 96.55 | 2020-03-23
Pika Energy | X11402 {208V} | Y | N | Y | Y | Y | Y | Y | Y | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.187 | 208 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [11/11/2019] | [12982] | 2018-10-15 | [11/11/2019] | 2020-03-23 | SunSpec Alliance | 2019-11-26 | 2020-03-23 |  | N | N | 0.13 |  |  | 390 | 400 | 420 | 1.12 | 2.24 | 3.36 | 5.59 | 8.39 | 11.19 | 97.2 | 97.4 | 97.6 | 97.6 | 97.4 | 97.1 | 97.5 | 97 | 97.3 | 97.7 | 97.5 | 97.3 | 96.9 | 97.3 | 95.8 | 97.2 | 97.3 | 97.4 | 97.1 | 96.9 | 97.1 | 2020-03-23
PointGuard Energy Inc. | PG Controller 3.8 {240V} | Y | Y | N | N | N | N | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 3.843 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-09-03 |  | N | N | 3.26 |  |  | 270 | 360 | 480 | 0.384 | 0.769 | 1.153 | 1.922 | 2.882 | 3.843 | 93 | 95.49 | 96.34 | 96.87 | 97 | 97.03 | 96.66 | 94.25 | 96.34 | 97.04 | 97.48 | 97.56 | 97.51 | 97.29 | 92.95 | 95.41 | 96.34 | 96.99 | 97.17 | 97.19 | 96.78 | 2024-09-03 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
PointGuard Energy Inc. | PG Controller 4.8 {240V} | Y | Y | N | N | N | N | Y* | Y | 4.8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 4.808 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-09-03 |  | N | N | 3.32 |  |  | 270 | 360 | 480 | 0.481 | 0.962 | 1.442 | 2.404 | 3.606 | 4.808 | 93.93 | 96.05 | 96.64 | 96.96 | 97.03 | 96.96 | 96.79 | 95.12 | 96.82 | 97.3 | 97.54 | 97.54 | 97.41 | 97.37 | 93.95 | 96.02 | 96.71 | 97.11 | 97.2 | 97.14 | 96.93 | 2024-09-03 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
PointGuard Energy Inc. | PG Controller 5.7 {240V} | Y | Y | N | N | N | N | Y* | Y | 5.7 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 5.776 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-09-03 |  | N | N | 3.37 |  |  | 270 | 360 | 480 | 0.578 | 1.155 | 1.733 | 2.888 | 4.332 | 5.776 | 94.61 | 96.34 | 96.8 | 97 | 97 | 96.89 | 96.84 | 95.59 | 97.05 | 97.42 | 97.55 | 97.46 | 97.32 | 97.37 | 94.49 | 96.33 | 96.88 | 97.16 | 97.16 | 97.05 | 96.97 | 2024-09-03 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
PointGuard Energy Inc. | PG Controller 7.6 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 7.689 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-09-03 |  | N | N | 3.36 |  |  | 270 | 360 | 480 | 0.769 | 1.538 | 2.307 | 3.844 | 5.767 | 7.689 | 95.46 | 96.7 | 96.9 | 97.03 | 96.89 | 96.69 | 96.84 | 96.37 | 97.33 | 97.52 | 97.51 | 97.32 | 97.2 | 97.34 | 95.42 | 96.76 | 97.07 | 97.18 | 97.04 | 96.87 | 96.98 | 2024-09-03 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
PointGuard Energy Inc. | PG Controller 9.6 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 9.653 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-09-03 |  | N | N | 3.35 |  |  | 270 | 360 | 480 | 0.965 | 1.931 | 2.896 | 4.827 | 7.24 | 9.653 | 96 | 96.87 | 96.99 | 96.96 | 96.72 | 96.46 | 96.77 | 96.79 | 97.48 | 97.55 | 97.39 | 97.23 | 97.1 | 97.29 | 95.96 | 96.98 | 97.16 | 97.12 | 96.91 | 96.78 | 96.94 | 2024-09-03 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
PointGuard Energy Inc. | PG Controller 11.4 {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality | 11.4601 | 240 | 97 | CSA Group | [5/14/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-02-06 | 2024-06-21 |  | N | N | 3.3 |  |  | 270 | 360 | 480 | 1.146 | 2.292 | 3.438 | 5.7301 | 8.5951 | 11.4601 | 96.1745 | 96.9088 | 97.1227 | 97.0709 | 96.8249 | 96.4944 | 96.874 | 96.8655 | 97.5022 | 97.6109 | 97.5252 | 97.1814 | 97.1326 | 97.3061 | 96.1379 | 97.0621 | 97.2015 | 97.1814 | 97.0036 | 96.6911 | 97.0174 | 2024-06-21 | 2026-08-11 | Y | N | N | N | N | N | Y | N | N
POMCube Inc. | PNZ-10K1N2-NA0 {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 10 kW, 240 Vac Split Phase, Transformerless Grid Support Utility Interactive Hybrid Inverter for PV and Energy Storage Application. The inverter is capable of PCS functionality. | 9.92 | 240 | 94 | Intertek | [12/1/2023] | Intertek | [12/1/2023] | ARM/10010, pv/10050, pcs/10025 | 2021-03-22 | [04/14/2021] | 2021-05-21 | SunSpec Alliance | 2021-03-23 | 2021-05-21 |  | N | N | 21.92 |  |  | 250 | 360 | 530 | 0.99227 | 1.9845 | 2.9768 | 4.9613 | 7.442 | 9.9227 | 91.2728 | 93.8665 | 92.8466 | 93.9818 | 94.1882 | 93.8918 | 93.8364 | 94.433 | 94.2287 | 93.579 | 93.0905 | 94.0391 | 94.2974 | 93.8229 | 93.3697 | 95.1764 | 93.7928 | 94.5765 | 94.8844 | 95.1581 | 94.6565 | 2021-03-22 | 2024-02-21
Power Center | Essential Hybrid 5 {120V} | Y | Y | N | N | N | N | N | N | 5 kW, 120 Vac Grid Support Utility Interactive PV and Battery Inverter | 4.7871 | 120 | 96.5 | TUV Rheinland | [8/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 11.7 |  |  | 200 | 312.5 | 425 | 0.47871 | 0.95742 | 1.4361 | 2.3935 | 3.5903 | 4.7871 | 94.422 | 96.792 | 97.112 | 96.518 | 95.908 | 95.576 | 96.1487 | 94.832 | 97.148 | 97.55 | 96.838 | 96.532 | 95.88 | 96.6486 | 94.292 | 96.732 | 97.052 | 96.49 | 95.946 | 95.406 | 96.1391 | 2024-05-13
Power Center | Essential Hybrid 5 {240V} | Y | Y | N | N | N | N | N | N | 8 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 7.9703 | 240 | 96.5 | TUV Rheinland | [8/17/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 19.3 |  |  | 200 | 312.5 | 425 | 0.79703 | 1.5941 | 2.3911 | 3.9851 | 5.9777 | 7.9703 | 94.432 | 96.79 | 97.304 | 96.606 | 96.184 | 95.546 | 96.3353 | 94.82 | 97.058 | 97.568 | 96.802 | 96.458 | 95.99 | 96.6045 | 94.374 | 96.7 | 97.082 | 96.412 | 95.828 | 95.31 | 96.0607 | 2024-05-13
Power Center | Flex 10 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, Grid Support Utility Interactive Inverter | 8.671 | 208 | 96.5 | Intertek | [5/28/2026] | Intertek | [5/28/2026] | [V0.1] | 46245 | [5/28/2026] | 46245 | Intertek | 46119 |  |  | N | N | 16.22 |  |  | 220 | 360 | 500 | 0.8671 | 1.7342 | 2.6013 | 4.3355 | 6.5032 | 8.671 | 94.6399 | 95.5162 | 96.3259 | 95.9573 | 95.5771 | 95.3524 | 95.695 | 95.5409 | 96.299 | 97.0577 | 96.8606 | 96.5499 | 96.1987 | 96.6056 | 96.1644 | 97.0926 | 97.8805 | 97.4985 | 97.5164 | 96.9415 | 97.4523 | 2026-08-11 |  | Y | N | N | N | N | N | Y | N | N
Power Center | Flex 10 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, Grid Support Utility Interactive Inverter | 9.9914 | 240 | 97 | Intertek | [5/28/2026] | Intertek | [5/28/2026] | [V0.1] | 46245 | [5/28/2026] | 46245 | Intertek | 46119 |  |  | N | N | 16.53 |  |  | 220 | 360 | 500 | 0.99914 | 1.9983 | 2.9974 | 4.9957 | 7.4936 | 9.9914 | 95.4308 | 96.2429 | 97.1609 | 96.681 | 96.131 | 95.6355 | 96.3229 | 96.0699 | 96.9269 | 97.9414 | 97.4965 | 97.0743 | 96.7243 | 97.202 | 96.7257 | 97.6788 | 98.5843 | 98.2362 | 97.8247 | 97.2475 | 97.9222 | 2026-08-11 |  | Y | N | N | N | N | N | Y | N | N
Power Center | Flex 12 {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 12 kW, Grid Support Utility Interactive Inverter | 11.517 | 208 | 96.5 | Intertek | [5/28/2026] | Intertek | [5/28/2026] | [V0.1] | 46245 | [5/28/2026] | 46245 | Intertek | 46119 |  |  | N | N | 16.25 |  |  | 220 | 360 | 500 | 1.1517 | 2.3034 | 3.4551 | 5.7585 | 8.6378 | 11.517 | 94.5637 | 95.0747 | 96.2219 | 95.9651 | 95.651 | 95.6393 | 95.7126 | 95.8105 | 96.2916 | 97.011 | 96.9717 | 96.4131 | 96.0207 | 96.5523 | 96.2546 | 96.9778 | 98.424 | 97.2969 | 97.1415 | 96.943 | 97.2745 | 2026-08-11 |  | Y | N | N | N | N | N | Y | N | N
Power Center | Flex 12 {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 12 kW, Grid Support Utility Interactive Inverter | 11.969 | 240 | 97 | Intertek | [5/28/2026] | Intertek | [5/28/2026] | [V0.1] | 46245 | [5/28/2026] | 46245 | Intertek | 46119 |  |  | N | N | 16.48 |  |  | 220 | 360 | 500 | 1.1969 | 2.3938 | 3.5907 | 5.9845 | 8.9767 | 11.969 | 95.5377 | 96.4105 | 97.2613 | 96.6277 | 96.3047 | 95.9192 | 96.4427 | 96.1402 | 97.3142 | 97.9948 | 97.5526 | 96.9976 | 96.7655 | 97.2038 | 96.9953 | 97.7455 | 98.6046 | 98.4266 | 97.9344 | 97.2686 | 98.0379 | 2026-08-11 |  | Y | N | N | N | N | N | Y | N | N
Power Center | Max Hybrid 15 {208V} | Y | Y | N | N | N | N | Y* | N | 15 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 13.01 | 208 | 96.5 | SGS | [7/19/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-01-12 | No Information Submitted |  | N | N | 21.2 |  |  | 200 | 320 | 425 | 1.3014 | 2.6029 | 3.9043 | 6.5072 | 9.7608 | 13.0145 | 93.374 | 95.8088 | 97.681 | 96.9864 | 96.551 | 96.3162 | 96.6021 | 93.6666 | 95.9928 | 97.712 | 97.172 | 96.6578 | 96.4328 | 96.7281 | 93.469 | 95.9614 | 97.63 | 97.0532 | 96.5632 | 96.3156 | 96.6279 | 2023-11-13 | 2024-11-01
Power Center | Max Hybrid 15 {240V} | Y | Y | N | N | N | N | Y* | N | 15 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 15.04 | 240 | 96.5 | SGS | [7/19/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-01-12 | No Information Submitted |  | N | N | 21.2 |  |  | 200 | 320 | 425 | 1.5044 | 3.0087 | 4.5131 | 7.5219 | 11.2828 | 15.0437 | 93.582 | 95.8704 | 97.6968 | 97.062 | 96.661 | 96.4142 | 96.6945 | 93.693 | 96.1402 | 97.7394 | 97.2496 | 96.7728 | 96.4702 | 96.819 | 93.6154 | 95.9584 | 97.6952 | 97.089 | 96.7006 | 96.4 | 96.726 | 2023-11-13 | 2024-11-01
Power Center | Max Hybrid 30 (208V) {120V} | Y | Y | N | N | N | N | Y* | N | 30 kW, 120 Vac Grid Support Interactive Hybrid Inverter with PCS functionality. | 30.025 | 120 | 96.5 | TUV Rheinland of North America | [3/5/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-09-16 | No Information Submitted |  | N | N | 31.9 |  |  | 270 | 385 | 500 | 3.0025 | 6.005 | 9.0076 | 15.0126 | 22.5189 | 30.0252 | 94.448 | 96.852 | 97.246 | 96.534 | 96.014 | 95.534 | 96.2263 | 94.814 | 97.092 | 97.534 | 96.824 | 96.44 | 95.92 | 96.5935 | 94.344 | 96.68 | 97.14 | 96.444 | 95.836 | 95.342 | 96.078 | 2024-06-11 | 2025-03-21
Power Center | Max Hybrid 60 {277V} | Y | Y | N | N | N | N | Y* | N | 60 kW, 277 Vac Grid Support Interactive Hybrid Inverter with PCS functionality. | 60.05 | 277 | 97.5 | TUV Rheinland | [3/5/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-09-16 | No Information Submitted |  | N | N | 5.29 |  |  | 540 | 695 | 850 | 6.005 | 12.01 | 18.015 | 30.025 | 45.0375 | 60.05 | 94.422 | 98.066 | 98.602 | 97.896 | 97.376 | 96.784 | 97.5191 | 94.748 | 98.504 | 98.834 | 98.228 | 97.77 | 97.26 | 97.8842 | 94.32 | 98.036 | 98.376 | 97.826 | 97.196 | 96.688 | 97.3715 | 2024-06-11 | 2025-03-21
Power Electronics | FP3000K3 {600V} | N | N | Y | Y | Y | N | N | N | 3300 kW, 600 Vac, Grid Support Utility Interactive Battery Inverter | 3116.969 | 600 | 98 | No Information Submitted | No Information Submitted | MET | [6/25/2019] | [1.0.0] | 2020-05-21 | [6/25/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is central control composed by 6 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of transformer effect based on 3000 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 442.59 |  |  | 849 | 940 | 1200 | 311.6969 | 623.3938 | 935.0906 | 1558.484 | 2337.727 | 3116.969 | 96.023 | 97.7207 | 98.1252 | 98.386 | 98.2657 | 98.0531 | 98.1465 | 95.9458 | 97.6341 | 98.0448 | 98.2818 | 98.158 | 97.9292 | 98.0443 | 95.9202 | 97.6234 | 98.0333 | 98.2876 | 98.1723 | 97.9444 | 98.0509 | 2020-05-21
POWER ELECTRONICS | FP3151K {660V} | N | N | Y | Y | Y | N | N | N | 3151 kW, 660 Vac, Grid Support Utility Interactive Inverter with a 33529 kVA GE Prolec MV Transformer. | 3145.17 | 660 | 98 | No Information Submitted | No Information Submitted | MET | [1/12/2023] | [2.1.0] | 2023-08-01 | [1/12/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is central control composed by 3 modules. The equipment must be connected to the grid through an isolation transformer. Efficiency data inclusive of a 33529 kVA GE Prolec MV Transformer. | N | N | 685 |  |  | 849 | 1024 | 1200 | 314.517 | 629.034 | 943.551 | 1572.585 | 2358.8775 | 3145.17 | 96.9525 | 98.0481 | 98.5307 | 98.8871 | 98.7775 | 98.6509 | 98.6551 | 96.5898 | 97.9613 | 98.4864 | 98.7932 | 98.7125 | 98.572 | 98.5728 | 96.5368 | 97.9048 | 98.4465 | 98.7799 | 98.8014 | 98.5599 | 98.6068 | 2023-08-01
Power Electronics | FP3510M3 {34500V} | N | N | Y | Y | Y | N | N | N | 3630 kW, 34500 Vac, with Internal Meduim Voltage Transformer, Grid Support Utility Interactive Centeral Battery Inverter | 3630.064 | 34500 | 97.5 | No Information Submitted | No Information Submitted | MET | [12/05/2019] | [1.0.0] | 2021-04-01 | [12/05/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is central control composed by 6 modules. No differences between modules, they use the same components. The equipment incorporates internal Medium Voltage transformer in order to provide a output voltage of 34.5 kVac. | N | N | 7640 |  |  | 934 | 1000 | 1200 | 363.0064 | 726.0128 | 1089.0192 | 1815.032 | 2722.548 | 3630.064 | 95.0637 | 96.9102 | 97.5292 | 97.7902 | 97.755 | 96.9845 | 97.5469 | 95.0013 | 96.8237 | 97.4321 | 97.6552 | 97.6302 | 96.8429 | 97.4268 | 94.9968 | 96.7694 | 97.4072 | 97.704 | 97.6231 | 97.0263 | 97.4366 | 2021-04-01
Power Electronics | FP3510M2 {34500V} | N | N | Y | Y | Y | N | N | N | 3662 kW, 34500 Vac, with Internal Medium Voltage Transformer, Grid Support Utility Interactive Central Battery Inverter | 3662.494 | 34500 | 97.5 | No Information Submitted | No Information Submitted | MET | [12/5/2019] | [1.0.0] | 2022-01-11 | [12/5/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | The inverter is central control composed by 6 modules. No differences between modules, they use the same components. The equipment incorporates internal Medium Voltage transformer, in order to provide a output voltage of 34.5 kVac. | N | N | 7640 |  |  | 934 | 1000 | 1200 | 366.2494 | 732.4988 | 1098.7482 | 1831.247 | 2746.8705 | 3662.494 | 95.1818 | 96.9663 | 97.4695 | 97.718 | 97.684 | 97.3087 | 97.5107 | 95.0143 | 96.855 | 97.3508 | 97.6283 | 97.594 | 97.2355 | 97.414 | 95.1818 | 96.9195 | 97.4312 | 97.6285 | 97.5837 | 97.2662 | 97.4296 | 2022-01-11
Power Electronics | FP4200M {34500V} | N | N | Y | Y | Y | N | N | N | 4200 kW, 34500 Vac Grid Support Utility Interactive Central Battery Inverter with internal transformer | 4198.71 | 34500 | 97.5 | No Information Submitted | No Information Submitted | MET | [1/12/2023] | [2.1.0] | 2023-09-01 | [1/12/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 7033 |  |  | 934 | 1067 | 1200 | 419.871 | 839.742 | 1259.613 | 2099.355 | 3149.0325 | 4198.71 | 93.6734 | 96.6868 | 97.5508 | 98.1224 | 98.2294 | 97.9764 | 97.8535 | 93.4288 | 96.6302 | 97.432 | 97.9258 | 98.0164 | 97.9536 | 97.6713 | 93.3212 | 96.3796 | 97.2426 | 97.8998 | 97.9728 | 97.856 | 97.5983 | 2023-09-01
Princeton Power Systems, Inc. | GTIB-480-30-WZZZZZZ-G1.3 {480V} | Y | N | Y | Y | Y | N | N | N | 30 kVA, 480 Vac, 830Vdc, Non-isolated, Bi-directional, Grid Support Utility Interactive PV or Battery Inverter; where Z can be -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or blank. Cannot accept PV and Battery DC input simultaneously. | 29.444 | 480 | 93.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/09/2019] | [V2.4.2] | 2019-06-17 | [05/09/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 35.14 |  |  | 540 | 750 | 830 | 2.9444 | 5.8889 | 8.8333 | 14.7222 | 22.0832 | 29.4443 | 86.7633 | 92.621 | 93.1032 | 93.8163 | 93.2421 | 92.0854 | 92.998 | 87.6485 | 93.2657 | 93.53 | 94.1163 | 93.4041 | 92.9205 | 93.3074 | 88.6063 | 92.4924 | 94.6691 | 94.5469 | 93.6549 | 93.0472 | 93.6735 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-30-ZZZZZZ-G1.3 {480V} | Y | N | Y | Y | Y | N | N | N | 30 kVA, 480 Vac, 830Vdc, Transformerless, Non-isolated, Bi-directional, Grid Support Utility Interactive PV or Battery Inverter; where Z can be -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or blank (Z≠-W). Cannot accept PV and Battery DC input simultaneously. | 29.956 | 480 | 97 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/09/2019] | [V2.4.2] | 2019-06-17 | [05/09/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 46.3 |  |  | 540 | 750 | 830 | 2.9956 | 5.9911 | 8.9867 | 14.9778 | 22.4667 | 29.9557 | 92.6541 | 95.1194 | 96.0767 | 96.8464 | 96.977 | 96.8538 | 96.5696 | 93.7759 | 95.2415 | 96.5013 | 97.1768 | 97.3758 | 97.3985 | 96.9795 | 92.7942 | 94.8855 | 96.3887 | 97.0579 | 97.1908 | 97.4251 | 96.7872 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-125XXXXXX-G1.5 {480V} | Y | N | Y | Y | Y | N | N | N | 125 kVA, 480 Vac, 830Vdc, Transformerless, Non-isolated, Grid Support Utility Interactive PV or Battery Inverter; where X can be -B, -D, -DH, -DA, -DD, -GN, -M, -OV, -V, or blank. Cannot accept PV and Battery DC input simultaneously. | 124.964 | 480 | 96 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/07/2019] | [V2.72] | 2019-06-17 | [05/07/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 68 |  |  | 350 | 710 | 830 | 12.4964 | 24.9928 | 37.4892 | 62.482 | 93.723 | 124.964 | 87.1196 | 92.9413 | 94.9723 | 95.2179 | 95.6593 | 95.2115 | 94.9843 | 91.9189 | 95.3761 | 95.8979 | 96.6258 | 96.8865 | 96.649 | 96.427 | 91.5596 | 95.713 | 96.4245 | 96.9684 | 96.936 | 96.8929 | 96.6031 | 2019-06-17
Princeton Power Systems, Inc. | GTIB-480-125XXXXXX-W-G1.5 {480V} | Y | N | Y | Y | Y | N | N | N | 125 kVA, 480 Vac, 830Vdc, Non-isolated, Grid Support Utility Interactive PV or Battery Inverter; where X can be -B, -D, -DH, -DA, -DD, -GN, -M, -OV, -V, or blank. Cannot accept PV and Battery DC input simultaneously. | 124.964 | 480 | 94.5 | No Information Submitted | No Information Submitted | TUV Rheinland of North America | [05/07/2019] | [V2.7.2] | 2019-06-17 | [05/07/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency includes efficiency of 125 kVA Jefferson Electric 423-D7-13 distribution transformer. | N | N | 68 |  |  | 350 | 710 | 830 | 12.4964 | 24.9928 | 37.4892 | 62.482 | 93.723 | 124.964 | 84.9387 | 91.6494 | 93.8422 | 94.0171 | 94.1574 | 93.2247 | 93.5493 | 89.6179 | 94.0504 | 94.7567 | 95.4072 | 95.3654 | 94.6322 | 94.9688 | 89.2675 | 94.3826 | 95.2771 | 95.7455 | 95.4141 | 94.8711 | 95.1427 | 2019-06-17
Qcells North America | Q.VOLT H3.8SX {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid support, utility-interactive hybrid inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 3.805 | 240 | 97 | CSA Group | [4/12/2024] | CSA Group | [9/8/2022];[3/14/2023] | [V1.05, V1.03, V1.10] | 2023-03-13 | [9/8/2022];[3/14/2023] | 2023-03-13 | Intertek | 2023-01-11 | 2023-03-13 |  | N | N | 1.2 |  |  | 175.4 | 337.9 | 499.5 | 0.38047 | 0.76094 | 1.1414 | 1.9023 | 2.8535 | 3.8047 | 92.7832 | 95.3783 | 96.1221 | 96.5347 | 96.5885 | 96.4765 | 96.3029 | 94.0899 | 96.2193 | 96.885 | 97.3248 | 97.4661 | 97.4427 | 97.1681 | 91.4685 | 96.3171 | 97.1281 | 97.4492 | 97.6556 | 97.6619 | 97.2348 | 2023-03-13 | 2024-06-03
Qcells North America | Q.VOLT A3.8SX {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid support, utility-interactive inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 3.81 | 240 | 95 | CSA Group | [4/12/2024] | CSA Group | [3/14/2023] | [V1.05, V1.03, V1.10] | 2023-04-03 | [3/14/2023] | 2023-04-03 | Intertek | 2023-01-11 | 2023-04-03 |  | N | Y | 1.2 |  |  | 75.6 | 262.8 | 450 | 0.38096 | 0.76192 | 1.1429 | 1.9048 | 2.8572 | 3.8096 | 89.5518 | 92.8592 | 93.7168 | 94.0193 | 93.779 | 93.4412 | 93.5901 | 88.0285 | 94.0298 | 95.5866 | 96.4637 | 96.7473 | 96.8458 | 96.0688 | 87.5436 | 93.8997 | 95.4778 | 96.3759 | 96.8597 | 97.0133 | 96.0793 | 2023-03-13 | 2024-06-03
Qcells North America | Q.VOLT H5.0SX {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid support, utility-interactive hybrid inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 5.003 | 240 | 97.5 | CSA Group | [4/12/2024] | CSA Group | [9/8/2022];[3/14/2023] | [V1.05, V1.03, V1.10] | 2023-03-13 | [9/8/2022];[3/14/2023] | 2023-03-13 | Intertek | 2023-01-11 | 2023-03-13 |  | N | N | 1.2 |  |  | 229.9 | 363.7 | 499.9 | 0.50027 | 1.0005 | 1.5008 | 2.5013 | 3.752 | 5.0027 | 94.4996 | 96.2452 | 96.7656 | 97.0082 | 96.9837 | 96.852 | 96.8198 | 95.7546 | 97.2612 | 97.4657 | 97.7249 | 97.7239 | 97.6405 | 97.5871 | 94.8122 | 97.071 | 97.3678 | 97.6591 | 97.7118 | 97.6279 | 97.5072 | 2023-03-13 | 2024-06-03
Qcells North America | Q.VOLT A5.0SX {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid support, utility-interactive inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 5.03 | 240 | 96 | CSA Group | [4/12/2024] | CSA Group | [3/14/2023] | [V1.05, V1.03, V1.10] | 2023-04-03 | [3/14/2023] | 2023-04-03 | Intertek | 2023-01-11 | 2023-04-03 |  | N | Y | 1.2 |  |  | 100.4 | 275.5 | 449.9 | 0.503 | 1.006 | 1.509 | 2.515 | 3.7725 | 5.03 | 91.3524 | 94.1166 | 94.7534 | 95.0269 | 94.8695 | 94.5367 | 94.6936 | 91.1403 | 95.3189 | 96.2129 | 96.6996 | 96.9043 | 96.9328 | 96.4699 | 89.7548 | 95.137 | 96.0905 | 96.6798 | 97.0081 | 97.0805 | 96.449 | 2023-03-13 | 2024-06-03
Qcells North America | Q.HOME+ HYB-G1-6.0 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac, single-phase, hybrid PV and battery, grid support utility interactive inverter | 5.57 | 240 | 94 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2021-01-11 | [10/23/2020] | 2021-01-11 | Intertek | 2020-09-11 | 2021-01-11 |  | N | N | 25 |  |  | 240 | 335 | 425 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 93.8526 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 94.3396 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888 | 94.1609 | 2021-01-11 | 2024-10-11
Qcells North America | Q.HOME+ AC-G1-6.0 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac, single-phase, battery, grid support utility interactive inverter | 5.732 | 240 | 94 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2021-02-01 | [10/23/2020] | 2021-02-01 | Intertek | 2020-09-25 | 2021-02-01 |  | N | N | 25 |  |  | 360 | 430 | 500 | 0.5732 | 1.1464 | 1.7196 | 2.866 | 4.299 | 5.732 | 86.1104 | 91.3885 | 93.3511 | 94.7498 | 94.8381 | 95.0506 | 94.1302 | 85.9074 | 91.6775 | 93.5459 | 95.0932 | 94.9449 | 95.3118 | 94.3016 | 85.5756 | 91.8187 | 93.6918 | 94.5668 | 94.968 | 95.2094 | 94.2095 | 2021-02-01 | 2024-10-11
Qcells North America | Q.VOLT H6.0SX {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Grid support, utility-interactive hybrid inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 6.017 | 240 | 97.5 | CSA Group | [4/12/2024] | CSA Group | [9/8/2022];[3/14/2023] | [V1.05, V1.03, V1.10] | 2023-03-13 | [9/8/2022];[3/14/2023] | 2023-03-13 | Intertek | 2023-01-11 | 2023-03-13 |  | N | N | 1.2 |  |  | 277 | 388.3 | 498.7 | 0.60166 | 1.2033 | 1.805 | 3.0083 | 4.5125 | 6.0166 | 95.0593 | 96.7801 | 97.1224 | 97.2712 | 97.1927 | 97.0029 | 97.0853 | 96.3129 | 97.458 | 97.7478 | 97.8566 | 97.7758 | 97.645 | 97.7085 | 94.8068 | 96.9441 | 97.5246 | 97.7657 | 97.6571 | 97.5829 | 97.5106 | 2023-03-13 | 2024-06-03
Qcells North America | Q.VOLT A6.0SX {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Grid support, utility-interactive inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 6.035 | 240 | 96 | CSA Group | [4/12/2024] | CSA Group | [3/14/2023] | [V1.05, V1.03, V1.10] | 2023-04-03 | [3/14/2023] | 2023-04-03 | Intertek | 2023-01-11 | 2023-04-03 |  | N | Y | 1.2 |  |  | 121.1 | 285.1 | 449.9 | 0.60349 | 1.207 | 1.8105 | 3.0174 | 4.5262 | 6.0349 | 92.4354 | 94.7517 | 95.3064 | 95.4957 | 95.3529 | 94.967 | 95.2113 | 92.582 | 95.9751 | 96.5614 | 96.8385 | 96.9642 | 96.915 | 96.6622 | 91.2831 | 95.6242 | 96.3268 | 96.8112 | 97.0461 | 97.0813 | 96.6106 | 2023-03-13 | 2024-06-03
Qcells North America | Q.HOME+ HYB-G1-7.0 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.0 kW, 240 Vac, single-phase, hybrid PV and battery, grid support utility interactive inverter | 6.666 | 240 | 94.5 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2021-01-11 | [10/23/2020] | 2021-01-11 | Intertek | 2020-09-11 | 2021-01-11 |  | N | N | 25 |  |  | 290 | 360 | 425 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 94.3168 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 94.5405 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836 | 94.4389 | 2021-01-11 | 2024-10-11
Qcells North America | Q.HOME+ AC-G1-7.0 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.0 kW, 240 Vac, single-phase, battery, grid support utility interactive inverter | 6.68 | 240 | 95 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2021-02-01 | [10/23/2020] | 2021-02-01 | Intertek | 2020-09-25 | 2021-02-01 |  | N | N | 25 |  |  | 280 | 390 | 500 | 0.668 | 1.336 | 2.004 | 3.34 | 5.01 | 6.68 | 88.2924 | 93.4839 | 94.8825 | 95.53 | 95.1135 | 94.4759 | 94.7871 | 88.5639 | 92.5762 | 94.6548 | 95.5514 | 95.4278 | 95.2339 | 94.9342 | 87.5631 | 92.1581 | 94.2612 | 95.3928 | 95.2266 | 94.6733 | 94.658 | 2021-02-01 | 2024-10-11
Qcells North America | Q.VOLT H7.6SX {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid support, utility-interactive hybrid inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 7.593 | 240 | 97.5 | CSA Group | [4/12/2024] | CSA Group | [9/8/2022];[3/14/2023] | [V1.05, V1.03, V1.10] | 2023-03-13 | [9/8/2022];[3/14/2023] | 2023-03-13 | Intertek | 2023-01-11 | 2023-03-13 |  | N | N | 1.2 |  |  | 234.1 | 365.5 | 498.4 | 0.75932 | 1.5186 | 2.278 | 3.7966 | 5.6949 | 7.5932 | 95.5301 | 96.9355 | 97.2078 | 97.319 | 96.9534 | 96.7056 | 96.9905 | 96.6677 | 97.8357 | 97.9705 | 97.937 | 97.774 | 97.5335 | 97.7786 | 96.0575 | 97.25 | 97.8206 | 97.8742 | 97.7481 | 97.6184 | 97.6843 | 2023-03-13 | 2024-06-03
Qcells North America | Q.VOLT A7.6SX {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid support, utility-interactive inverter, with Backup Interface (BI), Q.HOME HUB 200SX. Inverter with PCS functionality. | 7.601 | 240 | 96.5 | CSA Group | [4/12/2024] | CSA Group | [3/14/2023] | [V1.05, V1.03, V1.10] | 2023-04-03 | [3/14/2023] | 2023-04-03 | Intertek | 2023-01-11 | 2023-04-03 |  | N | Y | 1.2 |  |  | 149.7 | 300.1 | 449.8 | 0.76005 | 1.5201 | 2.2801 | 3.8003 | 5.7004 | 7.6005 | 93.371 | 95.3712 | 95.8107 | 95.8958 | 95.6855 | 95.3202 | 95.6182 | 94.124 | 96.454 | 96.8095 | 97.0054 | 96.9852 | 96.8122 | 96.8187 | 93.4413 | 96.1689 | 96.7056 | 96.9797 | 97.0796 | 97.0065 | 96.819 | 2023-03-13 | 2024-06-03
Qcells North America | Q.HOME+ HYB-G1-7.6 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, single-phase, hybrid PV and battery, grid support utility interactive inverter | 7.642 | 240 | 95.5 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2020-04-13 | [10/23/2020] | 2020-12-11 | Intertek | 2020-09-25 | 2020-10-12 |  | N | N | 44 |  |  | 304 | 402 | 500 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 95.4058 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 95.4118 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449 | 96.1997 | 2020-04-13 | 2024-10-11
Qcells North America | Q.HOME+ AC-G1-7.6 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, single-phase, battery, grid support utility interactive inverter | 7.832 | 240 | 95.5 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2020-04-13 | [10/23/2020] | 2020-12-11 | Intertek | 2020-09-25 | 2020-10-12 |  | N | N | 49.5 |  |  | 320 | 375 | 430 | 0.78321 | 1.5664 | 2.3496 | 3.916 | 5.874 | 7.8321 | 91.4312 | 94.9622 | 95.6242 | 95.751 | 95.4401 | 94.9759 | 95.32 | 92.2952 | 94.8694 | 95.6095 | 95.9358 | 95.7414 | 95.332 | 95.5645 | 92.7618 | 95.0616 | 95.7149 | 95.9028 | 95.7632 | 95.4369 | 95.6153 | 2020-04-13 | 2024-10-11
Qcells North America | Q.HOME+ HYB-G1-8.6 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, single-phase, hybrid PV and battery, grid support utility interactive inverter | 8.604 | 240 | 96 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2020-04-13 | [10/23/2020] | 2020-12-11 | Intertek | 2020-09-25 | 2020-10-12 |  | N | N | 40 |  |  | 258 | 379 | 500 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 95.2714 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 95.7814 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922 | 96.1906 | 2020-04-13 | 2024-10-11
Qcells North America | Q.HOME+ AC-G1-8.6 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, single-phase, battery, grid support utility interactive inverter | 8.613 | 240 | 95.5 | CSA Group | [12/12/2023] | CSA Group | [10/23/2020] | [V1.07, V1.03] | 2020-04-13 | [10/23/2020] | 2020-12-11 | Intertek | 2020-09-25 | 2020-10-12 |  | N | N | 42 |  |  | 363 | 396.5 | 430 | 0.8613 | 1.7226 | 2.5839 | 4.3065 | 6.4597 | 8.613 | 93.0135 | 95.2805 | 95.8088 | 95.9296 | 95.6312 | 95.1894 | 95.5709 | 92.8584 | 95.2474 | 95.8068 | 95.9989 | 95.7474 | 95.3227 | 95.6455 | 92.5757 | 95.1198 | 95.7234 | 95.9883 | 95.8346 | 95.4524 | 95.6683 | 2020-04-13 | 2024-10-11
RCT Power Energy Technology Corporation | Power Storage DC US-8.0 {208V} | Y | Y | Y | Y | Y | Y | N | Y | 7 kW, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.015 | 208 | 97 | CSA Group | [5/15/2024] | CSA Group | [5/15/2024] | [V127(2.27.0104-1.44)] | 2024-08-01 | [5/15/2024] | 2024-08-01 | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | N | 0.3 |  |  | 220 | 360 | 420 | 0.701 | 1.403 | 2.104 | 3.507 | 5.261 | 7.015 | 93.43 | 95.62 | 96.35 | 96.74 | 96.65 | 96.23 | 96.43 | 93.5 | 96.2 | 96.79 | 97.21 | 97.18 | 96.89 | 96.93 | 93.92 | 96.44 | 97.09 | 97.42 | 97.35 | 97.01 | 97.13 | 2024-08-01
RCT Power Energy Technology Corporation | Power Storage DC US-8.0 PRO {208V} | Y | Y | Y | Y | Y | Y | N | Y | 7 kW, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 7.015 | 208 | 97 | CSA Group | [5/15/2024] | CSA Group | [5/15/2024] | [V127(2.27.0104-1.44)] | 2024-08-01 | [5/15/2024] | 2024-08-01 | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | N | 0.3 |  |  | 220 | 360 | 420 | 0.701 | 1.403 | 2.104 | 3.507 | 5.261 | 7.015 | 93.4321 | 95.6214 | 96.3503 | 96.7391 | 96.6452 | 96.2338 | 96.4293 | 93.4986 | 96.2026 | 96.7947 | 97.209 | 97.1825 | 96.889 | 96.9305 | 93.9173 | 96.445 | 97.0889 | 97.4174 | 97.3475 | 97.0142 | 97.1321 | 2024-08-01
RCT Power Energy Technology Corporation | Power Storage DC US-8.0 {240V} | Y | Y | Y | Y | Y | Y | N | Y | 8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.0322 | 240 | 97 | CSA Group | [5/15/2024] | CSA Group | [5/15/2024] | [V127(2.27.0104-1.44)] | 2024-08-01 | [5/15/2024] | 2024-08-01 | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | N | 0.4025 |  |  | 220 | 360 | 420 | 0.80322 | 1.6064 | 2.4097 | 4.0161 | 6.0241 | 8.0322 | 94.4835 | 96.2889 | 96.8676 | 97.1353 | 96.9831 | 96.5638 | 96.8456 | 94.8035 | 96.8257 | 97.2969 | 97.5898 | 97.5257 | 97.2299 | 97.353 | 94.7472 | 96.886 | 97.455 | 97.7157 | 97.636 | 97.3371 | 97.463 | 2024-08-01
RCT Power Energy Technology Corporation | Power Storage DC US-8.0 PRO {240V} | Y | Y | Y | Y | Y | Y | N | Y | 8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.0322 | 240 | 97 | CSA Group | [5/15/2024] | CSA Group | [5/15/2024] | [V127(2.27.0104-1.44)] | 2024-08-01 | [5/15/2024] | 2024-08-01 | No Information Submitted | No Information Submitted | 2024-08-01 |  | N | N | 0.4025 |  |  | 220 | 360 | 420 | 0.80322 | 1.6064 | 2.4097 | 4.0161 | 6.0241 | 8.0322 | 94.4835 | 96.2889 | 96.8676 | 97.1353 | 96.9831 | 96.5638 | 96.8456 | 94.8035 | 96.8257 | 97.2969 | 97.5898 | 97.5257 | 97.2299 | 97.353 | 94.7472 | 96.886 | 97.455 | 97.7157 | 97.636 | 97.3371 | 97.463 | 2024-08-01
RCT Power Energy Technology Corporation | Power Storage DC US-15.0 {208V} | Y | Y | N | N | N | N | Y* | Y | 15 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 14.947 | 208 | 95.5 | CSA Group | [4/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-04-19 | 2025-07-01 |  | N | N | 16.1 |  |  | 220 | 380 | 440 | 1.495 | 2.989 | 4.484 | 7.473 | 11.21 | 14.947 | 91.8 | 93.83 | 94.74 | 95.19 | 95.05 | 94.69 | 94.83 | 92.49 | 94.62 | 95.44 | 95.86 | 95.79 | 95.51 | 95.56 | 93.2 | 95.35 | 95.98 | 96.24 | 96.09 | 95.75 | 95.94 | 2025-07-01
RCT Power Energy Technology Corporation | Power Storage DC US-15.0 {240V} | Y | Y | N | N | N | N | Y* | Y | 15 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 14.947 | 240 | 95.5 | CSA Group | [4/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-04-19 | 2025-07-01 |  | N | N | 16.1 |  |  | 220 | 380 | 440 | 1.495 | 2.989 | 4.484 | 7.473 | 11.21 | 14.947 | 90.56 | 93.08 | 94.22 | 94.88 | 94.87 | 94.58 | 94.52 | 92.58 | 94.69 | 95.49 | 95.96 | 95.92 | 95.66 | 95.67 | 93.17 | 95.39 | 96.01 | 96.32 | 96.22 | 95.93 | 96.04 | 2025-07-01
Rhombus Energy Solutions | BESI-50kW-480 {480V} | N | N | Y | Y | Y | N | N | N | 50kW, 480 Vac, transformer-less, 3-phase, Multi-Mode Grid Support Utility Interactive Energy Storage Inverter | 49.35 | 480 | 94 | No Information Submitted | No Information Submitted | UL | [06/29/2018] | [00021618] | 2018-10-15 | [06/29/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 103 |  |  | 550 | 636 | 840 | 4.935 | 9.87 | 14.805 | 24.675 | 37.0125 | 49.35 | 76.5714 | 88 | 92 | 95.1429 | 96 | 96 | 94.1629 | 79 | 89 | 92 | 95 | 96 | 96 | 94.28 | 79 | 88.8571 | 92 | 94 | 96 | 96 | 94.0629 | 2018-08-15 | 2018-10-15
Rhombus Energy Solutions | BESS-50kW-480 {480V} | N | N | Y | Y | Y | N | N | N | 50kW, 480 Vac, transformer-less, 3-phase, Grid Support Utility Interactive Energy Storage Inverter | 49.35 | 480 | 94 | No Information Submitted | No Information Submitted | UL | [06/29/2018] | [00021618] | 2018-10-15 | [06/29/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 103 |  |  | 550 | 636 | 840 | 4.935 | 9.87 | 14.805 | 24.675 | 37.0125 | 49.35 | 76.5714 | 88 | 92 | 95.1429 | 96 | 96 | 94.1629 | 79 | 89 | 92 | 95 | 96 | 96 | 94.28 | 79 | 88.8571 | 92 | 94 | 96 | 96 | 94.0629 | 2018-08-15 | 2018-10-15
Rhombus Energy Solutions | RES-BESS60DP-480 {480V} | Y | N | Y | Y | Y | Y | Y* | N | 60 kW, 480 Vac Grid Support Utility Interactive PV and Battery Inverter | 59.789 | 480 | 91.5 | No Information Submitted | No Information Submitted | UL | [09/03/2020] | [00020520] | 2020-12-11 | [09/03/2020] | 2022-02-11 | UL | 2021-12-20 | No Information Submitted |  | Y | N | 92 |  |  | 270 | 441 | 870 | 5.9789 | 11.9578 | 17.9367 | 29.8945 | 44.8418 | 59.789 | 82.328 | 88.79 | 91.344 | 93.2 | 93.729 | 93.632 | 92.6239 | 81.46 | 87.412 | 90.408 | 92.422 | 93.1 | 93 | 91.8796 | 79.44 | 86.038 | 88.894 | 91.278 | 92.026 | 92.06 | 90.6919 | 2020-12-11 | 2022-02-11
RNG International Inc. | RIV4850HI-SPS {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 5 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 5.0897 | 240 | 97 | SGS | [10/9/2023] | SGS | [11/7/2023] | [V1.04.06(DSP),V1.03.06(ARM)] | 2023-12-21 | [11/7/2023] | 2023-12-21 | SGS | 2023-10-20 | 2023-10-30 |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2023-06-01 | 2024-09-03
RNG International Inc. | RIV4860HI-SPS {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 6 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 6.117 | 240 | 97 | SGS | [10/9/2023] | SGS | [11/7/2023] | [V1.04.06(DSP),V1.03.06(ARM)] | 2023-12-21 | [11/7/2023] | 2023-12-21 | SGS | 2023-10-20 | 2023-10-30 |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2023-08-11 | 2024-09-03
RNG International Inc. | RIV4876HI-SPS {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 7 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 7.765 | 240 | 97 | SGS | [10/9/2023] | SGS | [11/7/2023] | [V1.04.06(DSP),V1.03.06(ARM)] | 2023-12-21 | [11/7/2023] | 2023-12-21 | SGS | 2023-10-20 | 2023-10-30 |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2023-08-11 | 2024-09-03
RNG International Inc. | RIV4880HI-SPS {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 8.084 | 240 | 97.5 | SGS | [10/9/2023] | SGS | [11/7/2023] | [V1.04.06(DSP),V1.03.06(ARM)] | 2023-12-21 | [11/7/2023] | 2023-12-21 | SGS | 2023-10-20 | 2023-10-30 |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2023-06-01 | 2024-09-03
RNG International Inc. | RIV4810HI-SPS {240V} | Y | Y | Y | Y | Y | Y | Y | Y | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 10.177 | 240 | 97 | SGS | [10/9/2023] | SGS | [11/7/2023] | [V1.04.06(DSP),V1.03.06(ARM)] | 2023-12-21 | [11/7/2023] | 2023-12-21 | SGS | 2023-10-20 | 2023-10-30 |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2023-08-11 | 2024-09-03
Savant Systems Inc. | PS-INV-10KW-100A-XX {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 10 kW, 240 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter, where XX are two characters, and with PCS functionality. | 9.9227 | 240 | 94 | Intertek | [12/11/2024] | Intertek | [5/9/2024] | [ARM/10010, pv/10050, pcs/10025] | 2024-02-12 | [12/1/2023] | 2024-02-12 | SunSpec Alliance | 2024-05-09 | No Information Submitted | Formerly SolarEdge Technologies Ltd. SE3800x {240V} | N | N | 21.92 |  |  | 250 | 360 | 530 | 0.99227 | 1.9845 | 2.9768 | 4.9613 | 7.442 | 9.9227 | 91.2728 | 93.8665 | 92.8466 | 93.9818 | 94.1882 | 93.8918 | 93.8364 | 94.433 | 94.2287 | 93.579 | 93.0905 | 94.0391 | 94.2974 | 93.8229 | 93.3697 | 95.1764 | 93.7928 | 94.5765 | 94.8844 | 95.1581 | 94.6565 | 2024-02-12 | 2024-12-23
Savant Systems Inc. | PS-INV-10KW-60A-XX {240V} | Y | Y | Y | Y | Y | Y | N | N | 10 kW, 240 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter, where XX can be any letters, numbers, or symbols | 9.9227 | 240 | 94 | Intertek | [12/1/2023] | Intertek | [12/1/2023] | [ARM/10010, pv/10050, pcs/10025] | 2024-02-12 | [12/1/2023] | 2024-02-12 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 21.92 |  |  | 250 | 360 | 530 | 0.99227 | 1.9845 | 2.9768 | 4.9613 | 7.442 | 9.9227 | 91.2728 | 93.8665 | 92.8466 | 93.9818 | 94.1882 | 93.8918 | 93.8364 | 94.433 | 94.2287 | 93.579 | 93.0905 | 94.0391 | 94.2974 | 93.8229 | 93.3697 | 95.1764 | 93.7928 | 94.5765 | 94.8844 | 95.1581 | 94.6565 | 2024-02-12
Savant Systems Inc. | PS-INV-12.5KW-100A-XX {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 12.5 kW, 240 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter, where XX are two characters, and with PCS functionality. | 12.4109 | 240 | 95 | Intertek | [12/11/2024] | Intertek | [5/9/2024] | [ARM/10010, pv/10050, pcs/10025] | 2024-02-12 | [12/1/2023] | 2024-02-12 | SunSpec Alliance | 2024-05-09 | No Information Submitted |  | N | N | 19.49 |  |  | 250 | 360 | 530 | 1.2411 | 2.4822 | 3.7233 | 6.2054 | 9.3082 | 12.4109 | 90.7047 | 93.4995 | 95.4688 | 95.3105 | 95.6568 | 96.2106 | 95.2832 | 90.4857 | 93.9644 | 94.7088 | 94.9923 | 95.5978 | 95.9127 | 95.0936 | 90.5641 | 94.3267 | 94.7516 | 94.8157 | 95.6216 | 96.0765 | 95.1036 | 2024-02-12 | 2024-12-23
Savant Systems Inc. | PS-INV-12.5KW-60A-XX {240V} | Y | Y | Y | Y | Y | Y | N | N | 12.5 kW, 240 Vac Transformerless Grid Support Utility Interactive Hybrid Inverter, where XX can be any letters, numbers, or symbols | 12.4109 | 240 | 95 | Intertek | [12/1/2023] | Intertek | [12/1/2023] | [ARM/10010, pv/10050, pcs/10025] | 2024-02-12 | [12/1/2023] | 2024-02-12 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 19.49 |  |  | 250 | 360 | 530 | 1.2411 | 2.4822 | 3.7233 | 6.2054 | 9.3082 | 12.4109 | 90.7047 | 93.4995 | 95.4688 | 95.3105 | 95.6568 | 96.2106 | 95.2832 | 90.4857 | 93.9644 | 94.7088 | 94.9923 | 95.5978 | 95.9127 | 95.0936 | 90.5641 | 94.3267 | 94.7516 | 94.8157 | 95.6216 | 96.0765 | 95.1036 | 2024-02-12 | 2023-01-11
Schneider Electric USA, Inc. | XW Pro 6848 NA {120V} | N | Y | Y | Y | Y | Y | Y* | Y | 5.75 kW, 120 Vac, Special Purpose Grid Support Utility Interactive Battery Inverter/Charger/Stand-alone | 5.747 | 120 | 93.5 | CSA Group | [1/15/2024] | CSA Group | [09/18/2020];[02/26/2021];[04/29/2021];[1/15/2024] | [V1.09BN09];[V1.11BN0028];[V1.11.BN0034];[V1.11.BN0049] | 2020-10-21 | [09/18/2020];[02/26/2021];[04/29/2021];[09/22/2021] | 2020-10-21 | CSA Group | 2019-12-18 | 2020-10-21 |  | N | N | 17.4 |  |  | 47 | 52 | 58 | 0.57472 | 1.1494 | 1.7242 | 2.8736 | 4.3104 | 5.7472 | 92.0582 | 94.5723 | 94.8034 | 94.5047 | 93.346 | 92.0348 | 93.7085 | 91.8256 | 94.4642 | 94.7 | 94.4268 | 93.245 | 91.9758 | 93.6085 | 91.6664 | 94.2323 | 94.5919 | 94.2474 | 93.1389 | 91.8939 | 93.4796 | 2020-10-21 | 2024-04-02
Schneider Electric USA, Inc. | XW Pro 6848 NA {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, Special Purpose Grid Support Utility Interactive Battery Inverter/Charger/Stand-alone, with PCS Functionality | 6.019 | 240 | 94 | CSA Group | [1/15/2024] | CSA Group | [09/18/2020];[02/26/2021];[04/29/2021]; [05/13/2022];[10/21/2022];[12/22/2022];[04/11/2023];[1/15/2024] | [V1.09BN09];[V1.11BN0028];[V1.11.BN0034];[V2.02BN08];[V2.04BN17];[v2.04BN26];[v2.04BN29];[v2.10BN25] | 2019-04-02 | [09/18/2020];[02/26/2021];[04/29/2021]; [05/13/2022];[10/21/2022];[12/22/2022];[04/11/2023] | 2020-04-13 | CSA Group | 2019-12-18 | 2020-01-21 |  | N | N | 0.37 |  |  | 47 | 52 | 58 | 0.60185 | 1.2037 | 1.8056 | 3.0093 | 4.5139 | 6.0185 | 92.9291 | 94.4949 | 94.7555 | 95.18 | 93.909 | 92.2423 | 94.1843 | 92.8245 | 94.4161 | 94.6733 | 95.15 | 93.8224 | 92.1594 | 94.1099 | 92.703 | 94.3317 | 94.5539 | 95.0913 | 93.7217 | 92.0594 | 94.0158 | 2019-04-02 | 2024-04-02
Schneider Electric USA, Inc. | HY8K1NA1 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.68 kW, 240Vac, Transformerless, Bi-directional, Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 7.626 | 240 | 97 | CSA Group | [5/14/2025] | CSA Group | [5/14/2025] | [M57] | 2023-10-11 | [10/20/2023] | 2024-03-21 | CSA Group | 2023-11-20 | 2024-01-11 |  | N | N | 13.71 |  |  | 200 | 360 | 480 | 0.763 | 1.525 | 2.288 | 3.813 | 5.72 | 7.626 | 93.03 | 95.42 | 96.11 | 96.65 | 96.61 | 96.38 | 96.34 | 93.66 | 96.41 | 97.06 | 97.43 | 97.4 | 97.14 | 97.15 | 93.55 | 96.53 | 97.2 | 97.61 | 97.55 | 97.81 | 97.32 | 2023-10-11 | 2025-09-22
Schneider Electric USA, Inc. | EMGPCS0500ACCANS00 {400V} | N | Y | N | N | N | N | N | N | 500 kW, 400 Vac, Grid Support Utility Interactive Inverter | 502.611 | 400 | 97 | Intertek | [4/24/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 335.38 |  |  | 600 | 750 | 900 | 50.261 | 100.522 | 150.783 | 251.306 | 376.958 | 502.611 | 95.7 | 97.31 | 97.82 | 98.1 | 98.05 | 97.87 | 97.89 | 93.86 | 96.13 | 96.9 | 97.38 | 97.43 | 97.35 | 97.14 | 92.39 | 95.39 | 96.34 | 96.98 | 97.09 | 97.05 | 96.7 | 2025-01-13
Shanghai Chelion RenewableTechnology Co., Ltd. | iHome-INV7.6K-H1H02 {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac Grid Support Power Conversion System | 7.581 | 240 | 97 | Intertek | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.7581 | 1.5162 | 2.2743 | 3.7905 | 5.6858 | 7.581 | 94.2651 | 95.2225 | 96.163 | 96.9234 | 97.1125 | 97.0636 | 96.748 | 95.2164 | 96.1836 | 96.7935 | 97.3649 | 97.6024 | 97.5348 | 97.2857 | 94.8243 | 95.8334 | 96.5515 | 97.2034 | 97.4231 | 97.3541 | 97.0855 | 2023-03-13
Shanghai Chelion RenewableTechnology Co., Ltd. | iHome-INV9.6K-H1H02 {240V} | Y | Y | N | N | N | N | N | N | 9 kW, 240 Vac Grid Support Power Conversion System | 9.5733 | 240 | 97 | Intertek | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.95733 | 1.9147 | 2.872 | 4.7866 | 7.1799 | 9.5733 | 94.324 | 95.4338 | 96.4736 | 97.0126 | 97.0914 | 97.0133 | 96.8032 | 95.7635 | 96.4127 | 97.0422 | 97.4839 | 97.5735 | 97.4048 | 97.352 | 94.8907 | 95.9847 | 96.8438 | 97.3145 | 97.3946 | 97.234 | 97.133 | 2023-03-13
Shanghai Chelion RenewableTechnology Co., Ltd. | iHome-INV10K-H1H02 {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Power Conversion System | 9.9563 | 240 | 97 | Intertek | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.99563 | 1.9913 | 2.9869 | 4.9782 | 7.4672 | 9.9563 | 94.3337 | 95.6136 | 96.5122 | 97.0308 | 97.0728 | 96.9826 | 96.8097 | 95.7935 | 96.475 | 97.0733 | 97.5049 | 97.543 | 97.3726 | 97.3468 | 95.184 | 96.0843 | 96.883 | 97.3434 | 97.3652 | 97.2134 | 97.1439 | 2023-03-13
Shanghai Chelion RenewableTechnology Co., Ltd. | iHome-INV11.4K-H1H02 {240V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 240 Vac Grid Support Power Conversion System | 11.3705 | 240 | 97 | Intertek | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.1371 | 2.2741 | 3.4112 | 5.6853 | 8.5279 | 11.3705 | 94.3642 | 96.055 | 96.9052 | 97.1019 | 97.0437 | 96.9028 | 96.8756 | 95.8125 | 96.7944 | 97.3353 | 97.6036 | 97.4725 | 97.2634 | 97.3728 | 95.284 | 96.5532 | 97.1622 | 97.414 | 97.3038 | 97.0831 | 97.1806 | 2023-03-13
Shanghai Chelion RenewableTechnology Co., Ltd. | iHome-INV12K-H1H02 {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Power Conversion System | 11.9682 | 240 | 97 | Intertek | [1/18/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.1968 | 2.3936 | 3.5905 | 5.9841 | 8.9761 | 11.9682 | 94.3841 | 96.0625 | 96.9237 | 97.1216 | 97.0131 | 96.8713 | 96.8654 | 95.8343 | 96.815 | 97.3428 | 97.6232 | 97.4548 | 97.223 | 97.3683 | 95.3154 | 96.5735 | 97.1839 | 97.4422 | 97.282 | 97.04 | 97.1777 | 2023-03-13
SHEN ZHEN MY SMART ENERGY ELECTRIC CO., LTD | MY-HL8K-P2WB {240V} | Y | Y | N | N | N | N | N |  | 8 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.9814 | 240 | 96 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.39 |  |  | 108 | 380 | 480 | 0.79814 | 1.5963 | 2.3944 | 3.9907 | 5.986 | 7.9814 | 90.9385 | 94.1039 | 94.9752 | 95.083 | 95.0387 | 94.6196 | 94.8087 | 92.1593 | 95.6656 | 96.6163 | 96.6433 | 97.0374 | 96.9779 | 96.6374 | 92.4438 | 95.9014 | 96.6012 | 97.0486 | 97.2916 | 97.2167 | 96.8905 | 2026-04-13 |  | Y | Y | Y | Y | Y | Y | Y | Y | N
SHEN ZHEN MY SMART ENERGY ELECTRIC CO., LTD | MY-HL10K-P2WB {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.0109 | 240 | 96 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.12 |  |  | 135 | 380 | 480 | 1.0011 | 2.0022 | 3.0033 | 5.0055 | 7.5082 | 10.0109 | 92.0512 | 94.9782 | 94.9328 | 95.3714 | 95.3991 | 94.9543 | 95.1601 | 93.0994 | 96.2304 | 96.2761 | 96.8719 | 97.0247 | 96.9062 | 96.7001 | 93.6663 | 96.3246 | 96.5808 | 97.0256 | 97.1253 | 97.0288 | 96.8558 | 2026-04-13 |  | Y | Y | Y | Y | Y | Y | Y | Y | N
SHEN ZHEN MY SMART ENERGY ELECTRIC CO., LTD | MY-HL12K-P2WB {240V} | Y | Y | N | N | N | N | N |  | 12 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.0145 | 240 | 96.5 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.39 |  |  | 161 | 380 | 480 | 1.2014 | 2.4029 | 3.6043 | 6.0072 | 9.0109 | 12.0145 | 93.1006 | 95.228 | 95.5523 | 95.8393 | 95.6025 | 95.1408 | 95.5043 | 94.3433 | 96.5994 | 96.675 | 97.0511 | 96.9701 | 96.7737 | 96.8183 | 95.2452 | 96.8669 | 96.9412 | 97.2998 | 97.1893 | 96.9458 | 97.0767 | 2026-04-13 |  | Y | Y | Y | Y | Y | Y | Y | Y | N
SHEN ZHEN MY SMART ENERGY ELECTRIC CO., LTD | MY-HL15K-P2WB {240V} | Y | Y | N | N | N | N | N |  | 15 kW, 240 Vac Grid Support Utility Interactive Inverter | 15.0148 | 240 | 96.5 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.08 |  |  | 202 | 380 | 480 | 1.5015 | 3.003 | 4.5045 | 7.5074 | 11.2611 | 15.0148 | 94.5483 | 95.5289 | 96.0138 | 96.1843 | 95.8054 | 95.25 | 95.8181 | 95.5893 | 96.5176 | 96.9793 | 97.101 | 96.8732 | 96.5137 | 96.8467 | 96.0793 | 96.8399 | 97.2558 | 97.3226 | 96.9795 | 96.6351 | 97.0245 | 2026-04-13 |  | Y | Y | Y | Y | Y | Y | Y | Y | N
SHENZHEN CLOU ELECTRONICS CO., LTD. | CL215HX-IEC/UL {690V} | N | Y | N | N | N | N | N |  | 236.841 kW, 690 Vac, Bi-directional, Transformerless, Grid Support Utility Interactive Inverter | 236.841 | 690 | 98.5 | CSA Group | [9/25/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 34.62 |  |  | 1060 | 1331 | 1500 | 23.684 | 47.368 | 71.052 | 118.42 | 177.631 | 236.841 | 97.59 | 98.6 | 98.7 | 98.71 | 98.89 | 98.56 | 98.75 | 96.73 | 98.4 | 98.39 | 98.47 | 98.69 | 98.36 | 98.5 | 97.01 | 98.24 | 98.33 | 98.36 | 98.59 | 98.29 | 98.42 | 2026-01-02
SHENZHEN CLOU ELECTRONICS CO., LTD. | CL430HX-IEC/UL {690V} | N | Y | N | N | N | N | N |  | 473.495 kW, 690 Vac, Bi-directional, Transformerless, Grid Support Utility Interactive Inverter | 473.495 | 690 | 98.5 | CSA Group | [9/25/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 72.52 |  |  | 1060 | 1331 | 1500 | 47.35 | 94.699 | 142.049 | 236.748 | 355.122 | 473.495 | 97.25 | 98.53 | 98.66 | 98.71 | 98.85 | 98.56 | 98.7 | 96.75 | 98.23 | 98.42 | 98.57 | 98.68 | 98.37 | 98.51 | 96.57 | 98.11 | 98.31 | 98.45 | 98.63 | 98.31 | 98.43 | 2026-01-02
Shenzhen Cubenergy Co., Ltd. | CBAC-140-HA-M-US {480V} | N | Y | N | N | N | N | N | N | 140 kW, 480Vac Grid Support Utility Interactive Inverter with 225 kW, liquid-immersed three-phase transformer | 140 | 480 | 97.5 | TUV Rheinland of North America | [2/28/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on the 225 kVA liquid-immersed transformer DOE tables. | N | N | 316 |  |  | 800 | 900 | 1000 | 15.467 | 30.934 | 46.402 | 77.336 | 116.004 | 154.672 | 96.09 | 97.33 | 97.48 | 97.6 | 97.5 | 97.19 | 97.44 | 95.68 | 97.21 | 97.38 | 97.43 | 97.35 | 97.07 | 97.28 | 95.39 | 96.86 | 97.18 | 97.39 | 97.19 | 96.98 | 97.13 | 2025-05-01
Shenzhen Cubenergy Co., Ltd. | EH-0200-HA-M-US {690V} | N | Y | N | N | N | N | N | N | 220 kW, 690 Vac Grid Support Utility Interactive Inverter with 225 kW, liquid-immersed three-phase transformer | 220.432 | 690 | 97.5 | TUV Rheinland of North America | [10/22/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on the 225 kVA liquid-immersed transformer DOE tables. | N | N | 316 |  |  | 1056 | 1199 | 1346 | 22.0432 | 44.0864 | 66.1296 | 110.216 | 165.324 | 220.432 | 96.2338 | 97.4415 | 97.8388 | 98.012 | 97.9147 | 97.6398 | 97.8214 | 95.7065 | 97.1207 | 97.6218 | 97.8341 | 97.7678 | 97.5577 | 97.6389 | 95.0323 | 96.5501 | 97.2843 | 97.6244 | 97.5903 | 97.3908 | 97.3964 | 2025-02-11
Shenzhen Eternalplanet Energy Pingshan Ltd. | HNA7G {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.58 | 240 | 95 | TUV Rheinland | [7/21/2022] | TUV Rheinland | [7/21/2022] | [V2.0] | 2023-09-21 | [7/21/2022] | 2023-09-21 | TUV Rheinland | 2022-09-05 | 2022-08-15 |  | N | N | 23 |  |  | 240 | 350 | 480 | 0.758 | 1.516 | 2.274 | 3.79 | 5.685 | 7.581 | 90 | 91.46 | 93.64 | 94.94 | 94.15 | 93.8 | 93.94 | 89.04 | 91.71 | 94.45 | 95.18 | 94.58 | 94.13 | 94.3 | 92.5 | 95.06 | 95.48 | 95.89 | 95.66 | 95.37 | 95.52 | 2023-09-21
Shenzhen Eternalplanet Energy Pingshan Ltd. | HNA7G_AT {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.58 | 240 | 95 | TUV Rheinland | [7/21/2022] | TUV Rheinland | [7/21/2022] | [V2.0] | 2023-09-21 | [7/21/2022] | 2023-09-21 | TUV Rheinland | 2022-09-05 | 2022-08-15 |  | N | N | 23 |  |  | 240 | 350 | 480 | 0.758 | 1.516 | 2.274 | 3.79 | 5.685 | 7.581 | 90 | 91.46 | 93.64 | 94.94 | 94.15 | 93.8 | 93.94 | 89.04 | 91.71 | 94.45 | 95.18 | 94.58 | 94.13 | 94.3 | 92.5 | 95.06 | 95.48 | 95.89 | 95.66 | 95.37 | 95.52 | 2023-09-21
Shenzhen Eternalplanet Energy Pingshan Ltd. | HNA7G_TT {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.58 | 240 | 95 | TUV Rheinland | [7/21/2022] | TUV Rheinland | [7/21/2022] | [V2.0] | 2023-09-21 | [7/21/2022] | 2023-09-21 | TUV Rheinland | 2022-09-05 | 2022-08-15 |  | N | N | 23 |  |  | 240 | 350 | 480 | 0.758 | 1.516 | 2.274 | 3.79 | 5.685 | 7.581 | 90 | 91.46 | 93.64 | 94.94 | 94.15 | 93.8 | 93.94 | 89.04 | 91.71 | 94.45 | 95.18 | 94.58 | 94.13 | 94.3 | 92.5 | 95.06 | 95.48 | 95.89 | 95.66 | 95.37 | 95.52 | 2023-09-21
Shenzhen Eternalplanet Energy Pingshan Ltd. | HNA7W {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.58 | 240 | 95 | TUV Rheinland | [7/21/2022] | TUV Rheinland | [7/21/2022] | [V2.0] | 2023-09-21 | [7/21/2022] | 2023-09-21 | TUV Rheinland | 2022-09-05 | 2022-08-15 |  | N | N | 23 |  |  | 240 | 350 | 480 | 0.758 | 1.516 | 2.274 | 3.79 | 5.685 | 7.581 | 90 | 91.46 | 93.64 | 94.94 | 94.15 | 93.8 | 93.94 | 89.04 | 91.71 | 94.45 | 95.18 | 94.58 | 94.13 | 94.3 | 92.5 | 95.06 | 95.48 | 95.89 | 95.66 | 95.37 | 95.52 | 2023-09-21
Shenzhen Eternalplanet Energy Pingshan Ltd. | HNA7W_TT {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.58 | 240 | 95 | TUV Rheinland | [7/21/2022] | TUV Rheinland | [7/21/2022] | [V2.0] | 2023-09-21 | [7/21/2022] | 2023-09-21 | TUV Rheinland | 2022-09-05 | 2022-08-15 |  | N | N | 23 |  |  | 240 | 350 | 480 | 0.758 | 1.516 | 2.274 | 3.79 | 5.685 | 7.581 | 90 | 91.46 | 93.64 | 94.94 | 94.15 | 93.8 | 93.94 | 89.04 | 91.71 | 94.45 | 95.18 | 94.58 | 94.13 | 94.3 | 92.5 | 95.06 | 95.48 | 95.89 | 95.66 | 95.37 | 95.52 | 2023-09-21
Shenzhen Growatt New Energy Co., Ltd. | MIN 3000TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 2.626 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 2.626 | 208 | 96.5 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.576 |  |  | 125 | 380 | 480 | 0.26259 | 0.52518 | 0.78777 | 1.3129 | 1.9694 | 2.6259 | 91.2934 | 93.7087 | 95.2183 | 95.8997 | 95.8355 | 95.6645 | 95.4784 | 93.5823 | 95.3477 | 96.9042 | 97.2283 | 97.3991 | 97.0876 | 97.033 | 92.5038 | 95.6858 | 96.4301 | 96.8779 | 96.8499 | 96.9624 | 96.579 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 3000TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 2.93 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 2.934 | 240 | 93.5 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 150 | 380 | 480 | 0.29344 | 0.58687 | 0.88031 | 1.4672 | 2.2008 | 2.9344 | 83.5494 | 88.742 | 91.5187 | 93.466 | 94.3778 | 94.5735 | 93.1381 | 82.9531 | 88.9774 | 91.284 | 94.7821 | 95.7609 | 95.9493 | 94.1761 | 81.2489 | 86.9992 | 91.7283 | 93.6156 | 94.9487 | 95.5889 | 93.3689 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 3000TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 3.0 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 2.999 | 208 | 93.5 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 150 | 380 | 480 | 0.29986 | 0.59972 | 0.89958 | 1.4993 | 2.249 | 2.9986 | 83.2934 | 88.7087 | 91.2183 | 93.3997 | 94.3355 | 94.6645 | 93.0584 | 83.5823 | 88.3477 | 91.9042 | 94.2283 | 95.3991 | 95.8876 | 93.933 | 82.5038 | 87.6858 | 91.4301 | 93.8779 | 94.8499 | 95.7624 | 93.429 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 3000TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.095 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 3.095 | 240 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.593 |  |  | 125 | 380 | 480 | 0.30951 | 0.61902 | 0.92853 | 1.5475 | 2.3213 | 3.0951 | 92.5494 | 94.742 | 95.5187 | 96.466 | 96.3778 | 96.1735 | 96.0481 | 94.9531 | 96.9774 | 97.284 | 97.7821 | 97.7609 | 97.4493 | 97.5411 | 93.2489 | 95.9992 | 96.7283 | 97.2156 | 97.3487 | 97.3889 | 97.0169 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 3800TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.324 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 3.324 | 208 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.576 |  |  | 160 | 380 | 480 | 0.33238 | 0.66477 | 0.99715 | 1.6619 | 2.4929 | 3.3238 | 91.7552 | 94.4271 | 95.625 | 96.3968 | 96.3716 | 96.2365 | 95.9987 | 92.8401 | 95.7332 | 97.3293 | 97.2908 | 97.7747 | 97.4727 | 97.3051 | 92.8717 | 95.7668 | 96.7784 | 97.4953 | 97.5884 | 97.4672 | 97.1859 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 3600TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 3.58 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 3.581 | 208 | 94 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 150 | 380 | 480 | 0.3581 | 0.7162 | 1.0743 | 1.7905 | 2.6858 | 3.581 | 84.9552 | 90.4271 | 92.825 | 93.7968 | 94.5716 | 94.4365 | 93.6007 | 85.0401 | 90.7332 | 93.4293 | 94.4908 | 95.7747 | 96.2727 | 94.5671 | 82.3717 | 88.9668 | 92.9784 | 94.2953 | 95.7884 | 95.6672 | 94.2539 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 3600TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 3.61 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.608 | 240 | 94 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 150 | 380 | 480 | 0.36084 | 0.72167 | 1.0825 | 1.8042 | 2.7063 | 3.6084 | 84.9226 | 90.0495 | 92.9079 | 93.7875 | 94.4318 | 94.456 | 93.5153 | 84.8681 | 90.93 | 93.8567 | 94.562 | 95.5583 | 95.9727 | 94.5066 | 82.4977 | 88.9887 | 92.2935 | 94.4687 | 94.7381 | 95.6144 | 93.6549 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 3800TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.888 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 3.888 | 240 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.593 |  |  | 160 | 380 | 480 | 0.38882 | 0.77764 | 1.1665 | 1.9441 | 2.9162 | 3.8882 | 92.9226 | 95.0495 | 95.9079 | 96.5875 | 96.7318 | 96.456 | 96.3523 | 95.8681 | 97.43 | 97.8567 | 98.062 | 98.0583 | 97.9727 | 97.9116 | 93.4977 | 96.4887 | 97.1935 | 97.6687 | 97.7381 | 97.6144 | 97.4199 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 4000TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 3.99 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.988 | 240 | 95 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 180 | 380 | 480 | 0.39884 | 0.79767 | 1.1965 | 1.9942 | 2.9913 | 3.9884 | 86.9226 | 91.0495 | 92.9079 | 94.5875 | 95.1318 | 95.156 | 94.2193 | 86.5681 | 92.23 | 94.3567 | 95.662 | 96.2583 | 96.1727 | 95.3116 | 84.4977 | 91.0887 | 93.3935 | 95.1687 | 96.1381 | 96.0144 | 94.8809 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 4000TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 4.0 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 4.004 | 208 | 95 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 150 | 380 | 480 | 0.4004 | 0.8008 | 1.2012 | 2.002 | 3.003 | 4.004 | 86.7552 | 91.4271 | 93.125 | 94.3968 | 94.9716 | 95.2365 | 94.1367 | 86.8401 | 92.1332 | 94.3293 | 95.6908 | 96.1747 | 96.1727 | 95.2761 | 84.8717 | 91.2668 | 93.5784 | 95.1953 | 96.0884 | 96.0672 | 94.9089 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 5000TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4.28 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 4.28 | 208 | 97.5 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.576 |  |  | 210 | 380 | 480 | 0.42805 | 0.85609 | 1.2841 | 2.1402 | 3.2104 | 4.2805 | 93.9969 | 95.6291 | 96.5292 | 97.277 | 96.8685 | 96.4968 | 96.7182 | 95.6415 | 97.3556 | 97.7545 | 97.9536 | 97.7989 | 97.5872 | 97.707 | 95.0137 | 96.8034 | 97.3434 | 97.6629 | 97.6924 | 97.3985 | 97.478 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 4600TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 4.598 | 240 | 95 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 180 | 380 | 480 | 0.45977 | 0.91955 | 1.3793 | 2.2989 | 3.4483 | 4.5977 | 86.9226 | 92.0495 | 93.3079 | 94.9095 | 95.2538 | 95.188 | 94.4512 | 86.8681 | 92.43 | 94.5567 | 95.897 | 96.2323 | 96.2077 | 95.3949 | 85.4977 | 91.4887 | 93.6035 | 95.4327 | 96.2821 | 96.1164 | 95.103 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 4600TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 4.6 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 4.604 | 208 | 95 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 180 | 380 | 480 | 0.4604 | 0.9208 | 1.3812 | 2.302 | 3.453 | 4.604 | 86.7552 | 91.6271 | 93.425 | 94.7968 | 95.1716 | 95.2365 | 94.3727 | 87.8401 | 92.8332 | 94.7293 | 95.7908 | 96.2747 | 96.2727 | 95.4781 | 85.8717 | 92.5668 | 94.0784 | 95.2953 | 96.3884 | 96.2672 | 95.2639 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 5000TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4.943 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 4.943 | 240 | 97.5 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.593 |  |  | 210 | 380 | 480 | 0.49432 | 0.98864 | 1.483 | 2.4716 | 3.7074 | 4.9432 | 94.2674 | 96.0279 | 96.6177 | 96.9688 | 96.7976 | 96.4626 | 96.6555 | 95.8274 | 97.6476 | 97.9929 | 98.1977 | 98.0262 | 97.7757 | 97.9388 | 95.1548 | 97.2155 | 97.7005 | 97.9802 | 97.817 | 97.6089 | 97.6903 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 5000TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 4.95 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 4.954 | 240 | 95 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 230 | 380 | 480 | 0.49537 | 0.99073 | 1.4861 | 2.4768 | 3.7153 | 4.9537 | 88.2674 | 92.0279 | 93.9177 | 95.1688 | 95.5976 | 95.4626 | 94.8275 | 88.8274 | 93.6476 | 94.5929 | 96.1977 | 96.5262 | 95.9757 | 95.7458 | 86.6548 | 92.4155 | 93.7005 | 95.5802 | 96.117 | 96.1089 | 95.1503 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 5000TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 4.97 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 4.969 | 208 | 95.5 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 230 | 380 | 480 | 0.49688 | 0.99376 | 1.4906 | 2.4844 | 3.7266 | 4.9688 | 87.9969 | 91.8291 | 94.0292 | 95.277 | 95.6685 | 95.4968 | 94.8822 | 88.6415 | 93.5556 | 94.7545 | 95.9536 | 96.5989 | 96.0872 | 95.746 | 87.0137 | 92.8034 | 93.5434 | 96.1629 | 96.0924 | 96.1985 | 95.279 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 6000TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.143 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 5.143 | 208 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.576 |  |  | 170 | 380 | 480 | 0.51426 | 1.0285 | 1.5428 | 2.5713 | 3.8569 | 5.1426 | 93.4812 | 95.1436 | 95.9216 | 96.4143 | 96.4086 | 96.2016 | 96.1607 | 95.7404 | 97.2023 | 97.6753 | 97.7276 | 97.7059 | 97.2003 | 97.5777 | 94.531 | 96.5287 | 97.1839 | 97.4841 | 97.5 | 97.1255 | 97.2727 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 6000TL BL-US {208V} | Y | N | Y | Y | Y | Y | Y* | Y | 5.23 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 5.232 | 208 | 96 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 230 | 380 | 480 | 0.52322 | 1.0464 | 1.5697 | 2.6161 | 3.9242 | 5.2322 | 91.6216 | 94.3804 | 95.004 | 95.6415 | 95.648 | 95.6498 | 95.345 | 94.0058 | 96.3321 | 96.66 | 96.8442 | 96.8058 | 96.5216 | 96.6465 | 93.9666 | 96.0001 | 96.4128 | 96.8643 | 96.7314 | 96.4957 | 96.5622 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 6000TL BL-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 5.86 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 5.864 | 240 | 96 | No Information Submitted | No Information Submitted | Intertek | [03/24/2021] | [RA1.0] | 2021-05-11 | [03/24/2021] | 2021-05-11 | Intertek | 2021-01-25 | 2021-05-11 |  | N | N | 15.128 |  |  | 230 | 380 | 480 | 0.58643 | 1.1729 | 1.7593 | 2.9322 | 4.3982 | 5.8643 | 91.5816 | 94.3604 | 94.954 | 95.5915 | 95.628 | 95.6398 | 95.3148 | 93.9658 | 96.3021 | 96.58 | 96.8142 | 96.7558 | 96.5216 | 96.601 | 93.9266 | 95.9701 | 96.3828 | 96.8343 | 96.7114 | 96.4757 | 96.5376 | 2021-05-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 6000TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.918 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 5.918 | 240 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.593 |  |  | 170 | 380 | 480 | 0.59178 | 1.1836 | 1.7753 | 2.9589 | 4.4383 | 5.9177 | 93.4931 | 95.0713 | 96.0091 | 96.5068 | 96.5375 | 96.277 | 96.2595 | 96.2836 | 97.6235 | 97.995 | 98.0323 | 97.7405 | 97.6407 | 97.7632 | 95.2829 | 97.0935 | 97.4899 | 97.8279 | 97.6998 | 97.4333 | 97.5612 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 7600TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.58 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 6.58 | 208 | 97 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.576 |  |  | 212 | 380 | 480 | 0.65804 | 1.3161 | 1.9741 | 3.2902 | 4.9353 | 6.5804 | 93.7826 | 95.5421 | 96.606 | 96.8324 | 96.8224 | 96.4415 | 96.5939 | 95.6144 | 97.208 | 97.6283 | 97.7129 | 97.8083 | 97.3895 | 97.628 | 94.0659 | 96.3435 | 97.3147 | 97.3793 | 97.4451 | 97.2215 | 97.2142 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 7600TL-XH2 US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.61 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 6.611 | 208 | 95.6 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.12 |  |  | 150 | 345 | 500 | 0.661 | 1.322 | 1.983 | 3.306 | 4.959 | 6.611 | 88.96 | 92.49 | 94 | 94.76 | 94.85 | 94.47 | 94.36 | 93.96 | 96.07 | 96.65 | 96.88 | 96.88 | 96.67 | 96.69 | 90.55 | 94.4 | 95.25 | 95.84 | 96.07 | 96.16 | 95.62 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | MIN 8200TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.2 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 7.166 | 208 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.71659 | 1.4332 | 2.1498 | 3.5829 | 5.3744 | 7.1659 | 93.818 | 95.9467 | 96.5916 | 96.9394 | 96.8921 | 96.7981 | 96.691 | 95.2258 | 97.2231 | 97.7432 | 97.9238 | 97.8229 | 97.7412 | 97.6966 | 93.7147 | 96.5216 | 97.2952 | 97.7041 | 97.7221 | 97.6373 | 97.4425 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | MIN 7600TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.524 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 7.524 | 240 | 97.5 | Intertek | [3/14/2023] | Intertek | [3/14/2023] | [UE1.0] | 2021-01-21 | [3/14/2023] | 2021-01-21 | Intertek | 2020-11-09 | 2021-01-21 |  | N | N | 1.593 |  |  | 212 | 380 | 480 | 0.75242 | 1.5048 | 2.2573 | 3.7621 | 5.6431 | 7.5242 | 94.8321 | 96.2443 | 96.9372 | 97.1359 | 97.0549 | 96.4681 | 96.899 | 96.1031 | 97.82 | 98.0103 | 98.1875 | 98.0302 | 97.4081 | 97.9421 | 95.2191 | 97.2034 | 97.6838 | 97.8749 | 97.7927 | 97.3782 | 97.6437 | 2021-01-21 | 2023-07-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 7600TL-XH2 US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 7.65 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 7.651 | 240 | 96 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.53 |  |  | 150 | 345 | 500 | 0.765 | 1.53 | 2.295 | 3.825 | 5.738 | 7.651 | 91.51 | 94.02 | 95.54 | 95.78 | 95.47 | 95.06 | 95.29 | 95.15 | 96.32 | 96.83 | 97.44 | 97.45 | 97.27 | 97.21 | 91.54 | 94.77 | 96.08 | 96.68 | 96.53 | 96.38 | 96.21 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | MIN 9000TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 7.874 | 208 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.78742 | 1.5748 | 2.3623 | 3.9371 | 5.9056 | 7.8742 | 93.9829 | 96.0797 | 96.6986 | 97.0304 | 96.9127 | 96.7846 | 96.7465 | 95.5872 | 97.3526 | 97.782 | 97.9238 | 97.7705 | 97.6713 | 97.6909 | 94.5847 | 96.692 | 97.396 | 97.712 | 97.6675 | 97.5806 | 97.4678 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | SPH 8000TL-HU-US(B) {208V} | Y | Y | Y | Y | Y | Y | Y* | N | 8kW, 208 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 7.9075 | 208 | 96 | Intertek | [12/16/2024] | Intertek | [12/16/2024] | [Skaa-00] | 2025-02-21 | [12/16/2024] | 2025-02-21 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 54.38 |  |  | 160 | 370 | 450 | 0.79075 | 1.5815 | 2.3723 | 3.9538 | 5.9306 | 7.9075 | 92.7147 | 94.7026 | 95.7205 | 95.3803 | 94.8072 | 94.5138 | 94.9335 | 93.3925 | 96.7303 | 98.328 | 97.8196 | 97.55 | 96.4208 | 97.4362 | 96.0032 | 97.2174 | 97.722 | 96.9998 | 96.0451 | 96.139 | 96.5084 | 2025-02-21 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 8000TL-HU-US(B) {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 8kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 7.9251 | 240 | 96 | Intertek | [12/16/2024] | Intertek | [12/16/2024] | [Skaa-00] | 2025-02-21 | [12/16/2024] | 2025-02-21 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 53.28 |  |  | 160 | 370 | 450 | 0.79251 | 1.585 | 2.3775 | 3.9625 | 5.9438 | 7.9251 | 93.7414 | 94.3116 | 95.3773 | 96.1404 | 95.1985 | 94.2518 | 95.2678 | 93.9854 | 96.9456 | 97.0733 | 96.317 | 96.6317 | 96.3931 | 96.5165 | 95.2983 | 96.6715 | 96.9225 | 96.7206 | 96.1224 | 95.9018 | 96.3275 | 2025-02-21 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 8200TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.2 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 8.251 | 240 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.82514 | 1.6503 | 2.4754 | 4.1257 | 6.1886 | 8.2514 | 93.9258 | 96.1247 | 96.8143 | 97.2666 | 97.2617 | 97.0721 | 97.0092 | 95.5722 | 97.4863 | 97.9916 | 98.2391 | 98.1842 | 98.0166 | 98.0249 | 93.7743 | 96.6734 | 97.4868 | 97.9609 | 97.966 | 97.9229 | 97.673 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | MIN 10000TL-XH2 US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 8.61 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 8.606 | 208 | 96 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.12 |  |  | 150 | 345 | 500 | 0.861 | 1.721 | 2.582 | 4.303 | 6.455 | 8.606 | 91.98 | 94.53 | 95.17 | 95.38 | 94.87 | 94.34 | 94.85 | 94.99 | 96.51 | 96.87 | 96.97 | 96.71 | 96.34 | 96.68 | 92.54 | 95.17 | 95.88 | 96.22 | 96.1 | 95.81 | 95.9 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | MIN 10000TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 8.76 | 208 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.87595 | 1.7519 | 2.6278 | 4.3797 | 6.5696 | 8.7595 | 94.7147 | 96.1872 | 96.7641 | 96.9456 | 96.7226 | 96.627 | 96.6625 | 96.1898 | 97.4947 | 97.8331 | 97.8547 | 97.653 | 97.5442 | 97.6451 | 94.884 | 96.9958 | 97.5353 | 97.726 | 97.6134 | 97.5151 | 97.4827 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | MIN 9000TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 9.063 | 240 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.90625 | 1.8125 | 2.7188 | 4.5312 | 6.7969 | 9.0625 | 94.2384 | 96.2702 | 96.908 | 97.3235 | 97.2 | 97.0403 | 97.018 | 95.9482 | 97.6026 | 98.0707 | 98.2515 | 98.1428 | 97.9914 | 98.0346 | 94.3716 | 96.8985 | 97.6347 | 98.0229 | 98.0409 | 97.9412 | 97.7795 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | SPH 10000TL-HU-US {208V} | Y | Y | Y | Y | Y | Y | Y* | N | 10 kW, 208Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.767 | 208 | 97 | Intertek | [3/8/2024] | Intertek | [3/8/2024] | [Skaa-00] | 2024-05-21 | [3/8/2024] | 2024-05-21 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 71.72 |  |  | 165 | 370 | 450 | 0.9767 | 1.9534 | 2.9301 | 4.8835 | 7.3252 | 9.767 | 94.6343 | 95.553 | 95.9068 | 96.6465 | 96.199 | 95.45 | 96.1256 | 96.8912 | 97.4223 | 97.7861 | 97.6411 | 97.3935 | 97.2927 | 97.4689 | 95.6167 | 96.5583 | 97.6099 | 97.2567 | 96.061 | 95.8447 | 96.4942 | 2024-05-21 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 10000TL-HU-US(B) {208V} | Y | Y | Y | Y | Y | Y | Y* | N | 10 kW, 208 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 9.767 | 208 | 96.5 | Intertek | [8/26/2024] | Intertek | [8/26/2024] | [Skaa-00] | 2024-12-23 | [8/26/2024] | 2024-12-23 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 71.72 |  |  | 165 | 370 | 450 | 0.9767 | 1.9534 | 2.9301 | 4.8835 | 7.3252 | 9.767 | 94.6343 | 95.553 | 95.9068 | 96.6465 | 96.199 | 95.45 | 96.1256 | 96.8912 | 97.4223 | 97.7861 | 97.6411 | 97.3935 | 97.2927 | 97.4689 | 95.6167 | 96.5583 | 97.6099 | 97.2567 | 96.061 | 95.8447 | 96.4942 | 2024-12-23 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 11400TL-XH2 US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 9.83 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 9.827 | 208 | 96 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.12 |  |  | 150 | 345 | 500 | 0.983 | 1.965 | 2.948 | 4.914 | 7.371 | 9.827 | 92.75 | 94.53 | 95.11 | 95.21 | 94.79 | 94.19 | 94.79 | 95.4 | 96.64 | 96.95 | 96.91 | 96.57 | 96.12 | 96.62 | 93.16 | 95.44 | 96.01 | 96.2 | 96.01 | 95.63 | 95.89 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | SPH 10000TL-HU-US {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 10 kW, 240Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.925 | 240 | 96 | Intertek | [3/8/2024] | Intertek | [3/8/2024] | [Skaa-00] | 2024-05-21 | [3/8/2024] | 2024-05-21 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 77.25 |  |  | 165 | 370 | 450 | 0.9925 | 1.985 | 2.9775 | 4.9625 | 7.4438 | 9.925 | 92.1758 | 95.1599 | 95.5659 | 95.379 | 94.481 | 94.14 | 94.7244 | 96.9763 | 97.4188 | 97.8105 | 97.5927 | 97.2795 | 97.203 | 97.4 | 95.6685 | 96.3912 | 97.5705 | 97.0698 | 96.0899 | 95.9206 | 96.4631 | 2024-05-21 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | SPH 10000TL-HU-US(B) {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 10 kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 9.925 | 240 | 96 | Intertek | [8/26/2024] | Intertek | [8/26/2024] | [Skaa-00] | 2024-12-23 | [8/26/2024] | 2024-12-23 | Intertek | 2025-07-01 | No Information Submitted |  | N | N | 77.25 |  |  | 165 | 370 | 450 | 0.9925 | 1.985 | 2.9775 | 4.9625 | 7.4438 | 9.925 | 92.1758 | 95.1599 | 95.5659 | 95.379 | 94.481 | 94.14 | 94.7244 | 96.9763 | 97.4188 | 97.8105 | 97.5927 | 97.2795 | 97.203 | 97.4 | 95.6685 | 96.3912 | 97.5705 | 97.0698 | 96.0899 | 95.9206 | 96.4631 | 2024-12-23 | 2025-08-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 11400TL-XH-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 10.04 | 208 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.004 | 2.008 | 3.0119 | 5.0199 | 7.5298 | 10.0398 | 95.0284 | 96.5616 | 97.0154 | 97.1814 | 96.9023 | 96.8567 | 96.8802 | 95.703 | 97.5294 | 97.8587 | 97.8733 | 97.7607 | 97.7179 | 97.7001 | 95.102 | 97.007 | 97.5024 | 97.6871 | 97.6273 | 97.6013 | 97.4916 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | MIN 10000TL-XH2 US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10.0 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 10.057 | 240 | 96 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.53 |  |  | 150 | 345 | 500 | 1.006 | 2.011 | 3.017 | 5.028 | 7.543 | 10.057 | 92.34 | 94.23 | 94.98 | 95.27 | 95.01 | 94.61 | 94.9 | 95.92 | 97.15 | 97.46 | 97.53 | 97.29 | 97.04 | 97.29 | 93.38 | 95.77 | 96.41 | 96.71 | 96.64 | 96.4 | 96.44 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | MIN 10000TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 10.082 | 240 | 97.5 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.0082 | 2.0164 | 3.0246 | 5.041 | 7.5615 | 10.082 | 95.1276 | 96.4976 | 97.0675 | 97.3296 | 97.1985 | 96.9229 | 97.0787 | 96.3253 | 97.7618 | 98.1384 | 98.2919 | 98.1462 | 97.9316 | 98.0731 | 95.0134 | 97.1984 | 97.7803 | 98.0517 | 98.0092 | 97.8719 | 97.8234 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | MIN 11400TL-XH2 US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 9.83 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 11.354 | 240 | 96.5 | Intertek | [1/9/2026] | Intertek | [1/9/2026] | UF1.0 | 2026-03-23 | [12/26/2025] | 2026-03-11 | Intertek | 2025-12-15 |  |  | N | N | 12.53 |  |  | 150 | 345 | 500 | 1.135 | 2.271 | 3.406 | 5.677 | 8.516 | 11.354 | 93.14 | 94.89 | 95.47 | 95.55 | 95.13 | 94.56 | 95.14 | 96.25 | 97.26 | 97.52 | 97.43 | 97.18 | 96.86 | 97.22 | 93.94 | 96.02 | 96.6 | 96.76 | 96.57 | 96.22 | 96.46 | 2026-03-23 |  | N | N | N | N | N | N | N | N | Y
Shenzhen Growatt New Energy Co., Ltd. | MIN 11400TL-XH-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 11.52 | 240 | 98 | Intertek | [11/30/2022] | Intertek | [03/17/2021] | [UE1.0] | 2021-03-22 | [03/17/2021] | 2021-03-22 | Intertek | 2020-11-09 | 2021-03-22 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.152 | 2.304 | 3.456 | 5.76 | 8.64 | 11.52 | 95.3626 | 96.9572 | 97.4775 | 97.685 | 97.5433 | 97.3539 | 97.4392 | 96.5819 | 98.0275 | 98.3999 | 98.5274 | 98.4351 | 98.2539 | 98.3467 | 95.457 | 97.1914 | 97.7448 | 97.9708 | 97.8318 | 97.6582 | 97.7149 | 2021-03-22 | 2023-03-13
Shenzhen Growatt New Energy Co., Ltd. | WIT 28K-H-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 28 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 27.8239 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.6 |  |  | 340 | 445 | 550 | 2.7824 | 5.5648 | 8.3472 | 13.912 | 20.8679 | 27.8239 | 89.3535 | 92.9799 | 93.5425 | 93.7804 | 94.1758 | 94.1687 | 93.7638 | 86.3526 | 91.6348 | 93.2996 | 94.6671 | 95.226 | 95.6842 | 94.3659 | 89.5969 | 93.4201 | 94.3331 | 94.4212 | 94.5744 | 94.4525 | 94.2504 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 28K-HU-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 28 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 27.8239 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.6 |  |  | 340 | 445 | 550 | 2.7824 | 5.5648 | 8.3472 | 13.912 | 20.8679 | 27.8239 | 89.3535 | 92.9799 | 93.5425 | 93.7804 | 94.1758 | 94.1687 | 93.7638 | 86.3526 | 91.6348 | 93.2996 | 94.6671 | 95.226 | 95.6842 | 94.3659 | 89.5969 | 93.4201 | 94.3331 | 94.4212 | 94.5744 | 94.4525 | 94.2504 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 28K-A-US L2 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 28 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 27.8794 | 208 | 97 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.84 |  |  | 380 | 512 | 650 | 2.7879 | 5.5759 | 8.3638 | 13.9397 | 20.9095 | 27.8794 | 96.5073 | 97.3428 | 98.0569 | 97.837 | 97.4748 | 97.1207 | 97.5577 | 96.2295 | 96.9691 | 97.3266 | 97.4154 | 97.314 | 96.8732 | 97.2541 | 95.1438 | 96.5477 | 97.0132 | 97.0605 | 96.8748 | 96.652 | 96.8337 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 28K-AU-US L2 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 28 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 27.8794 | 208 | 97 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.84 |  |  | 380 | 512 | 650 | 2.7879 | 5.5759 | 8.3638 | 13.9397 | 20.9095 | 27.8794 | 96.5073 | 97.3428 | 98.0569 | 97.837 | 97.4748 | 97.1207 | 97.5577 | 96.2295 | 96.9691 | 97.3266 | 97.4154 | 97.314 | 96.8732 | 97.2541 | 95.1438 | 96.5477 | 97.0132 | 97.0605 | 96.8748 | 96.652 | 96.8337 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 35K-H-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 35 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 34.8249 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.8 |  |  | 340 | 445 | 550 | 3.4825 | 6.965 | 10.4475 | 17.4124 | 26.1187 | 34.8249 | 90.1793 | 92.1362 | 92.9634 | 93.9766 | 94.1926 | 94.0402 | 93.7288 | 89.55 | 92.7943 | 93.9785 | 94.8535 | 95.0543 | 95.0025 | 94.5473 | 89.8865 | 92.2004 | 92.8939 | 93.9755 | 94.2824 | 94.2525 | 93.7699 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 35K-HU-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 35 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 34.8249 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.8 |  |  | 340 | 445 | 550 | 3.4825 | 6.965 | 10.4475 | 17.4124 | 26.1187 | 34.8249 | 90.1793 | 92.1362 | 92.9634 | 93.9766 | 94.1926 | 94.0402 | 93.7288 | 89.55 | 92.7943 | 93.9785 | 94.8535 | 95.0543 | 95.0025 | 94.5473 | 89.8865 | 92.2004 | 92.8939 | 93.9755 | 94.2824 | 94.2525 | 93.7699 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 35K-A-US L2 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 35 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 34.8547 | 208 | 97 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.95 |  |  | 380 | 512 | 650 | 3.4855 | 6.9709 | 10.4564 | 17.4273 | 26.141 | 34.8547 | 96.9391 | 97.5394 | 97.5878 | 97.3985 | 97.1423 | 96.8311 | 97.2457 | 96.1133 | 97.1182 | 97.2448 | 97.0788 | 96.8703 | 96.6022 | 96.9277 | 95.035 | 96.6591 | 96.8569 | 96.8715 | 96.6894 | 96.4018 | 96.6657 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 35K-AU-US L2 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 35 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 34.8547 | 208 | 97 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.95 |  |  | 380 | 512 | 650 | 3.4855 | 6.9709 | 10.4564 | 17.4273 | 26.141 | 34.8547 | 96.9391 | 97.5394 | 97.5878 | 97.3985 | 97.1423 | 96.8311 | 97.2457 | 96.1133 | 97.1182 | 97.2448 | 97.0788 | 96.8703 | 96.6022 | 96.9277 | 95.035 | 96.6591 | 96.8569 | 96.8715 | 96.6894 | 96.4018 | 96.6657 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 40K-A-US L2 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 40 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 39.8373 | 208 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.72 |  |  | 380 | 512 | 650 | 3.9837 | 7.9675 | 11.9512 | 19.9187 | 29.878 | 39.8373 | 96.9585 | 97.4559 | 97.4483 | 97.2232 | 96.9022 | 96.5823 | 97.0491 | 95.5282 | 96.668 | 96.8924 | 96.8437 | 96.5911 | 96.2909 | 96.6266 | 94.883 | 96.4617 | 96.7081 | 96.7307 | 96.3985 | 96.0889 | 96.4325 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 40K-AU-US L2 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 40 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 39.8373 | 208 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.72 |  |  | 380 | 512 | 650 | 3.9837 | 7.9675 | 11.9512 | 19.9187 | 29.878 | 39.8373 | 96.9585 | 97.4559 | 97.4483 | 97.2232 | 96.9022 | 96.5823 | 97.0491 | 95.5282 | 96.668 | 96.8924 | 96.8437 | 96.5911 | 96.2909 | 96.6266 | 94.883 | 96.4617 | 96.7081 | 96.7307 | 96.3985 | 96.0889 | 96.4325 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 40K-H-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 40 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 39.9153 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.86 |  |  | 340 | 445 | 550 | 3.9915 | 7.9831 | 11.9746 | 19.9577 | 29.9365 | 39.9153 | 88.6409 | 91.9185 | 93.0057 | 93.731 | 93.8832 | 93.745 | 93.4311 | 90.4709 | 93.2534 | 94.2632 | 94.9549 | 95.0333 | 94.9341 | 94.648 | 87.8965 | 91.953 | 93.0647 | 93.8311 | 93.9925 | 93.8533 | 93.4945 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 40K-HU-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 40 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 39.9153 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.86 |  |  | 340 | 445 | 550 | 3.9915 | 7.9831 | 11.9746 | 19.9577 | 29.9365 | 39.9153 | 88.6409 | 91.9185 | 93.0057 | 93.731 | 93.8832 | 93.745 | 93.4311 | 90.4709 | 93.2534 | 94.2632 | 94.9549 | 95.0333 | 94.9341 | 94.648 | 87.8965 | 91.953 | 93.0647 | 93.8311 | 93.9925 | 93.8533 | 93.4945 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 50K-H-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 277 Vac Grid Support Utility Interactive Inverter | 49.2183 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.78 |  |  | 520 | 660 | 800 | 4.9218 | 9.8437 | 14.7655 | 24.6092 | 36.9137 | 49.2183 | 91.024 | 93.4794 | 94.4915 | 95.4508 | 95.8863 | 96.0973 | 95.3232 | 89.7386 | 92.6539 | 93.6591 | 95.4146 | 95.663 | 96.5287 | 95.0262 | 92.5268 | 94.5347 | 95.9508 | 96.8739 | 97.0983 | 97.1578 | 96.6054 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 50K-H-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 49.2183 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.78 |  |  | 520 | 660 | 800 | 4.9218 | 9.8437 | 14.7655 | 24.6092 | 36.9137 | 49.2183 | 91.024 | 93.4794 | 94.4915 | 95.4508 | 95.8863 | 96.0973 | 95.3232 | 89.7386 | 92.6539 | 93.6591 | 95.4146 | 95.663 | 96.5287 | 95.0262 | 92.5268 | 94.5347 | 95.9508 | 96.8739 | 97.0983 | 97.1578 | 96.6054 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 50K-HU-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 277 Vac Grid Support Utility Interactive Inverter | 49.2183 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.78 |  |  | 520 | 660 | 800 | 4.9218 | 9.8437 | 14.7655 | 24.6092 | 36.9137 | 49.2183 | 91.024 | 93.4794 | 94.4915 | 95.4508 | 95.8863 | 96.0973 | 95.3232 | 89.7386 | 92.6539 | 93.6591 | 95.4146 | 95.663 | 96.5287 | 95.0262 | 92.5268 | 94.5347 | 95.9508 | 96.8739 | 97.0983 | 97.1578 | 96.6054 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 50K-HU-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 49.2183 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.78 |  |  | 520 | 660 | 800 | 4.9218 | 9.8437 | 14.7655 | 24.6092 | 36.9137 | 49.2183 | 91.024 | 93.4794 | 94.4915 | 95.4508 | 95.8863 | 96.0973 | 95.3232 | 89.7386 | 92.6539 | 93.6591 | 95.4146 | 95.663 | 96.5287 | 95.0262 | 92.5268 | 94.5347 | 95.9508 | 96.8739 | 97.0983 | 97.1578 | 96.6054 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 50K-A-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 49.7633 | 480 | 99 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.65 |  |  | 750 | 819 | 900 | 4.9763 | 9.9527 | 14.929 | 24.8817 | 37.3225 | 49.7633 | 98.4582 | 98.8 | 99.1 | 99.2 | 98.9 | 98.5 | 98.9443 | 97.92 | 98.5 | 98.8 | 99 | 98.8533 | 98.4 | 98.8001 | 97.7647 | 98.4364 | 98.7168 | 98.92 | 98.7 | 98.3 | 98.6776 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 50K-AU-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 49.7633 | 480 | 99 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.65 |  |  | 750 | 819 | 900 | 4.9763 | 9.9527 | 14.929 | 24.8817 | 37.3225 | 49.7633 | 98.4582 | 98.8 | 99.1 | 99.2 | 98.9 | 98.5 | 98.9443 | 97.92 | 98.5 | 98.8 | 99 | 98.8533 | 98.4 | 98.8001 | 97.7647 | 98.4364 | 98.7168 | 98.92 | 98.7 | 98.3 | 98.6776 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 55K-A-US L2 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 55 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 54.7978 | 208 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.72 |  |  | 380 | 512 | 650 | 5.4798 | 10.9596 | 16.4393 | 27.3989 | 41.0984 | 54.7978 | 96.7086 | 97.1683 | 97.1561 | 96.929 | 96.498 | 96.0077 | 96.6849 | 96.1857 | 96.8397 | 96.896 | 96.7175 | 96.179 | 95.6631 | 96.3857 | 95.7816 | 96.5744 | 96.7253 | 96.4164 | 95.9784 | 95.5109 | 96.1586 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 55K-AU-US L2 {208V} | N | Y | Y | Y | Y | Y | Y* | Y | 55 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 54.7978 | 208 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.72 |  |  | 380 | 512 | 650 | 5.4798 | 10.9596 | 16.4393 | 27.3989 | 41.0984 | 54.7978 | 96.7086 | 97.1683 | 97.1561 | 96.929 | 96.498 | 96.0077 | 96.6849 | 96.1857 | 96.8397 | 96.896 | 96.7175 | 96.179 | 95.6631 | 96.3857 | 95.7816 | 96.5744 | 96.7253 | 96.4164 | 95.9784 | 95.5109 | 96.1586 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 55K-H-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 55 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 54.972 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.87 |  |  | 340 | 445 | 550 | 5.4972 | 10.9944 | 16.4916 | 27.486 | 41.229 | 54.972 | 90.4576 | 92.7793 | 93.5202 | 93.8925 | 93.7285 | 93.3291 | 93.5397 | 92.1892 | 94.1012 | 94.8002 | 95.0847 | 94.9182 | 94.5949 | 94.7728 | 90.3443 | 92.8849 | 93.5981 | 93.9775 | 93.8679 | 93.5563 | 93.6528 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 55K-HU-US L2 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 55 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 54.972 | 208 | 94 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 16.87 |  |  | 340 | 445 | 550 | 5.4972 | 10.9944 | 16.4916 | 27.486 | 41.229 | 54.972 | 90.4576 | 92.7793 | 93.5202 | 93.8925 | 93.7285 | 93.3291 | 93.5397 | 92.1892 | 94.1012 | 94.8002 | 95.0847 | 94.9182 | 94.5949 | 94.7728 | 90.3443 | 92.8849 | 93.5981 | 93.9775 | 93.8679 | 93.5563 | 93.6528 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 63K-H-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 63 kW, 277 Vac Grid Support Utility Interactive Inverter | 62.5698 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.66 |  |  | 520 | 660 | 800 | 6.257 | 12.514 | 18.7709 | 31.2849 | 46.9274 | 62.5698 | 92.7451 | 94.0137 | 94.892 | 95.6379 | 96.0413 | 96.1506 | 95.5909 | 90.7529 | 93.1172 | 94.3637 | 96.0455 | 96.3439 | 96.7951 | 95.6812 | 96.0987 | 96.9077 | 97.1195 | 97.2451 | 97.1695 | 96.8696 | 97.1085 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 63K-H-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 63 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 62.5698 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.66 |  |  | 520 | 660 | 800 | 6.257 | 12.514 | 18.7709 | 31.2849 | 46.9274 | 62.5698 | 92.7451 | 94.0137 | 94.892 | 95.6379 | 96.0413 | 96.1506 | 95.5909 | 90.7529 | 93.1172 | 94.3637 | 96.0455 | 96.3439 | 96.7951 | 95.6812 | 96.0987 | 96.9077 | 97.1195 | 97.2451 | 97.1695 | 96.8696 | 97.1085 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 63K-HU-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 63 kW, 277 Vac Grid Support Utility Interactive Inverter | 62.5698 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.66 |  |  | 520 | 660 | 800 | 6.257 | 12.514 | 18.7709 | 31.2849 | 46.9274 | 62.5698 | 92.7451 | 94.0137 | 94.892 | 95.6379 | 96.0413 | 96.1506 | 95.5909 | 90.7529 | 93.1172 | 94.3637 | 96.0455 | 96.3439 | 96.7951 | 95.6812 | 96.0987 | 96.9077 | 97.1195 | 97.2451 | 97.1695 | 96.8696 | 97.1085 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 63K-HU-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 63 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 62.5698 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.66 |  |  | 520 | 660 | 800 | 6.257 | 12.514 | 18.7709 | 31.2849 | 46.9274 | 62.5698 | 92.7451 | 94.0137 | 94.892 | 95.6379 | 96.0413 | 96.1506 | 95.5909 | 90.7529 | 93.1172 | 94.3637 | 96.0455 | 96.3439 | 96.7951 | 95.6812 | 96.0987 | 96.9077 | 97.1195 | 97.2451 | 97.1695 | 96.8696 | 97.1085 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 63K-A-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 63 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 63.4281 | 480 | 97.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 18.95 |  |  | 750 | 819 | 900 | 6.3428 | 12.6856 | 19.0284 | 31.7141 | 47.5711 | 63.4281 | 95.938 | 97.3572 | 97.8325 | 98.0717 | 98.0278 | 97.7163 | 97.8809 | 95.2745 | 96.9623 | 97.5341 | 97.8513 | 97.8026 | 97.5857 | 97.6266 | 95.0797 | 96.8345 | 97.4862 | 97.7125 | 97.6872 | 97.4101 | 97.5076 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 63K-AU-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 63 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 63.4281 | 480 | 97.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 18.95 |  |  | 750 | 819 | 900 | 6.3428 | 12.6856 | 19.0284 | 31.7141 | 47.5711 | 63.4281 | 95.938 | 97.3572 | 97.8325 | 98.0717 | 98.0278 | 97.7163 | 97.8809 | 95.2745 | 96.9623 | 97.5341 | 97.8513 | 97.8026 | 97.5857 | 97.6266 | 95.0797 | 96.8345 | 97.4862 | 97.7125 | 97.6872 | 97.4101 | 97.5076 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 75K-A-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 74.5274 | 480 | 98.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.71 |  |  | 750 | 819 | 900 | 7.4527 | 14.9055 | 22.3582 | 37.2637 | 55.8956 | 74.5274 | 98.5616 | 98.7298 | 98.6603 | 98.4865 | 98.19 | 98.1145 | 98.3468 | 98.5359 | 98.7669 | 98.6798 | 98.4761 | 98.1846 | 98.0941 | 98.3439 | 98.4294 | 98.6378 | 98.5385 | 98.3629 | 98.0911 | 98.0295 | 98.2397 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 75K-AU-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 74.5274 | 480 | 98.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.71 |  |  | 750 | 819 | 900 | 7.4527 | 14.9055 | 22.3582 | 37.2637 | 55.8956 | 74.5274 | 98.5616 | 98.7298 | 98.6603 | 98.4865 | 98.19 | 98.1145 | 98.3468 | 98.5359 | 98.7669 | 98.6798 | 98.4761 | 98.1846 | 98.0941 | 98.3439 | 98.4294 | 98.6378 | 98.5385 | 98.3629 | 98.0911 | 98.0295 | 98.2397 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 75K-H-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 277 Vac Grid Support Utility Interactive Inverter | 74.5887 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.39 |  |  | 520 | 660 | 800 | 7.4589 | 14.9177 | 22.3766 | 37.2944 | 55.9415 | 74.5887 | 92.7584 | 94.4451 | 95.2606 | 95.9213 | 96.2493 | 96.4023 | 95.8396 | 91.7788 | 93.5602 | 94.9048 | 96.3781 | 96.6739 | 96.7728 | 96.053 | 93.9304 | 95.5069 | 96.3065 | 96.9396 | 97.0081 | 97.0747 | 96.7147 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 75K-H-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 74.5887 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.39 |  |  | 520 | 660 | 800 | 7.4589 | 14.9177 | 22.3766 | 37.2944 | 55.9415 | 74.5887 | 92.7584 | 94.4451 | 95.2606 | 95.9213 | 96.2493 | 96.4023 | 95.8396 | 91.7788 | 93.5602 | 94.9048 | 96.3781 | 96.6739 | 96.7728 | 96.053 | 93.9304 | 95.5069 | 96.3065 | 96.9396 | 97.0081 | 97.0747 | 96.7147 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 75K-HU-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 277 Vac Grid Support Utility Interactive Inverter | 74.5887 | 277 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.39 |  |  | 520 | 660 | 800 | 7.4589 | 14.9177 | 22.3766 | 37.2944 | 55.9415 | 74.5887 | 92.7584 | 94.4451 | 95.2606 | 95.9213 | 96.2493 | 96.4023 | 95.8396 | 91.7788 | 93.5602 | 94.9048 | 96.3781 | 96.6739 | 96.7728 | 96.053 | 93.9304 | 95.5069 | 96.3065 | 96.9396 | 97.0081 | 97.0747 | 96.7147 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 75K-HU-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 75 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 74.5887 | 480 | 96 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.39 |  |  | 520 | 660 | 800 | 7.4589 | 14.9177 | 22.3766 | 37.2944 | 55.9415 | 74.5887 | 92.7584 | 94.4451 | 95.2606 | 95.9213 | 96.2493 | 96.4023 | 95.8396 | 91.7788 | 93.5602 | 94.9048 | 96.3781 | 96.6739 | 96.7728 | 96.053 | 93.9304 | 95.5069 | 96.3065 | 96.9396 | 97.0081 | 97.0747 | 96.7147 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 100K-H-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 277 Vac Grid Support Utility Interactive Inverter | 99.3703 | 277 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.36 |  |  | 520 | 660 | 800 | 9.937 | 19.8741 | 29.8111 | 49.6852 | 74.5277 | 99.3703 | 93.283 | 94.9912 | 95.423 | 95.9323 | 96.2295 | 96.1392 | 95.886 | 93.0324 | 94.3918 | 95.4827 | 96.4392 | 96.6953 | 96.5074 | 96.2249 | 94.6296 | 96.1332 | 96.7387 | 97.0403 | 97.0238 | 96.9629 | 96.8497 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 100K-H-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 99.3703 | 480 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.36 |  |  | 520 | 660 | 800 | 9.937 | 19.8741 | 29.8111 | 49.6852 | 74.5277 | 99.3703 | 93.283 | 94.9912 | 95.423 | 95.9323 | 96.2295 | 96.1392 | 95.886 | 93.0324 | 94.3918 | 95.4827 | 96.4392 | 96.6953 | 96.5074 | 96.2249 | 94.6296 | 96.1332 | 96.7387 | 97.0403 | 97.0238 | 96.9629 | 96.8497 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 100K-HU-US {277V} | Y | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 277 Vac Grid Support Utility Interactive Inverter | 99.3703 | 277 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.36 |  |  | 520 | 660 | 800 | 9.937 | 19.8741 | 29.8111 | 49.6852 | 74.5277 | 99.3703 | 93.283 | 94.9912 | 95.423 | 95.9323 | 96.2295 | 96.1392 | 95.886 | 93.0324 | 94.3918 | 95.4827 | 96.4392 | 96.6953 | 96.5074 | 96.2249 | 94.6296 | 96.1332 | 96.7387 | 97.0403 | 97.0238 | 96.9629 | 96.8497 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 100K-HU-US {480V} | Y | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality | 99.3703 | 480 | 96.5 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-05-27 | 2024-06-21 |  | N | N | 18.36 |  |  | 520 | 660 | 800 | 9.937 | 19.8741 | 29.8111 | 49.6852 | 74.5277 | 99.3703 | 93.283 | 94.9912 | 95.423 | 95.9323 | 96.2295 | 96.1392 | 95.886 | 93.0324 | 94.3918 | 95.4827 | 96.4392 | 96.6953 | 96.5074 | 96.2249 | 94.6296 | 96.1332 | 96.7387 | 97.0403 | 97.0238 | 96.9629 | 96.8497 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 100K-A-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 99.3887 | 480 | 98 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.5 |  |  | 750 | 819 | 900 | 9.9389 | 19.8777 | 29.8166 | 49.6944 | 74.5415 | 99.3887 | 98.4108 | 98.6379 | 98.5852 | 98.3559 | 98.227 | 97.876 | 98.3074 | 98.1368 | 98.3086 | 98.3256 | 98.1409 | 98.1516 | 97.8076 | 98.1603 | 98.0473 | 98.172 | 98.2217 | 98.0593 | 97.9062 | 97.5713 | 97.9784 | 2024-06-21
Shenzhen Growatt New Energy Co., Ltd. | WIT 100K-AU-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 100 kW, 480 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 99.3887 | 480 | 98 | Intertek | [11/27/2023] | Intertek | [11/27/2023] | [TO1.0] | 2024-06-21 | [11/27/2023] | 2024-06-21 | Intertek | 2024-04-18 | 2024-06-21 |  | N | N | 19.5 |  |  | 750 | 819 | 900 | 9.9389 | 19.8777 | 29.8166 | 49.6944 | 74.5415 | 99.3887 | 98.4108 | 98.6379 | 98.5852 | 98.3559 | 98.227 | 97.876 | 98.3074 | 98.1368 | 98.3086 | 98.3256 | 98.1409 | 98.1516 | 97.8076 | 98.1603 | 98.0473 | 98.172 | 98.2217 | 98.0593 | 97.9062 | 97.5713 | 97.9784 | 2024-06-21
Shenzhen GSL Energy Co., Ltd. | HS-LV8KNA {208V} | Y | Y | N | N | N | N | N |  | 8.8 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 8.8085 | 208 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.88085 | 1.7617 | 2.6426 | 4.4043 | 6.6064 | 8.8085 | 94.444 | 95.624 | 96.816 | 96.49 | 97.126 | 95.666 | 96.6999 | 94.382 | 95.75 | 96.022 | 96.526 | 97.2 | 95.958 | 96.6698 | 93.96 | 94.784 | 96.388 | 96.654 | 96.84 | 95.102 | 96.4418 | 2025-11-21
Shenzhen GSL Energy Co., Ltd. | HS-LV8KNA {240V} | Y | Y | N | N | N | N | N |  | 8.8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 8.81 | 240 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.88096 | 1.7619 | 2.6429 | 4.4048 | 6.6072 | 8.8096 | 94.272 | 95.424 | 96.778 | 96.326 | 97.096 | 95.646 | 96.6271 | 93.65 | 95.692 | 96.638 | 96.466 | 97.23 | 96.198 | 96.7268 | 94.002 | 95.676 | 96.698 | 96.354 | 96.548 | 95.556 | 96.3302 | 2025-11-21
Shenzhen GSL Energy Co., Ltd. | HS-LV10KNA {208V} | Y | Y | N | N | N | N | N |  | 10 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.0057 | 208 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 72.5 |  |  | 275 | 362.5 | 450 | 1.0006 | 2.0011 | 3.0017 | 5.0028 | 7.5043 | 10.0057 | 93.636 | 96.268 | 96.57 | 96.558 | 97.164 | 94.944 | 96.6685 | 94.79 | 96.362 | 96.58 | 96.79 | 97.524 | 95.16 | 96.9709 | 93.936 | 96.22 | 96.374 | 96.486 | 96.948 | 95.296 | 96.5426 | 2025-11-21
Shenzhen GSL Energy Co., Ltd. | HS-LV10KNA {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 10.0082 | 240 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 73.6 |  |  | 275 | 362.5 | 450 | 1.0008 | 2.0016 | 3.0025 | 5.0041 | 7.5061 | 10.0082 | 92.884 | 96.19 | 96.28 | 96.506 | 97.094 | 94.834 | 96.5462 | 93.182 | 96.368 | 96.912 | 96.706 | 97.522 | 95.052 | 96.9226 | 93.246 | 96.288 | 96.896 | 97.016 | 96.938 | 95.276 | 96.6861 | 2025-11-21
Shenzhen GSL Energy Co., Ltd. | HS-LV12KNA {208V} | Y | Y | N | N | N | N | N |  | 12 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.3972 | 208 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.0397 | 2.0794 | 3.1192 | 5.1986 | 7.7979 | 10.3972 | 95.11 | 95.714 | 96.534 | 96.55 | 96.714 | 95.27 | 96.4716 | 95.33 | 96.102 | 96.616 | 96.924 | 97.478 | 95.264 | 96.9928 | 95.036 | 95.774 | 96.604 | 96.55 | 96.668 | 95.186 | 96.4515 | 2025-11-21
Shenzhen GSL Energy Co., Ltd. | GSL-H-12KLV-US {208V} | Y | Y | N | N | N | N | N | Y | 10.4 kW, 208 Vac Grid support Utility Interactive Hybrid Inverter | 10.499 | 208 | 96.5 | Intertek | [9/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2022-12-12 |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.0499 | 2.0999 | 3.1498 | 5.2497 | 7.8745 | 10.4994 | 93.4773 | 95.2677 | 95.9298 | 95.8461 | 95.6083 | 95.2856 | 95.5784 | 95.0713 | 96.6555 | 97.0252 | 97.3102 | 97.0957 | 96.4058 | 96.9948 | 94.2867 | 96.7139 | 97.1633 | 96.953 | 96.7744 | 96.4653 | 96.7406 | 2022-12-12
Shenzhen GSL Energy Co., Ltd. | GSL-H-12KLV-US {240V} | Y | Y | N | N | N | N | N | Y | 12 kW, 240 Vac Grid support Utility Interactive Hybrid Inverter | 11.933 | 240 | 97 | Intertek | [9/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2022-12-12 |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.1933 | 2.3865 | 3.5798 | 5.9663 | 8.9494 | 11.9326 | 95.0246 | 96.0981 | 96.5396 | 96.4958 | 96.126 | 95.9005 | 96.1965 | 96.5925 | 97.1942 | 97.5102 | 97.3417 | 97.2365 | 97.1037 | 97.2569 | 95.8173 | 97.0077 | 97.4221 | 97.2641 | 97.1385 | 97.0353 | 97.1344 | 2022-12-12
Shenzhen GSL Energy Co., Ltd. | HS-LV12KNA {240V} | Y | Y | N | N | N | N | N |  | 12 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 11.9957 | 240 | 96.5 | Intertek | [5/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.1996 | 2.3991 | 3.5987 | 5.9979 | 8.9968 | 11.9957 | 95.452 | 95.688 | 96.376 | 96.392 | 96.504 | 95.226 | 96.3183 | 95.568 | 96.168 | 96.69 | 96.874 | 97.428 | 95.228 | 96.9757 | 95.526 | 95.868 | 96.596 | 96.456 | 96.536 | 95.324 | 96.392 | 2025-11-21
Shenzhen Kstar New Energy Company Limited | E8KD {240V} | Y | Y | N | N | N | N | N | Y | 8 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.024 | 240 | 97.5 | CSA Group | [5/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-12-11 |  | N | N | 20.79 |  |  | 200 | 300 | 400 | 0.802 | 1.605 | 2.407 | 4.012 | 6.018 | 8.024 | 95.56 | 96.7 | 96.92 | 96.95 | 96.64 | 96.29 | 96.68 | 96.57 | 97.45 | 97.7 | 97.59 | 97.37 | 97.04 | 97.41 | 96.78 | 98.15 | 98.24 | 98.08 | 97.84 | 97.49 | 97.89 | 2024-12-11
Shenzhen Kstar New Energy Company Limited | E10KD {240V} | Y | Y | N | N | N | N | N | Y | 10 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 10.036 | 240 | 97.5 | CSA Group | [5/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-12-11 |  | N | N | 20.79 |  |  | 240 | 300 | 400 | 1.004 | 2.007 | 3.011 | 5.018 | 7.527 | 10.036 | 96.22 | 97.14 | 97.18 | 97.14 | 96.76 | 96.29 | 96.86 | 97.06 | 97.65 | 97.59 | 97.49 | 97.14 | 96.7 | 97.26 | 97.38 | 98 | 98.08 | 97.89 | 97.59 | 97.18 | 97.7 | 2024-12-11
Shenzhen Kstar New Energy Company Limited | E12KD {240V} | Y | Y | N | N | N | N | N | Y | 12 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 12.02 | 240 | 97 | CSA Group | [5/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-12-11 |  | N | N | 20.79 |  |  | 200 | 300 | 400 | 1.202 | 2.404 | 3.606 | 6.01 | 9.015 | 12.02 | 95.15 | 96.36 | 96.71 | 96.63 | 96.2 | 95.67 | 96.29 | 95.34 | 96.88 | 97.22 | 97.18 | 96.85 | 96.36 | 96.88 | 96.15 | 97.26 | 97.5 | 97.64 | 97.21 | 96.84 | 97.28 | 2024-12-11
Shenzhen Kstar New Energy Company Limited | E15KD {240V} | Y | Y | N | N | N | N | N | Y | 15 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 14.993 | 240 | 97 | CSA Group | [5/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-12-11 |  | N | N | 20.79 |  |  | 240 | 300 | 400 | 1.499 | 2.999 | 4.498 | 7.497 | 11.245 | 14.993 | 96.25 | 97.24 | 97.34 | 96.97 | 96.34 | 95.56 | 96.6 | 96.53 | 97.55 | 97.62 | 97.28 | 96.68 | 95.93 | 96.92 | 97.54 | 98.07 | 98.1 | 97.72 | 97.11 | 96.45 | 97.39 | 2024-12-11
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 8K {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.8599 | 208 | 96.5 | Intertek | [3/12/2024] | Intertek | [3/12/2024] | [EA1.0] | 2024-04-22 | [3/12/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-08-11 |  | N | N | 18.53 |  |  | 210 | 360 | 480 | 0.78599 | 1.572 | 2.358 | 3.93 | 5.895 | 7.8599 | 92.7458 | 94.8821 | 95.7877 | 96.2814 | 95.7548 | 95.5452 | 95.6949 | 95.3183 | 96.7852 | 96.9298 | 97.2401 | 96.7733 | 96.6331 | 96.8255 | 94.866 | 96.387 | 96.7215 | 97.1053 | 96.6941 | 96.6144 | 96.6913 | 2022-08-11 | 2024-08-12
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 8K {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 7.8627 | 240 | 96.5 | Intertek | [3/12/2024] | Intertek | [3/12/2024] | [EA1.0] | 2024-04-22 | [3/12/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-08-11 |  | N | N | 18.84 |  |  | 210 | 360 | 480 | 0.78627 | 1.5725 | 2.3588 | 3.9313 | 5.897 | 7.8627 | 92.9578 | 94.8899 | 95.7481 | 96.2838 | 95.9702 | 95.8604 | 95.8294 | 95.5741 | 96.5787 | 96.6854 | 97.0389 | 96.7425 | 96.7486 | 96.7433 | 94.682 | 96.1785 | 96.6318 | 96.9367 | 96.7571 | 96.7998 | 96.67 | 2022-08-11 | 2024-08-12
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 10K {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.7577 | 208 | 96.5 | Intertek | [3/12/2024] | Intertek | [3/12/2024] | [EA1.0] | 2024-04-22 | [3/12/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-08-11 |  | N | N | 14.8 |  |  | 210 | 360 | 480 | 0.97577 | 1.9515 | 2.9273 | 4.8789 | 7.3183 | 9.7577 | 92.7092 | 94.8879 | 95.3456 | 95.9721 | 95.5079 | 95.3565 | 95.4354 | 96.1203 | 96.8726 | 97.0518 | 97.3038 | 96.7285 | 96.5437 | 96.8618 | 95.0454 | 96.5267 | 96.8926 | 97.167 | 96.5064 | 96.4285 | 96.6301 | 2022-08-11 | 2024-08-12
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 10K {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.7586 | 240 | 96.5 | Intertek | [3/12/2024] | Intertek | [3/12/2024] | [EA1.0] | 2024-04-22 | [3/12/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-08-11 |  | N | N | 14.3 |  |  | 210 | 360 | 480 | 0.97586 | 1.9517 | 2.9276 | 4.8793 | 7.3189 | 9.7586 | 93.035 | 95.0464 | 95.7433 | 96.0352 | 95.4309 | 95.34 | 95.4757 | 95.1061 | 96.6509 | 97.0749 | 97.2195 | 96.6243 | 96.5263 | 96.7391 | 94.2113 | 96.1002 | 96.6822 | 96.9911 | 96.5706 | 96.5369 | 96.5527 | 2022-08-11 | 2024-08-12
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 12K {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 10.499 | 208 | 96.5 | Intertek | [3/13/2024] | Intertek | [3/13/2024] | [fA1.0] | 2024-04-22 | [3/13/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-10-03 |  | N | N | 14.5 |  |  | 230 | 360 | 480 | 1.0499 | 2.0999 | 3.1498 | 5.2497 | 7.8745 | 10.4994 | 93.4773 | 95.2677 | 95.9298 | 95.8461 | 95.6083 | 95.2856 | 95.5784 | 95.0713 | 96.6555 | 97.0252 | 97.3102 | 97.0957 | 96.4058 | 96.9948 | 94.2867 | 96.7139 | 97.1633 | 96.953 | 96.7744 | 96.4653 | 96.7406 | 2022-10-03 | 2024-04-22
Shenzhen Lux Power Technology Co., Ltd. | GEN-LB-US 13K {208V} | Y | Y | Y | Y | Y | Y | Y* | N | 13 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.325 | 208 | 97 | Intertek | [6/23/2025] | Intertek | [6/23/2025] | [fA1.0] | 2025-08-01 | [6/16/2025] | 2025-08-01 | Intertek | 2025-04-14 | No Information Submitted |  | N | N | 31.95 |  |  | 250 | 360 | 440 | 1.133 | 2.265 | 3.398 | 5.663 | 8.494 | 11.325 | 96.29 | 96.28 | 96.21 | 96.25 | 96.23 | 96.33 | 96.24 | 96.07 | 96.94 | 97.19 | 97.71 | 97.5 | 96.64 | 97.38 | 95.73 | 97.68 | 97.82 | 98 | 97.11 | 97.31 | 97.36 | 2025-08-01
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 13K {208V} | Y | Y | Y | Y | Y | Y | N | N | 16 kW, 208 Vac Grid support Hybrid Inverter with PCS functionality. | 11.325 | 208 | 97 | Intertek | [1/22/2025] | Intertek | [1/22/2025] | [fA1.0] | 2025-05-01 | [1/22/2025] | 2025-05-01 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 31.95 |  |  | 250 | 360 | 440 | 1.1325 | 2.265 | 3.3975 | 5.6625 | 8.4937 | 11.325 | 96.2893 | 96.2849 | 96.2071 | 96.2512 | 96.2259 | 96.3252 | 96.2394 | 96.0747 | 96.9361 | 97.1869 | 97.7129 | 97.4996 | 96.6438 | 97.3789 | 95.7303 | 97.6771 | 97.8156 | 97.9986 | 97.1094 | 97.3148 | 97.3644 | 2025-05-01
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 12K {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 11.933 | 240 | 97 | Intertek | [3/13/2024] | Intertek | [3/13/2024] | [fA1.0] | 2024-04-22 | [3/13/2024] | 2024-04-22 | Intertek | 2022-05-27 | 2022-10-03 |  | N | N | 14.29 |  |  | 230 | 360 | 480 | 1.1933 | 2.3865 | 3.5798 | 5.9663 | 8.9494 | 11.9326 | 95.0246 | 96.0981 | 96.5396 | 96.4958 | 96.126 | 95.9005 | 96.1965 | 96.5925 | 97.1942 | 97.5102 | 97.3417 | 97.2365 | 97.1037 | 97.2569 | 95.8173 | 97.0077 | 97.4221 | 97.2641 | 97.1385 | 97.0353 | 97.1344 | 2022-10-03 | 2024-04-22
Shenzhen Lux Power Technology Co., Ltd. | GEN-LB-US 13K {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 13 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.997 | 240 | 96.5 | Intertek | [6/23/2025] | Intertek | [6/23/2025] | [fA1.0] | 2025-08-01 | [6/16/2025] | 2025-08-01 | Intertek | 2025-04-14 | No Information Submitted |  | N | N | 29.57 |  |  | 250 | 360 | 440 | 1.3 | 2.599 | 3.899 | 6.499 | 9.748 | 12.997 | 95.84 | 96.15 | 95.67 | 96.57 | 96.39 | 96.14 | 96.3 | 96.62 | 97.05 | 97.3 | 98.11 | 96.99 | 96.68 | 97.24 | 96.24 | 96.52 | 96.56 | 96.51 | 96.26 | 96.12 | 96.35 | 2025-08-01
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 13K {240V} | Y | Y | Y | Y | Y | Y | N | N | 16 kW, 240 Vac Grid support Hybrid Inverter with PCS functionality. | 12.9973 | 240 | 96.5 | Intertek | [1/22/2025] | Intertek | [1/22/2025] | [fA1.0] | 2025-05-01 | [1/22/2025] | 2025-05-01 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 29.57 |  |  | 250 | 360 | 440 | 1.2997 | 2.5995 | 3.8992 | 6.4986 | 9.748 | 12.9973 | 95.8394 | 96.1488 | 95.6701 | 96.568 | 96.3915 | 96.1373 | 96.2951 | 96.6194 | 97.0472 | 97.3014 | 98.1054 | 96.9933 | 96.6758 | 97.2357 | 96.2395 | 96.5234 | 96.5619 | 96.5053 | 96.2597 | 96.1215 | 96.353 | 2025-05-01
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 16K {208V} | Y | Y | Y | Y | Y | Y | N | N | 13.8 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 13.8987 | 208 | 96.5 | Intertek | [10/11/24] | Intertek | [1/22/2025] | [fA1.0] | 2025-02-03 | [1/22/2025] | 2025-02-03 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.3899 | 2.7797 | 4.1696 | 6.9494 | 10.424 | 13.8987 | 95.2216 | 96.3623 | 96.3314 | 96.3567 | 96.0039 | 95.9864 | 96.103 | 95.5416 | 96.5717 | 96.9718 | 97.1706 | 97.0713 | 96.2488 | 96.9529 | 95.5994 | 96.8339 | 97.3771 | 97.1744 | 97.0907 | 96.9737 | 97.0643 | 2025-02-03
Shenzhen Lux Power Technology Co., Ltd. | GEN-LB-US 16K {208V} | Y | Y | Y | Y | Y | Y | Y* | N | 16 kW, 208 Vac Grid Support Utility Interactive Inverter | 13.899 | 208 | 96.5 | Intertek | [5/23/2025] | Intertek | [5/23/2025] | [fA1.0] | 2025-08-01 | [5/19/2025] | 2025-08-01 | Intertek | 2025-04-14 | No Information Submitted |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.39 | 2.78 | 4.17 | 6.949 | 10.424 | 13.899 | 95.22 | 96.36 | 96.33 | 96.36 | 96 | 95.99 | 96.1 | 95.54 | 96.57 | 96.97 | 97.17 | 97.07 | 96.25 | 96.95 | 95.6 | 96.83 | 97.38 | 97.17 | 97.09 | 96.97 | 97.06 | 2025-08-01
Shenzhen Lux Power Technology Co., Ltd. | GEN-LB-US 16K {240V} | Y | Y | Y | Y | Y | Y | Y* | N | 16 kW, 240 Vac Grid Support Utility Interactive Inverter | 16.153 | 240 | 97 | Intertek | [5/23/2025] | Intertek | [5/23/2025] | [fA1.0] | 2025-08-01 | [5/19/2025] | 2025-08-01 | Intertek | 2025-04-14 | No Information Submitted |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.615 | 3.231 | 4.846 | 8.077 | 12.115 | 16.153 | 95.1 | 96 | 96.39 | 96.4 | 96.73 | 95.86 | 96.48 | 96.47 | 97.1 | 97.48 | 97.12 | 97.08 | 96.94 | 97.1 | 95.46 | 96.91 | 97.25 | 97.17 | 96.99 | 96.82 | 96.99 | 2025-08-01
Shenzhen Lux Power Technology Co., Ltd. | LXP-LB-US 16K {240V} | Y | Y | Y | Y | Y | Y | N | N | 16 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter with PCS functionality. | 16.1532 | 240 | 97 | Intertek | [10/11/24] | Intertek | [1/22/2025] | [fA1.0] | 2025-02-03 | [1/22/2025] | 2025-02-03 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 29.36 |  |  | 250 | 360 | 440 | 1.6153 | 3.2306 | 4.846 | 8.0766 | 12.1149 | 16.1532 | 95.0963 | 95.9965 | 96.3882 | 96.4022 | 96.7311 | 95.8608 | 96.4752 | 96.4687 | 97.0976 | 97.478 | 97.1222 | 97.077 | 96.941 | 97.1045 | 95.4554 | 96.9149 | 97.2473 | 97.1696 | 96.9929 | 96.8158 | 96.9863 | 2025-02-03
Shenzhen Lux Power Technology Co., Ltd. | GEN-HB-US 25K {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 21.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 21.6632 | 208 | 96.5 | Intertek | [10/27/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2025-11-17 |  |  | Y | N | 34.81 |  |  | 190 | 360 | 480 | 2.1663 | 4.3326 | 6.499 | 10.8316 | 16.2474 | 21.6632 | 95.7337 | 96.059 | 96.1625 | 96.1561 | 96.0996 | 95.9915 | 96.0969 | 95.9398 | 96.2286 | 96.3225 | 96.526 | 96.2301 | 96.2494 | 96.2926 | 96.3084 | 96.5349 | 96.6268 | 96.9377 | 96.5422 | 96.4234 | 96.6198 | 2026-06-22 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
Shenzhen Lux Power Technology Co., Ltd. | GEN-HB-US 25K {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 25 kW, 240 Vac Grid Support Utility Interactive Inverter | 25.1291 | 240 | 96.5 | Intertek | [10/27/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2025-11-17 |  |  | Y | N | 28.42 |  |  | 190 | 360 | 480 | 2.5129 | 5.0258 | 7.5387 | 12.5646 | 18.8468 | 25.1291 | 96.0006 | 96.1397 | 96.3289 | 96.5333 | 96.3477 | 96.2381 | 96.3546 | 96.1449 | 96.3247 | 96.5119 | 96.6265 | 96.4352 | 96.3402 | 96.4627 | 96.3032 | 96.6022 | 96.8131 | 97.1518 | 96.5163 | 96.4328 | 96.677 | 2026-06-22 |  | Y | Y | Y | Y | Y | Y | Y | Y | Y
Shenzhen Megarevo Technology Co., Ltd. | R5KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 5.081 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.4332 |  |  | 180 | 360 | 430 | 0.508 | 1.016 | 1.524 | 2.541 | 3.811 | 5.081 | 94.78 | 95.87 | 96.54 | 97.73 | 97.23 | 96.77 | 97.06 | 95.47 | 96.39 | 97.44 | 98.31 | 97.79 | 97.53 | 97.68 | 95.11 | 96.89 | 96.83 | 97.99 | 97.73 | 97.13 | 97.5 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R5KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 5.0897 | 240 | 97 | SGS | [9/15/2023] | SGS | [9/15/2023] | [Ver0306] | No Information Submitted | [9/15/2023] | No Information Submitted | SGS | 2023-07-19 | No Information Submitted |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2023-05-11 | 2024-03-21
Shenzhen Megarevo Technology Co., Ltd. | R6KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 6.082 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.02 |  |  | 180 | 360 | 430 | 0.608 | 1.216 | 1.825 | 3.041 | 4.562 | 6.082 | 94.57 | 95.91 | 96.64 | 97.49 | 96.98 | 96.44 | 96.87 | 95.36 | 96.6 | 97.72 | 98.25 | 97.84 | 97.32 | 97.72 | 94.95 | 96.15 | 97.25 | 97.96 | 97.52 | 97.06 | 97.38 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R6KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 6.117 | 240 | 97 | SGS | [9/15/2023] | SGS | [9/15/2023] | [Ver0306] | No Information Submitted | [9/15/2023] | No Information Submitted | SGS | 2023-07-19 | No Information Submitted |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2023-05-11 | 2024-03-21
Shenzhen Megarevo Technology Co., Ltd. | R7K6H1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 7.765 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.3655 |  |  | 180 | 360 | 430 | 0.776 | 1.553 | 2.329 | 3.882 | 5.823 | 7.765 | 94.67 | 95.75 | 96.57 | 97.46 | 96.99 | 96.45 | 96.85 | 95.25 | 96.32 | 97.47 | 98.31 | 97.88 | 97.29 | 97.71 | 94.9 | 95.96 | 97.14 | 97.88 | 97.37 | 96.89 | 97.26 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R7K6LNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 7.765 | 240 | 97 | SGS | [9/15/2023] | SGS | [9/15/2023] | [Ver0306] | No Information Submitted | [9/15/2023] | No Information Submitted | SGS | 2023-07-19 | No Information Submitted |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2023-05-11 | 2024-03-21
Shenzhen Megarevo Technology Co., Ltd. | R8KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 8.084 | 240 | 97.5 | SGS | [9/15/2023] | SGS | [9/15/2023] | [Ver0306] | No Information Submitted | [9/15/2023] | No Information Submitted | SGS | 2023-07-19 | No Information Submitted |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2023-05-11 | 2024-03-21
Shenzhen Megarevo Technology Co., Ltd. | R8KLNA-P4 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.0 kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 8.111 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 20.205 |  |  | 150 | 360 | 430 | 0.8111 | 1.6222 | 2.4333 | 4.0555 | 6.0832 | 8.111 | 93.7032 | 94.658 | 95.6518 | 96.6831 | 96.5045 | 96.1164 | 96.2159 | 94.1867 | 95.5035 | 96.5637 | 97.5413 | 97.1721 | 96.9438 | 96.9623 | 94.0252 | 95.3961 | 96.1441 | 97.253 | 96.9761 | 96.6831 | 96.7227 | 2024-11-21
Shenzhen Megarevo Technology Co., Ltd. | R8KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 8.116 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.021 |  |  | 200 | 360 | 430 | 0.812 | 1.623 | 2.435 | 4.058 | 6.087 | 8.116 | 94.42 | 95.83 | 96.39 | 97.57 | 97.36 | 96.6 | 97.06 | 95.36 | 96.47 | 97.54 | 98.25 | 97.81 | 97.37 | 97.69 | 94.87 | 96.17 | 97.07 | 97.94 | 97.8 | 97.13 | 97.51 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R8KLNA-P6 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.0 kW, 240Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 8.1809 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 19.254 |  |  | 150 | 360 | 430 | 0.81809 | 1.6362 | 2.4543 | 4.0905 | 6.1357 | 8.1809 | 93.4783 | 94.6843 | 95.5771 | 96.7312 | 96.4419 | 96.1554 | 96.1782 | 94.1318 | 95.3434 | 96.55 | 97.5594 | 97.2213 | 96.7995 | 96.9732 | 93.9303 | 95.1558 | 96.1549 | 97.2766 | 97.0383 | 96.4559 | 96.7348 | 2024-11-21
Shenzhen Megarevo Technology Co., Ltd. | R9KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 9 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 9.103 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.1397 |  |  | 200 | 360 | 430 | 0.91 | 1.821 | 2.731 | 4.551 | 6.827 | 9.103 | 94.43 | 95.76 | 96.56 | 97.5 | 97.03 | 96.53 | 96.88 | 95.28 | 96.44 | 97.43 | 98.28 | 97.77 | 97.3 | 97.65 | 95.14 | 95.94 | 97.15 | 97.85 | 97.48 | 96.99 | 97.32 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R10KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 10 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 10.154 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.0848 |  |  | 250 | 360 | 430 | 1.015 | 2.031 | 3.046 | 5.077 | 7.616 | 10.154 | 94.46 | 95.68 | 96.64 | 97.53 | 96.98 | 96.37 | 96.86 | 95.29 | 96.36 | 97.31 | 98.21 | 97.97 | 97.45 | 97.73 | 94.84 | 95.95 | 96.94 | 97.77 | 97.47 | 96.97 | 97.26 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R10KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter with PCS functionality. | 10.177 | 240 | 97 | SGS | [9/15/2023] | SGS | [9/15/2023] | [Ver0306] | No Information Submitted | [9/15/2023] | No Information Submitted | SGS | 2023-07-19 | No Information Submitted |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.0177 | 2.0353 | 3.053 | 5.0883 | 7.6325 | 10.1767 | 94.6879 | 95.9385 | 96.4038 | 96.8027 | 97.3387 | 96.7524 | 96.9086 | 95.3918 | 96.3253 | 96.8522 | 97.4475 | 97.971 | 97.3705 | 97.5113 | 94.9347 | 95.9602 | 96.6452 | 97.0116 | 97.5563 | 97.0255 | 97.1214 | 2023-05-11 | 2024-03-21
Shenzhen Megarevo Technology Co., Ltd. | R11K4H1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 11.4 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 11.598 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.0512 |  |  | 250 | 360 | 430 | 1.16 | 2.32 | 3.479 | 5.799 | 8.699 | 11.598 | 94.52 | 95.67 | 96.86 | 97.58 | 96.98 | 96.68 | 96.91 | 95.34 | 96.27 | 97.31 | 98.23 | 97.96 | 97.37 | 97.72 | 94.94 | 95.86 | 97.01 | 97.89 | 97.36 | 97.09 | 97.25 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R12KLNA-P4 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12.0 kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 12.1371 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 19.85 |  |  | 200 | 360 | 430 | 1.2137 | 2.4274 | 3.6411 | 6.0686 | 9.1028 | 12.1371 | 93.6636 | 94.7366 | 95.8921 | 96.8165 | 96.5363 | 96.1752 | 96.2949 | 94.2679 | 95.609 | 96.6993 | 97.5191 | 97.2309 | 96.7878 | 97.0058 | 94.2082 | 95.4735 | 96.3042 | 97.2515 | 96.9592 | 96.5623 | 96.7378 | 2024-11-21
Shenzhen Megarevo Technology Co., Ltd. | R12KLNA-P6 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 12.0 kW, 240 Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 12.2135 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 13.202 |  |  | 200 | 360 | 430 | 1.2214 | 2.4427 | 3.6641 | 6.1068 | 9.1601 | 12.2135 | 93.6096 | 94.6754 | 95.8363 | 96.8413 | 96.422 | 95.9874 | 96.2182 | 94.3362 | 95.3888 | 96.4568 | 97.5342 | 97.106 | 96.8384 | 96.908 | 93.9397 | 95.049 | 96.1157 | 97.2352 | 96.8097 | 96.3485 | 96.5899 | 2024-11-21
Shenzhen Megarevo Technology Co., Ltd. | R12KH1NA {240V} | Y | Y | Y | Y | Y | Y | N | Y | 12 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 12.362 | 240 | 97.5 | SGS | [1/26/2024] | SGS | [1/26/2024] | [V1.02.22(DSP), V1.01.43(ARM)] | 2024-05-01 | [1/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | 2024-05-01 |  | N | N | 13.0487 |  |  | 250 | 360 | 430 | 1.236 | 2.472 | 3.709 | 6.181 | 9.272 | 12.362 | 94.43 | 95.74 | 96.84 | 97.57 | 97.16 | 96.62 | 97 | 95.1 | 96.35 | 97.29 | 98.24 | 97.9 | 97.33 | 97.68 | 94.93 | 96 | 96.97 | 97.89 | 97.43 | 97.09 | 97.28 | 2024-05-01
Shenzhen Megarevo Technology Co., Ltd. | R16LNA-P4 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 16.0 kW, 240Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 16.1309 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 19.23 |  |  | 220 | 360 | 430 | 1.6131 | 3.2262 | 4.8393 | 8.0655 | 12.0982 | 16.1309 | 93.7909 | 94.8057 | 95.743 | 96.6913 | 96.4404 | 95.9995 | 96.1996 | 94.4435 | 95.6318 | 96.6583 | 97.5607 | 97.1891 | 96.599 | 96.9863 | 94.2996 | 95.0169 | 96.238 | 97.1403 | 96.7969 | 96.3892 | 96.5927 | 2024-11-21
Shenzhen Megarevo Technology Co., Ltd. | R16KLNA-P6 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 16.0 kW, 240Vac, Grid Support Utility Interactive Inverter with PCS functionality. | 16.1988 | 240 | 96.5 | SGS | [10/9/2024] | SGS | [10/9/2024] | [Ver 1.0406(DSP), Ver 2.0306(ARM)] | 2024-11-21 | [10/9/2024] | 2024-11-21 | SGS | 2024-09-29 | 2024-11-21 |  | N | N | 20.465 |  |  | 220 | 360 | 430 | 1.6199 | 3.2398 | 4.8596 | 8.0994 | 12.1491 | 16.1988 | 93.6398 | 94.6882 | 95.7477 | 96.6139 | 96.4152 | 96.0602 | 96.1617 | 94.3008 | 95.4624 | 96.4359 | 97.5442 | 97.2542 | 96.8193 | 96.9875 | 93.8386 | 95.1008 | 96.1652 | 97.1016 | 96.8655 | 96.2759 | 96.5923 | 2024-11-21
Shenzhen Poweroak Newener Co Ltd | EP900 {240V} | Y | Y | N | N | N | N | Y* | N | 9 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 9.23 | 240 | 95 | Intertek | [12/20/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-01-09 | No Information Submitted |  | N | N | 11.7 |  |  | 86 | 100 | 113 | 0.92297 | 1.8459 | 2.7689 | 4.6149 | 6.9223 | 9.2297 | 91.2622 | 94.8345 | 95.4546 | 95.2169 | 94.5125 | 93.662 | 94.6171 | 91.4645 | 94.5626 | 95.4472 | 95.3814 | 94.9862 | 94.2891 | 94.9276 | 90.698 | 94.6443 | 94.8447 | 95.3783 | 95.212 | 94.6643 | 94.9665 | 2023-05-22 | 2025-12-01
Shenzhen Poweroak Newener Co Ltd | EnergyPro 13K {240V} | Y | Y | N | N | N | N | Y* |  | 13.2 kVA, 240V split phase, Grid Support Inverter with PCS functionality | 13.1961 | 240 | 97 | Intertek | [7/8/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2025-07-11 |  |  | N | N | 16.4 |  |  | 370 | 420 | 500 | 1.3196 | 2.6392 | 3.9588 | 6.598 | 9.8971 | 13.1961 | 95.5412 | 97.4059 | 97.655 | 97.6563 | 97.4482 | 97.1279 | 97.4223 | 95.0427 | 97.0198 | 97.3378 | 97.4362 | 97.2394 | 96.9072 | 97.1771 | 94.0961 | 96.5435 | 96.954 | 97.1164 | 96.952 | 96.6122 | 96.8351 | 2025-09-02 | 2025-10-13
Shenzhen Poweroak Newener Co., Ltd. | EnergyPro 6K {240V} | N | Y | N | N | N | N | Y* |  | 5.777 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.777 | 240 | 95 | SGS | [9/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-09-23 |  |  | N | N | 10.68 |  |  | 63 | 76 | 87 | 0.578 | 1.155 | 1.733 | 2.888 | 4.332 | 5.777 | 90.8 | 94.14 | 95.16 | 95.33 | 95.15 | 94.4 | 94.93 | 91.82 | 94.16 | 95.47 | 95.43 | 95.48 | 95.54 | 95.26 | 91.74 | 94.46 | 95.1 | 95.46 | 95.76 | 95.62 | 95.39 | 2025-12-22
Shenzhen Senergy Technology Co., Ltd. | SE 5KHB-130-D2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 5.02 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 92.68 | 95.27 | 95.93 | 96.35 | 96.16 | 95.99 | 95.98 | 93.57 | 95.86 | 96.53 | 97.03 | 97.08 | 96.97 | 96.8 | 93.73 | 95.93 | 96.5 | 96.81 | 96.9 | 96.81 | 96.65 | 2024-02-01
Shenzhen Senergy Technology Co., Ltd. | SE 5KHB-130-D2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 5.04 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.504 | 1.008 | 1.512 | 2.52 | 3.78 | 5.04 | 92.99 | 95.51 | 96.13 | 96.56 | 96.34 | 96.22 | 96.18 | 93.67 | 95.99 | 96.75 | 97.31 | 97.43 | 97.38 | 97.1 | 93.79 | 96.14 | 96.61 | 96.98 | 97.24 | 97.24 | 96.92 | 2024-02-01 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 6KHB-130-D2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 6.124 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.61237 | 1.2247 | 1.8371 | 3.0618 | 4.5927 | 6.1237 | 91.5057 | 94.3751 | 95.4429 | 96.1451 | 96.2033 | 96.0221 | 95.8115 | 93.6071 | 95.9507 | 96.6981 | 97.1632 | 97.1394 | 97.0155 | 96.8845 | 93.0132 | 95.454 | 96.3177 | 96.9016 | 96.9299 | 96.7629 | 96.6117 | 2024-02-01 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 6KHB-130-D2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 6.149 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.61493 | 1.2299 | 1.8448 | 3.0747 | 4.612 | 6.1493 | 91.5991 | 94.4496 | 95.4631 | 96.2597 | 96.4111 | 96.355 | 95.9722 | 93.875 | 96.1389 | 96.881 | 97.3815 | 97.4928 | 97.4245 | 97.1802 | 92.6866 | 95.4464 | 96.4097 | 97.0954 | 97.2951 | 97.2686 | 96.8688 | 2024-02-01 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 7K6HB-180-T2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6472 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.76472 | 1.5294 | 2.2942 | 3.8236 | 5.7354 | 7.6472 | 92.9526 | 95.5516 | 96.215 | 96.6536 | 96.4528 | 96.189 | 96.2682 | 89.7494 | 96.0782 | 96.7932 | 97.1622 | 96.9742 | 96.771 | 96.648 | 94.069 | 96.2392 | 96.7722 | 97.1198 | 96.913 | 96.6498 | 96.7789 | 2023-11-13 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 7K6HB-180-T2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 7.648 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.736 | 7.648 | 92.946 | 95.544 | 96.21 | 96.648 | 96.448 | 96.186 | 96.2631 | 93.74 | 96.074 | 96.788 | 97.158 | 96.97 | 96.766 | 96.8034 | 94.064 | 96.234 | 96.766 | 97.116 | 96.906 | 96.704 | 96.7759 | 2024-02-01 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 8KHB-180-T2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 240 Vac Grid Support Utility Interactive Inverter | 8.0472 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.80472 | 1.6094 | 2.4142 | 4.0236 | 6.0354 | 8.0472 | 92.9526 | 95.5528 | 96.2152 | 96.6546 | 96.452 | 96.1892 | 96.2681 | 93.7514 | 96.077 | 96.7964 | 97.1666 | 96.974 | 96.7728 | 96.8093 | 94.0688 | 96.2392 | 96.77 | 97.1224 | 96.9124 | 96.6488 | 96.7788 | 2023-11-13 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 8KHB-180-T2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 kW, 208 Vac Grid Support Utility Interactive Inverter | 8.06 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 17.78 |  |  | 200 | 360 | 480 | 0.806 | 1.612 | 2.418 | 4.03 | 6.045 | 8.06 | 92.852 | 95.4494 | 96.1102 | 96.5538 | 96.3506 | 96.0918 | 96.1665 | 93.649 | 95.9818 | 96.693 | 97.0644 | 96.8732 | 96.6702 | 96.708 | 93.969 | 96.1426 | 96.6718 | 97.023 | 96.8134 | 96.5544 | 96.6802 | 2023-11-13 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 11K4HB-210-T2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac, Grid Support Utility Interactive Hybrid Inverter | 10.14 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.91 | 95.48 | 96.12 | 96.56 | 96.36 | 96.1 | 96.18 | 93.66 | 96.02 | 96.72 | 97.07 | 96.88 | 96.68 | 96.72 | 94.07 | 96.17 | 96.67 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-07-22 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 10KHB-210-T2/UL {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.1472 | 240 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.0147 | 2.0294 | 3.0442 | 5.0736 | 7.6104 | 10.1472 | 92.9963 | 95.5759 | 96.2237 | 96.6613 | 96.4562 | 96.1983 | 96.2761 | 93.7907 | 96.1027 | 96.8102 | 97.1618 | 96.9743 | 96.7739 | 96.8131 | 94.1119 | 96.2672 | 96.7835 | 97.1258 | 96.9159 | 96.6586 | 96.7866 | 2023-11-13 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 10KHB-210-T2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.1858 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.0186 | 2.0372 | 3.0557 | 5.0929 | 7.6393 | 10.1858 | 92.8933 | 95.4787 | 96.1281 | 96.5592 | 96.3579 | 96.0975 | 96.177 | 93.6955 | 96.0051 | 96.7063 | 97.0717 | 96.8789 | 96.675 | 96.7174 | 94.0173 | 96.1625 | 96.6817 | 96.9927 | 96.8158 | 96.5601 | 96.6795 | 2023-11-13 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 11K4HB-210-T2/UL {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac, Grid Support Utility Interactive Hybrid Inverter | 10.186 | 208 | 96.5 | SGS | [1/24/2025] | SGS | [1/24/2025] | [051001] | 2025-04-01 | [1/24/2025] | 2025-04-01 | SGS | 2025-01-13 | 2025-04-01 |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.028 | 3.042 | 5.07 | 7.605 | 10.14 | 93.05 | 95.58 | 96.24 | 96.66 | 96.45 | 96.2 | 96.28 | 93.72 | 96.07 | 96.82 | 97.15 | 96.96 | 96.78 | 96.8 | 94.05 | 96.25 | 96.79 | 97.12 | 96.92 | 96.66 | 96.79 | 2024-07-22 | 2025-04-01
Shenzhen Senergy Technology Co., Ltd. | SE 11K4HB-T2/LV-ULP {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 11.5669 | 240 | 96.5 | SGS | [3/28/2025] | SGS | [3/28/2025] | [051001] | 2025-07-01 | [3/28/2025] | 2025-07-01 | SGS | 2025-06-06 | 2025-07-01 |  | N | N | 19 |  |  | 200 | 360 | 480 | 1.1567 | 2.3134 | 3.4701 | 5.7834 | 8.6752 | 11.5669 | 93.0675 | 95.5749 | 96.2997 | 96.6409 | 96.4392 | 96.2088 | 96.2752 | 93.6781 | 96.0439 | 96.7972 | 97.1353 | 96.9536 | 96.7793 | 96.7878 | 94.0465 | 96.3229 | 96.8228 | 97.1182 | 96.9286 | 96.6545 | 96.7965 | 2025-07-01
Shenzhen Senergy Technology Co., Ltd. | SE 11K4HB-T2/LV-ULP {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 11.6088 | 208 | 96.5 | SGS | [3/28/2025] | SGS | [3/28/2025] | [051001] | 2025-07-01 | [3/28/2025] | 2025-07-01 | SGS | 2025-06-06 | 2025-07-01 |  | N | N | 19 |  |  | 200 | 360 | 480 | 1.1609 | 2.3218 | 3.4827 | 5.8044 | 8.7066 | 11.6088 | 92.8881 | 95.4935 | 96.1138 | 96.5693 | 96.353 | 96.1025 | 96.1756 | 93.6426 | 96.0296 | 96.7159 | 97.0645 | 96.8809 | 96.677 | 96.7174 | 94.0961 | 96.1711 | 96.6734 | 96.9968 | 96.8241 | 96.5565 | 96.6871 | 2025-07-01
Shenzhen Sinexcel Electric Co., Ltd. | PWS2-30P-NA {480V} | N | Y | N | N | N | N | N | N | 30kW, 480 Vac Bi-directional Grid Support Utility Interactive Inverter. | 29.907 | 480 | 95.5 | TUV SUD America | [2/20/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 36.02 |  |  | 355 | 600 | 750 | 2.9907 | 5.9814 | 8.9721 | 14.9535 | 22.4303 | 29.907 | 88.8953 | 92.6624 | 94.1195 | 95.103 | 95.1553 | 94.8591 | 94.6302 | 90.5876 | 93.6352 | 95.1535 | 96.2698 | 96.4172 | 96.4649 | 95.8647 | 90.1916 | 93.8984 | 94.9689 | 96.095 | 96.5957 | 96.4619 | 95.8976 | 2023-06-12
Shenzhen Sinexcel Electric Co., Ltd. | PWS2-30K-NA {480V} | N | N | Y | Y | Y | Y | Y* | Y | 30 kW, 480 Vac wall-mounted, bi-directional Grid Support Utility Interactive Energy Storage Inverter | 30.02 | 480 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [9/18/2017] | [V126] | 2018-10-15 | [9/18/2017] | 2021-10-01 | Intertek | 2021-09-13 | 2021-10-01 |  | N | N | 1.857 |  |  | 350 | 600 | 750 | 3.002 | 6.004 | 9.006 | 15.01 | 22.515 | 30.02 | 91.2328 | 94.2776 | 95.1804 | 95.6343 | 95.5611 | 95.1895 | 95.2749 | 94.0804 | 95.9185 | 96.6069 | 97.0086 | 97.0306 | 96.8722 | 96.7936 | 94.9891 | 96.635 | 97.1812 | 97.4446 | 97.4471 | 97.2664 | 97.2667 | 2017-11-01 | 2021-10-01
Shenzhen Sinexcel Electric Co., Ltd. | PWS1-50K-NA {480V} | N | N | Y | Y | Y | N | N | N | 50 kW, 480 Vac Grid Support Utility Interactive Inverter with 1 Inverter modules | 48.58 | 480 | 94 | No Information Submitted | No Information Submitted | Intertek | [4/23/2017] | [1320, 130, 1420] | 2018-10-15 | [4/23/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 860 |  |  | 500 | 650 | 850 | 4.858 | 9.716 | 14.574 | 24.29 | 36.435 | 48.58 | 87.3239 | 92.4174 | 93.9642 | 94.911 | 94.9348 | 94.6249 | 94.3675 | 86.4796 | 91.8343 | 93.5215 | 94.5382 | 94.6245 | 94.3137 | 93.9931 | 85.5066 | 91.2148 | 92.8921 | 94.1271 | 94.1483 | 93.9232 | 93.4895 | 2017-07-01 | 2018-10-15
Shenzhen Sinexcel Electric Co., Ltd. | PWS1-100K-NA {480V} | N | N | Y | Y | Y | N | N | N | 100 kW, 480 Vac Grid Support Utility Interactive Inverter with 2 Inverter modules | 98.013 | 480 | 94 | No Information Submitted | No Information Submitted | Intertek | [4/23/2017] | [1320, 130, 1420] | 2018-10-15 | [4/23/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 997 |  |  | 500 | 650 | 850 | 9.8013 | 19.6026 | 29.4039 | 49.0065 | 73.5097 | 98.013 | 87.3115 | 92.4599 | 94.0486 | 95.0349 | 95.1062 | 94.7968 | 94.5048 | 86.5716 | 91.9322 | 93.5785 | 94.5421 | 94.644 | 94.3807 | 94.0231 | 85.5959 | 91.2784 | 92.9994 | 94.0717 | 94.2626 | 94.044 | 93.5641 | 2017-07-01 | 2018-10-15
Shenzhen Sinexcel Electric Co., Ltd. | PWS1-150K-NA {480V} | N | N | Y | Y | Y | N | N | N | 150 kW, 480 Vac Grid Support Utility Interactive Inverter with 3 Inverter modules | 147.47 | 480 | 94.5 | No Information Submitted | No Information Submitted | Intertek | [4/23/2017] | [1320, 130, 1420] | 2018-10-15 | [4/23/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1360 |  |  | 500 | 650 | 850 | 14.747 | 29.494 | 44.241 | 73.735 | 110.6025 | 147.47 | 88.5911 | 93.0981 | 94.4501 | 95.1722 | 95.219 | 94.8928 | 94.7294 | 87.8328 | 92.6191 | 94.0834 | 94.9672 | 95.0226 | 94.7007 | 94.4744 | 86.7442 | 91.8963 | 93.4554 | 94.3477 | 94.4727 | 94.2361 | 93.8746 | 2017-07-01 | 2018-10-15
Shenzhen Sinexcel Electric Co., Ltd. | PWS1-250K-NA {480V} | N | N | Y | Y | Y | N | N | N | 250 kW, 480 Vac Grid Support Utility Interactive Inverter with 5 Inverter modules | 244.026 | 480 | 95 | No Information Submitted | No Information Submitted | Intertek | [4/23/2017] | [1320, 130, 1420] | 2018-10-15 | [4/23/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1860 |  |  | 500 | 650 | 850 | 24.4026 | 48.8052 | 73.2078 | 122.013 | 183.0195 | 244.026 | 91.3922 | 94.968 | 95.7012 | 96.033 | 95.7801 | 95.4154 | 95.5894 | 90.4456 | 94.3962 | 95.2142 | 95.5745 | 95.3838 | 95.0192 | 95.1384 | 89.2163 | 93.5746 | 94.5987 | 95.0795 | 94.9604 | 94.63 | 94.6264 | 2017-07-01 | 2018-10-15
Shenzhen Sinexcel Electric Co., Ltd. | PWS1-500KTL-NA {400V} | N | N | Y | Y | Y | N | N | N | 500 kW, 400 Vac Grid Support Utility-Interactive Energy Storage Inverter | 498.34 | 400 | 96 | No Information Submitted | No Information Submitted | Intertek | [02/26/2018] | [1400] | 2018-10-15 | [02/26/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 5 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216. | N | N | 289.9 |  |  | 640 | 750 | 900 | 49.83 | 99.67 | 149.5 | 249.17 | 373.76 | 498.34 | 93.95 | 96 | 96.6 | 96.83 | 96.64 | 96.31 | 96.52 | 93.16 | 95.61 | 96.3 | 96.61 | 96.47 | 96.13 | 96.28 | 92.19 | 95.03 | 95.86 | 96.27 | 96.14 | 95.84 | 95.9 | 2018-05-01 | 2018-10-15
Shenzhen Sinexcel Electric Co., Ltd. | PWS1-500KTL-NA-8M1 {400V} | N | Y | N | N | N | N | N | N | 500 kW, 400 Vac Grid Support Utility-Interactive Energy Storage lnverter | 498.34 | 400 | 96 | Intertek | [9/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency data includes the 500 kW Powerel Enterprise Co., Ltd. transformer, | N | N | 289.9 |  |  | 640 | 750 | 900 | 49.834 | 99.668 | 149.502 | 249.17 | 373.755 | 498.34 | 93.2694 | 95.6732 | 96.4581 | 96.784 | 96.6907 | 96.45 | 96.4826 | 92.4929 | 95.2819 | 96.1529 | 96.5648 | 96.5191 | 96.2732 | 96.2495 | 91.5306 | 94.71 | 95.7136 | 96.2171 | 96.1896 | 95.9802 | 95.8674 | 2024-09-11
Shenzhen Sinexcel Electric Co., Ltd. | PWS1-500KTL-NA-8M8 {400V} | N | Y | N | N | N | N | N | N | 500 kW, 400 Vac Grid Support Utility-Interactive Energy Storage lnverter | 498.754 | 400 | 96 | Intertek | [9/22/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency data includes the 500 kW Powerel Enterprise Co., Ltd. transformer, | N | N | 289.8 |  |  | 640 | 750 | 900 | 49.8754 | 99.7508 | 149.6262 | 249.377 | 374.0655 | 498.754 | 93.2394 | 95.688 | 96.414 | 96.8107 | 96.7067 | 96.4443 | 96.4907 | 92.4627 | 95.2937 | 96.1623 | 96.5237 | 96.515 | 96.2782 | 96.2395 | 91.5295 | 94.7341 | 95.7481 | 96.2323 | 96.1861 | 96.0092 | 95.8756 | 2024-09-11
Shenzhen Sinexcel Electric Co., Ltd. | PWS1-1725KTL-H-NA-8M1 {690V} | N | Y | N | N | N | N | N | N | 1725 kW, 690 Vac Grid Support Utility-Interactive Energy Storage lnverter | 1708.18 | 690 | 93 | Intertek | [4/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency data includes the 1725 kW Powerel Enterprise Co., Ltd. transformer, | N | N | 321.25 |  |  | 1080 | 1300 | 1450 | 170.818 | 341.636 | 512.454 | 854.09 | 1281.135 | 1708.18 | 91.8947 | 91.5318 | 93.0119 | 93.4969 | 93.1504 | 93.4552 | 93.0906 | 89.0632 | 90.6275 | 92.1708 | 92.7686 | 92.5559 | 93.4828 | 92.3646 | 84.5823 | 89.5347 | 91.3839 | 92.7554 | 93.1099 | 93.5747 | 92.3317 | 2024-09-11
Shenzhen Sinexcel Electric Co., Ltd. | PWS1-1725KTL-H-NA-8M8 {690V} | N | Y | N | N | N | N | N | N | 1725 kW, 690 Vac Grid Support Utility-Interactive Energy Storage lnverter | 1710.71 | 690 | 93 | Intertek | [4/28/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Weighted Efficiency data includes the 1725 kW Powerel Enterprise Co., Ltd. transformer, | N | N | 310.06 |  |  | 1080 | 1300 | 1450 | 171.071 | 342.142 | 513.213 | 855.355 | 1283.0325 | 1710.71 | 92.2633 | 90.9798 | 92.8009 | 93.6812 | 92.9024 | 93.8281 | 92.9783 | 87.2275 | 90.8218 | 91.873 | 93.1491 | 93.1782 | 92.0924 | 92.6053 | 85.3306 | 89.7668 | 91.4501 | 93.0336 | 92.6245 | 92.787 | 92.143 | 2024-09-11
Shenzhen Sinexcel Isuna Energy Technology Co., Ltd. | Isuna U10K-PH {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 10.074 | 240 | 97 | Intertek | [12/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 21.406 |  |  | 140 | 320 | 500 | 1.007 | 2.015 | 3.022 | 5.037 | 7.555 | 10.074 | 92.03 | 93.91 | 95.29 | 96.22 | 96.62 | 96.53 | 96.05 | 93.89 | 95.38 | 96.16 | 96.87 | 97.32 | 97.34 | 96.85 | 95.68 | 96.99 | 97.54 | 97.87 | 98.03 | 97.89 | 97.78 | 2026-02-23 |  | Y | N | N | N | N | N | N | N | N
Shenzhen Sinexcel Isuna Energy Technology Co., Ltd. | Isuna U15K-PH {240V} | Y | Y | N | N | N | N | N |  | 15 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 15.042 | 240 | 97 | Intertek | [12/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 21.42 |  |  | 140 | 320 | 500 | 1.504 | 3.008 | 4.513 | 7.521 | 11.281 | 15.042 | 95.39 | 95.29 | 96.25 | 96.62 | 96.44 | 96.07 | 96.34 | 95.33 | 96.16 | 96.99 | 97.32 | 97.32 | 97.16 | 97.14 | 97.49 | 97.54 | 98 | 98.03 | 97.84 | 97.58 | 97.85 | 2026-02-23 |  | Y | N | N | N | N | N | N | N | N
Shenzhen Sinexcel Isuna Energy Technology Co., Ltd. | Isuna U20K-PH {240V} | Y | Y | N | N | N | N | N |  | 20 kW, 240 Vac Grid Support Hybrid Utility Interactive Inverter | 20.181 | 240 | 97 | Intertek | [12/3/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 21.408 |  |  | 140 | 320 | 500 | 2.018 | 4.036 | 6.054 | 10.09 | 15.136 | 20.181 | 93.91 | 95.93 | 96.47 | 96.53 | 96.07 | 95.54 | 96.09 | 95.38 | 97.14 | 97.14 | 97.34 | 97.16 | 96.73 | 97.1 | 96.99 | 97.82 | 98 | 97.89 | 97.58 | 96.64 | 97.64 | 2026-02-23 |  | Y | N | N | N | N | N | N | N | N
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL8K-P2US {240V} | Y | Y | N | N | N | N | Y* |  | 7.98 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.9814 | 240 | 96 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.39 |  |  | 108 | 380 | 480 | 0.79814 | 1.5963 | 2.3944 | 3.9907 | 5.986 | 7.9814 | 90.9385 | 94.1039 | 94.9752 | 95.083 | 95.0387 | 94.6196 | 94.8087 | 92.1593 | 95.6656 | 96.6163 | 96.6433 | 97.0374 | 96.9779 | 96.6374 | 92.4438 | 95.9014 | 96.6012 | 97.0486 | 97.2916 | 97.2167 | 96.8905 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL8K-P2US-S {240V} | Y | Y | N | N | N | N | Y* |  | 7.98 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.9814 | 240 | 96 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.39 |  |  | 108 | 380 | 480 | 0.79814 | 1.5963 | 2.3944 | 3.9907 | 5.986 | 7.9814 | 90.9385 | 94.1039 | 94.9752 | 95.083 | 95.0387 | 94.6196 | 94.8087 | 92.1593 | 95.6656 | 96.6163 | 96.6433 | 97.0374 | 96.9779 | 96.6374 | 92.4438 | 95.9014 | 96.6012 | 97.0486 | 97.2916 | 97.2167 | 96.8905 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL10K-P2US {240V} | Y | Y | N | N | N | N | Y* |  | 10.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.0109 | 240 | 96 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.12 |  |  | 135 | 380 | 480 | 1.0011 | 2.0022 | 3.0033 | 5.0055 | 7.5082 | 10.0109 | 92.0512 | 94.9782 | 94.9328 | 95.3714 | 95.3991 | 94.9543 | 95.1601 | 93.0994 | 96.2304 | 96.2761 | 96.8719 | 97.0247 | 96.9062 | 96.7001 | 93.6663 | 96.3246 | 96.5808 | 97.0256 | 97.1253 | 97.0288 | 96.8558 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL10K-P2US-S {240V} | Y | Y | N | N | N | N | Y* |  | 10.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.0109 | 240 | 96 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.12 |  |  | 135 | 380 | 480 | 1.0011 | 2.0022 | 3.0033 | 5.0055 | 7.5082 | 10.0109 | 92.0512 | 94.9782 | 94.9328 | 95.3714 | 95.3991 | 94.9543 | 95.1601 | 93.0994 | 96.2304 | 96.2761 | 96.8719 | 97.0247 | 96.9062 | 96.7001 | 93.6663 | 96.3246 | 96.5808 | 97.0256 | 97.1253 | 97.0288 | 96.8558 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL12K-P2US {240V} | Y | Y | N | N | N | N | Y* |  | 12.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.0145 | 240 | 96.5 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.39 |  |  | 161 | 380 | 480 | 1.2014 | 2.4029 | 3.6043 | 6.0072 | 9.0109 | 12.0145 | 93.1006 | 95.228 | 95.5523 | 95.8393 | 95.6025 | 95.1408 | 95.5043 | 94.3433 | 96.5994 | 96.675 | 97.0511 | 96.9701 | 96.7737 | 96.8183 | 95.2452 | 96.8669 | 96.9412 | 97.2998 | 97.1893 | 96.9458 | 97.0767 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL12K-P2US-S {240V} | Y | Y | N | N | N | N | Y* |  | 12.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.0145 | 240 | 96.5 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.39 |  |  | 161 | 380 | 480 | 1.2014 | 2.4029 | 3.6043 | 6.0072 | 9.0109 | 12.0145 | 93.1006 | 95.228 | 95.5523 | 95.8393 | 95.6025 | 95.1408 | 95.5043 | 94.3433 | 96.5994 | 96.675 | 97.0511 | 96.9701 | 96.7737 | 96.8183 | 95.2452 | 96.8669 | 96.9412 | 97.2998 | 97.1893 | 96.9458 | 97.0767 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL15K-P2US {240V} | Y | Y | N | N | N | N | Y* |  | 15.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 15.0148 | 240 | 96.5 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.08 |  |  | 202 | 380 | 480 | 1.5015 | 3.003 | 4.5045 | 7.5074 | 11.2611 | 15.0148 | 94.5483 | 95.5289 | 96.0138 | 96.1843 | 95.8054 | 95.25 | 95.8181 | 95.5893 | 96.5176 | 96.9793 | 97.101 | 96.8732 | 96.5137 | 96.8467 | 96.0793 | 96.8399 | 97.2558 | 97.3226 | 96.9795 | 96.6351 | 97.0245 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Shenzhen SOSEN Innovation Technology Co.,Ltd | SSE-HL15K-P2US-S {240V} | Y | Y | N | N | N | N | Y* |  | 15.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 15.0148 | 240 | 96.5 | CSA Group | [11/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-11-20 |  |  | N | N | 10.08 |  |  | 202 | 380 | 480 | 1.5015 | 3.003 | 4.5045 | 7.5074 | 11.2611 | 15.0148 | 94.5483 | 95.5289 | 96.0138 | 96.1843 | 95.8054 | 95.25 | 95.8181 | 95.5893 | 96.5176 | 96.9793 | 97.101 | 96.8732 | 96.5137 | 96.8467 | 96.0793 | 96.8399 | 97.2558 | 97.3226 | 96.9795 | 96.6351 | 97.0245 | 2026-02-02 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Sichuan Clou Energy Electric Co., Ltd. | NEPCS-1600 {630V} | N | N | Y | Y | Y | N | N | N | 1600 kVA, 630 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter | 1617.2811 | 630 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [9/7/2022] | [V1C1B4] | 2023-01-03 | [9/7/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 581 |  |  | 915 | 1200 | 1500 | 161.7281 | 323.4562 | 485.1843 | 808.6406 | 1212.9609 | 1617.2811 | 98.34 | 98.718 | 98.832 | 98.814 | 98.794 | 98.764 | 98.7793 | 98.164 | 98.446 | 98.568 | 98.528 | 98.486 | 98.336 | 98.4823 | 97.852 | 98.188 | 98.36 | 98.268 | 98.224 | 98.138 | 98.2286 | 2023-01-03
Sichuan Clou Energy Electric Co., Ltd. | NEPCS-2000 {690V} | N | N | Y | Y | Y | N | N | N | 2000 kVA, 690 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter | 2000.4 | 690 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [9/7/2022] | [V1C1B4] | 2023-01-03 | [9/7/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 685 |  |  | 1050 | 1250 | 1500 | 200.04 | 400.08 | 600.12 | 1000.2 | 1500.3 | 2000.4 | 98.398 | 98.7 | 98.874 | 98.852 | 98.828 | 98.778 | 98.8125 | 98.3 | 98.574 | 98.706 | 98.666 | 98.596 | 98.554 | 98.6089 | 97.954 | 98.234 | 98.466 | 98.376 | 98.302 | 98.236 | 98.3166 | 2023-01-03
Sichuan Clou Energy Electric Co., Ltd. | NEPCS-2300 {800V} | N | N | Y | Y | Y | N | N | N | 2300 kVA, 800 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter | 2299.96 | 800 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [9/7/2022] | [V1C1B4] | 2023-01-03 | [9/7/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 752 |  |  | 1200 | 1350 | 1500 | 229.996 | 459.992 | 689.988 | 1149.98 | 1724.97 | 2299.96 | 98.392 | 98.738 | 98.892 | 98.878 | 98.832 | 98.776 | 98.8238 | 98.252 | 98.488 | 98.71 | 98.652 | 98.564 | 98.502 | 98.5806 | 97.918 | 98.26 | 98.434 | 98.328 | 98.264 | 98.234 | 98.2823 | 2023-01-03
Sichuan Clou Energy Electric Co., Ltd. | NEPCS-2600 {900V} | N | N | Y | Y | Y | N | N | N | 2600 kVA, 900 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter | 2602.35 | 900 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [9/7/2022] | [V1C1B4] | 2023-01-03 | [9/7/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 879 |  |  | 1320 | 1400 | 1500 | 260.235 | 520.47 | 780.705 | 1301.175 | 1951.7625 | 2602.35 | 98.358 | 98.742 | 98.84 | 98.802 | 98.75 | 98.632 | 98.7497 | 98.276 | 98.582 | 98.702 | 98.636 | 98.498 | 98.37 | 98.5404 | 97.966 | 98.378 | 98.51 | 98.468 | 98.358 | 98.204 | 98.377 | 2023-01-03
Sichuan Clou Energy Electric Co., Ltd. | NEPCSH-3200 {630V} | N | N | Y | Y | Y | N | N | N | 3200 kVA, 630 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter | 3200.5687 | 630 | 98.5 | No Information Submitted | No Information Submitted | Intertek | [9/7/2022] | [V1C1B4] | 2023-01-03 | [9/7/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 1379 |  |  | 915 | 1200 | 1500 | 320.0569 | 640.1137 | 960.1706 | 1600.2844 | 2400.4266 | 3200.5687 | 98.3097 | 98.7069 | 98.8537 | 98.8291 | 98.8088 | 98.732 | 98.7896 | 98.1932 | 98.4563 | 98.5748 | 98.5098 | 98.4591 | 98.4187 | 98.4708 | 98.004 | 98.174 | 98.302 | 98.2956 | 98.236 | 98.128 | 98.2387 | 2023-01-03
Sigenergy Technology Co., Ltd. | SigenStor EC 4.8 SP US {240V} | Y | Y | N | N | N | N | Y* | Y | 4.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.808 | 240 | 97 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 | 2025-08-21 |  | N | N | 3.3 |  |  | 270 | 360 | 480 | 0.481 | 0.962 | 1.442 | 2.404 | 3.606 | 4.808 | 93.93 | 96.05 | 96.64 | 96.96 | 97.03 | 96.96 | 96.79 | 95.12 | 96.82 | 97.3 | 97.54 | 97.54 | 97.41 | 97.37 | 93.95 | 96.02 | 96.71 | 97.11 | 97.2 | 97.14 | 96.93 | 2025-08-21
Sigenergy Technology Co., Ltd. | SigenStor EC 5.7 SP US {240V} | Y | Y | N | N | N | N | Y* | Y | 5.7 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.776 | 240 | 97 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 | 2025-08-21 |  | N | N | 3.3 |  |  | 270 | 360 | 480 | 0.578 | 1.155 | 1.733 | 2.888 | 4.332 | 5.776 | 94.61 | 96.34 | 96.8 | 97 | 97 | 96.89 | 96.84 | 95.59 | 97.05 | 97.42 | 97.55 | 97.46 | 97.32 | 97.37 | 94.49 | 96.33 | 96.88 | 97.16 | 97.16 | 97.05 | 96.97 | 2025-08-21
Sigenergy Technology Co., Ltd. | SigenStor EC 7.6 SP US {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.649 | 240 | 97 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 | 2025-08-21 |  | N | N | 3.3 |  |  | 270 | 360 | 480 | 0.765 | 1.53 | 2.295 | 3.824 | 5.737 | 7.649 | 95.46 | 96.7 | 96.9 | 97.03 | 96.89 | 96.69 | 96.84 | 96.37 | 97.33 | 97.52 | 97.51 | 97.32 | 97.2 | 97.34 | 95.42 | 96.76 | 97.07 | 97.18 | 97.04 | 96.87 | 96.98 | 2025-08-21
Sigenergy Technology Co., Ltd. | SigenStor EC 9.6 SP US {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.6533 | 240 | 97 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 | 2025-08-21 |  | N | N | 3.3 |  |  | 270 | 360 | 480 | 0.96533 | 1.9307 | 2.896 | 4.8266 | 7.24 | 9.6533 | 95.9936 | 96.8717 | 96.9858 | 96.9572 | 96.7235 | 96.46 | 96.7691 | 96.7865 | 97.4783 | 97.5478 | 97.3936 | 97.2278 | 97.1 | 97.2895 | 95.9591 | 96.975 | 97.1574 | 97.1165 | 96.9118 | 96.779 | 96.9427 | 2025-08-21
Sigenergy Technology Co., Ltd. | SigenStor EC SP US {240V} | Y | Y | N | N | N | N | Y* | Y | 11.5 kW, 240 Vac Grid Support Utility Interactive Inverter with PCS functionality. | 11.503 | 240 | 97 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 | 2025-08-21 |  | N | N | 9.6 |  |  | 270 | 360 | 480 | 1.15 | 2.301 | 3.451 | 5.751 | 8.627 | 11.503 | 96.17 | 96.91 | 97.12 | 97.07 | 96.82 | 96.49 | 96.87 | 96.87 | 97.5 | 97.61 | 97.53 | 97.18 | 97.13 | 97.31 | 96.14 | 97.06 | 97.2 | 97.18 | 97 | 96.69 | 97.02 | 2025-08-21 | 2025-10-01
Sigenergy Technology Co., Ltd. | SigenStor EC SP US {208V} | Y | Y | N | N | N | N | Y* |  | 11.5 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.504 | 208 | 96.5 | CSA Group | [6/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-07-02 |  |  | N | N | 10.2 |  |  | 270 | 360 | 480 | 1.15 | 2.301 | 3.451 | 5.752 | 8.628 | 11.504 | 95.63 | 96.31 | 96.52 | 96.48 | 96.21 | 94.78 | 96.21 | 96.26 | 96.92 | 97.03 | 96.93 | 96.62 | 94.8 | 96.64 | 95.58 | 96.5 | 96.7 | 96.63 | 96.36 | 94.54 | 96.34 | 2026-09-01 |  | Y | N | N | N | N | N | Y | N | N
SimpliPhi Power | SPHI-IN-6 {120V} | Y | N | Y | Y | Y | N | N | N | 6 kW, 120 Vac Split Phase, Transformerless Grid Support Utility Interactive Inverter | 6.0177 | 120 | 93.5 | No Information Submitted | No Information Submitted | Intertek | [8/24/2023] | [V01.14] | 2023-11-13 | [7/13/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 43 |  |  | 250 | 370 | 500 | 0.60177 | 1.2035 | 1.8053 | 3.0088 | 4.5133 | 6.0177 | 84.5 | 90.4 | 92.4 | 93.9 | 94.5 | 94.4 | 93.5 | 83.8 | 90.3 | 92.5 | 94.1 | 94.9 | 94.9 | 93.7 | 80.8 | 88.9 | 91 | 93.4 | 94.1 | 94.3 | 92.8 | 2023-11-13
SINENG ELECTRIC CO., LTD. | EH-0200-HA-M-US {690V} | N | Y | N | N | N | N | N | N | 220 kW, 690 Vac Grid Support Utility Interactive Inverter connect to grid with 225 kW, liquid-immersed three-phase transformer | 220.432 | 690 | 97.5 | TUV Rheinland | [10/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 316 |  |  | 1056 | 1199 | 1346 | 22.0432 | 44.0864 | 66.1296 | 110.216 | 165.324 | 220.432 | 96.2338 | 97.4415 | 97.8388 | 98.012 | 97.9147 | 97.6398 | 97.8214 | 95.7065 | 97.1207 | 97.6218 | 97.8341 | 97.7678 | 97.5577 | 97.6389 | 95.0323 | 96.5501 | 97.2843 | 97.6244 | 97.5903 | 97.3908 | 97.3964 | 2023-03-21
SINENG ELECTRIC CO., LTD. | EH-1250-HB-UD-US {690V} | N | Y | N | N | N | N | N | Y | 1250 kW, 690 Vac Grid Support Utility Interactive Inverter | 1250.7351 | 690 | 98 | CSA Group | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-08-01 | Efficiency data inclusive of transformer effect based on 1500 KVA Liquid-Immersed Distribution Transformer Table in DOE2016 | N | N | 204.94 |  |  | 1000 | 1250 | 1500 | 125.0735 | 250.147 | 375.2205 | 625.3676 | 938.0514 | 1250.7351 | 96.9589 | 98.0148 | 98.2081 | 98.2166 | 98.2052 | 98.0532 | 98.141 | 96.9688 | 98.0219 | 98.0645 | 98.2237 | 98.2067 | 98.0574 | 98.127 | 96.561 | 97.7732 | 98.039 | 98.1313 | 98.1427 | 98.0148 | 98.0397 | 2025-08-01
SINENG ELECTRIC CO., LTD. | EH-1725-HA-UD-US {690V} | N | Y | N | N | N | N | N | Y | 1725 kW, 690 Vac Grid Support Utility Interactive Inverter | 1726.7022 | 690 | 98 | CSA Group | [10/25/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-21 | Efficiency data inclusive of transformer effect based on 2000 kW Liquid-Immersed Distribution Transformer Table in DOE2016 | N | N | 157.41 |  |  | 1000 | 1250 | 1500 | 172.6702 | 345.3404 | 518.0107 | 863.3511 | 1295.0267 | 1726.7022 | 95.6137 | 97.902 | 97.8676 | 98.4783 | 98.5554 | 98.4013 | 98.2986 | 94.6345 | 97.5737 | 97.6082 | 98.2848 | 98.4346 | 98.312 | 98.1028 | 94.0932 | 97.0876 | 97.3452 | 98.1038 | 98.3079 | 98.226 | 97.9158 | 2024-08-21
SINENG ELECTRIC CO., LTD. | EH-2000-HA-UD-US {690V} | N | Y | N | N | N | N | N | Y | 2000 kW, 690 Vac Grid Support Utility Interactive Inverter | 2003.824 | 690 | 98 | CSA Group | [10/25/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-08-21 | Efficiency data inclusive of transformer effect based on 2000 kW Liquid-Immersed Distribution Transformer Table in DOE2016 | N | N | 159.36 |  |  | 1000 | 1250 | 1500 | 200.3824 | 400.7648 | 601.1472 | 1001.912 | 1502.868 | 2003.824 | 95.8415 | 98.0865 | 98.0841 | 98.5453 | 98.5356 | 98.1699 | 98.335 | 95.269 | 97.6974 | 97.8048 | 98.376 | 98.44 | 98.1311 | 98.1709 | 94.5038 | 97.3159 | 97.5749 | 98.2187 | 98.3401 | 98.062 | 98.0042 | 2024-08-21
SMA America | SBSE3.8-US-50 {208V} | Y | Y | N | N | N | N | Y* | Y | 3.8 kW, 208 Vac Grid Support Utility Interactive Inverters | 3.332 | 208 | 97 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.27 |  |  | 91 | 377 | 480 | 0.3332 | 0.6664 | 0.99961 | 1.666 | 2.499 | 3.332 | 91.9689 | 95.4371 | 95.015 | 95.362 | 95.1386 | 94.7227 | 95.038 | 90.7699 | 95.5679 | 96.3617 | 97.5224 | 97.7374 | 97.606 | 97.1334 | 93.4654 | 96.7253 | 97.4773 | 99.8451 | 98.089 | 97.991 | 98.1264 | 2024-04-02
SMA America | SBS3.8-US-10 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac, 1-phase, Sunny Boy Storage- Permanently-connected, Transformerless Multimode - Grid Support Utility Interactive and Standalone functionality - Inverter | 3.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | UL | [12/14/2017] | [1.00.04.R] | 2018-10-15 | [12/14/2017] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | N | N | 6.53 |  |  | 220 | 360 | 550 | 0.38129 | 0.76257 | 1.1439 | 1.9064 | 2.8596 | 3.8129 | 92.6936 | 95.522 | 96.0988 | 96.4348 | 96.4124 | 96.2874 | 96.18 | 93.606 | 96.4562 | 97.1022 | 97.4216 | 97.4656 | 97.3776 | 97.2035 | 88.5644 | 94.7228 | 96.0868 | 96.8482 | 97.0258 | 97.0206 | 96.422 | 2018-07-02 | 2020-01-13
SMA America | SBSE3.8-US-50 {240V} | Y | Y | N | N | N | N | Y* | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverters | 3.8699 | 240 | 96.5 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.22 |  |  | 91 | 377 | 480 | 0.38699 | 0.77399 | 1.161 | 1.935 | 2.9025 | 3.8699 | 93.0814 | 95.6956 | 95.2874 | 95.4254 | 95.1957 | 94.6509 | 95.1681 | 92.0493 | 95.9549 | 96.9939 | 97.7121 | 97.9883 | 97.752 | 97.4599 | 92.1616 | 96.1067 | 97.2841 | 97.9366 | 98.0623 | 98.0861 | 97.6099 | 2024-04-02
SMA America | SBSE4.8-US-50 {208V} | Y | Y | N | N | N | N | Y* | Y | 4.8 kW, 208 Vac Grid Support Utility Interactive Inverters | 4.166 | 208 | 97 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.27 |  |  | 112 | 383 | 480 | 0.4166 | 0.8332 | 1.2498 | 2.083 | 3.1245 | 4.166 | 92.7583 | 95.9984 | 96.4304 | 96.0094 | 95.7187 | 95.2343 | 95.7365 | 92.472 | 95.9293 | 97.0746 | 97.5559 | 97.5201 | 97.4297 | 97.1882 | 94.8507 | 97.0524 | 97.8281 | 98.3703 | 98.0199 | 97.8937 | 97.889 | 2024-04-02
SMA America | SBSE4.8-US-50 {240V} | Y | Y | N | N | N | N | Y* | Y | 4.8 kW, 240 Vac Grid Support Utility Interactive Inverters | 4.8229 | 240 | 97 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.22 |  |  | 112 | 383 | 480 | 0.48229 | 0.96458 | 1.4469 | 2.4114 | 3.6172 | 4.8229 | 93.5741 | 96.248 | 96.0843 | 96.094 | 95.8009 | 95.2777 | 95.8036 | 93.1963 | 96.5204 | 97.2174 | 97.9076 | 97.7361 | 97.671 | 97.4643 | 93.8017 | 96.6521 | 97.4959 | 97.9434 | 98.0153 | 97.982 | 97.6995 | 2024-04-02
SMA America | SBSE5.8-US-50 {208V} | Y | Y | N | N | N | N | Y* | Y | 5.8 kW, 208 Vac Grid Support Utility Interactive Inverters | 4.9999 | 208 | 97 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.27 |  |  | 136 | 389 | 480 | 0.49999 | 0.99998 | 1.5 | 2.5 | 3.7499 | 4.9999 | 93.5256 | 96.2479 | 97.0897 | 96.4304 | 96.1394 | 95.7037 | 96.1937 | 92.791 | 96.6303 | 97.3739 | 97.6607 | 97.4597 | 97.3226 | 97.2565 | 94.8507 | 97.4773 | 98.7461 | 98.1057 | 97.9486 | 97.7884 | 97.9218 | 2024-04-02
SMA America | SBS5.0-US-10 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac, 1-phase, Sunny Boy Storage- Permanently-connected, Transformerless Multimode - Grid Support Utility Interactive and Standalone functionality - Inverter | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | UL | [12/14/2017] | [1.00.04.R] | 2018-10-15 | [12/14/2017] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | N | N | 6.53 |  |  | 220 | 360 | 550 | 0.5016 | 1.0032 | 1.5048 | 2.508 | 3.762 | 5.016 | 93.7572 | 95.9944 | 96.3534 | 96.4338 | 96.3082 | 96.1104 | 96.2124 | 94.6136 | 96.9314 | 97.3164 | 97.4512 | 97.3954 | 97.2108 | 97.2539 | 92.4176 | 95.7396 | 96.5304 | 96.9972 | 97.034 | 96.5908 | 96.6943 | 2018-07-02 | 2020-01-13
SMA America | SBSE5.8-US-50 {240V} | Y | Y | N | N | N | N | Y* | Y | 5.8 kW, 240 Vac Grid Support Utility Interactive Inverters | 5.7759 | 240 | 97.5 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.22 |  |  | 136 | 389 | 480 | 0.57759 | 1.1552 | 1.7328 | 2.8879 | 4.3319 | 5.7759 | 94.5499 | 96.8326 | 97.173 | 96.576 | 96.2533 | 95.7726 | 96.3682 | 94.4396 | 96.989 | 97.5907 | 97.7376 | 97.6853 | 97.5726 | 97.5146 | 94.7989 | 97.2841 | 97.8769 | 98.0724 | 98.0767 | 97.9079 | 97.8726 | 2024-04-02
SMA America | SBS6.0-US-10 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac, 1-phase, Sunny Boy Storage- Permanently-connected, Transformerless Multimode - Grid Support Utility Interactive and Standalone functionality - Inverter | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | UL | [12/14/2017] | [1.00.04.R] | 2018-10-15 | [12/14/2017] | 2020-01-13 | UL | 2019-12-16 | 2020-01-13 |  | N | N | 6.53 |  |  | 220 | 360 | 550 | 0.6022 | 1.2044 | 1.8066 | 3.011 | 4.5165 | 6.022 | 94.4642 | 96.1546 | 96.429 | 96.4004 | 96.1916 | 95.9566 | 96.1812 | 95.8482 | 97.1984 | 97.4014 | 97.4512 | 97.284 | 96.9922 | 97.2569 | 93.2534 | 96.2388 | 96.799 | 97.0266 | 96.9664 | 96.8002 | 96.7657 | 2018-07-02 | 2020-01-13
SMA America | SBSE7.7-US-50 {208V} | Y | Y | N | N | N | N | Y* | Y | 7.7 kW, 208 Vac Grid Support Utility Interactive Inverters | 6.6445 | 208 | 97 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.27 |  |  | 180 | 400 | 480 | 0.66445 | 1.3289 | 1.9933 | 3.3222 | 4.9834 | 6.6445 | 94.2736 | 96.912 | 97.2224 | 96.8823 | 96.4626 | 96.0167 | 96.5545 | 94.4081 | 97.1816 | 97.5354 | 97.4703 | 97.3359 | 97.076 | 97.2502 | 96.3053 | 97.9159 | 98.3666 | 98.0074 | 97.8107 | 97.5284 | 97.8497 | 2024-04-02
SMA America | SBSE7.7-US-50 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.7 kW, 240 Vac Grid Support Utility Interactive Inverters | 7.622 | 240 | 97.5 | UL | [2/13/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2023-12-11 | 2024-04-02 |  | N | N | 11.22 |  |  | 180 | 400 | 480 | 0.7622 | 1.5244 | 2.2866 | 3.811 | 5.7165 | 7.622 | 95.3476 | 96.8667 | 97.3793 | 96.977 | 96.5693 | 96.1249 | 96.6959 | 95.0761 | 97.1689 | 97.5056 | 97.6173 | 97.5144 | 97.2864 | 97.4088 | 95.8559 | 97.6306 | 97.9239 | 98.0164 | 97.9176 | 97.5194 | 97.8224 | 2024-04-02
SMA America | SBSE9.6-US-50 {208V} | Y | Y | N | N | N | N | Y* | N | 9.6 kW, 208Vac Grid Support Utility Interactive Inverter | 8.338 | 208 | 97 | Intertek | [3/7/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | [3/19/2025] | No Information Submitted |  | N | N | 11.09 |  |  | 168 | 395 | 480 | 0.834 | 1.668 | 2.501 | 4.169 | 6.253 | 8.338 | 94.37 | 96.75 | 97.07 | 96.78 | 96.43 | 96.14 | 96.5 | 94.42 | 96.64 | 97.24 | 97.24 | 97.13 | 97.01 | 97.03 | 95.41 | 97.46 | 97.84 | 97.77 | 97.62 | 97.42 | 97.57 | 2025-05-01
SMA America | SBSE9.6-US-50 {240V} | Y | Y | N | N | N | N | Y* | N | 9.6 kW, 240Vac Grid Support Utility Interactive Inverter | 9.569 | 240 | 97.5 | Intertek | [3/7/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | [3/19/2025] | No Information Submitted |  | N | N | 11.02 |  |  | 168 | 395 | 480 | 0.957 | 1.914 | 2.871 | 4.784 | 7.176 | 9.569 | 95 | 97.05 | 97.45 | 96.99 | 96.66 | 96.31 | 96.76 | 94.88 | 97.25 | 97.61 | 97.59 | 97.47 | 97.33 | 97.39 | 95.9 | 97.74 | 97.98 | 98.02 | 97.96 | 97.73 | 97.87 | 2025-05-01
SMA America | SBSE11.5-US-50 {208V} | Y | Y | N | N | N | N | Y* | N | 11.5 kW, 208Vac Grid Support Utility Interactive Inverter | 10.053 | 208 | 97 | Intertek | [3/7/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | [3/19/2025] | No Information Submitted |  | N | N | 11.04 |  |  | 200 | 405 | 480 | 1.005 | 2.011 | 3.016 | 5.026 | 7.54 | 10.053 | 94.82 | 97.1 | 97.35 | 96.92 | 96.6 | 96.26 | 96.7 | 94.41 | 97.1 | 97.21 | 97.31 | 97.13 | 96.93 | 97.06 | 95.96 | 97.65 | 97.82 | 97.7 | 97.52 | 97.18 | 97.52 | 2025-05-01
SMA America | SBSE11.5-US-50 {240V} | Y | Y | N | N | N | N | Y* | N | 11.5 kW, 240Vac Grid Support Utility Interactive Inverter | 11.483 | 240 | 97.5 | Intertek | [3/7/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | [3/19/2025] | No Information Submitted |  | N | N | 10.97 |  |  | 200 | 405 | 480 | 1.148 | 2.297 | 3.445 | 5.742 | 8.613 | 11.483 | 95.08 | 97.15 | 97.47 | 97.19 | 96.84 | 96.47 | 96.91 | 95.75 | 97.38 | 97.48 | 97.59 | 97.43 | 97.25 | 97.39 | 96.41 | 97.94 | 98.01 | 97.99 | 97.82 | 97.57 | 97.82 | 2025-05-01
SMA America | STPS27US-20 {208V} | N | Y | N | N | N | N | N | N | 27 kW, 208 Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 27 | 208 | 95.5 | UL | [2/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 17.602 |  |  | 200 | 775 | 980 | 2.718 | 5.435 | 8.153 | 13.588 | 20.382 | 27.176 | 91.7 | 94.26 | 94.82 | 94.92 | 94.33 | 93.3 | 94.35 | 96.52 | 97.15 | 97.26 | 96.73 | 96.52 | 95.91 | 96.65 | 91.44 | 95.5 | 96.01 | 96.32 | 95.65 | 95.2 | 95.63 | 2024-07-11
SMA America | SI27-US208-20 {208V} | N | Y | N | N | N | N | Y* |  | 27 kW, 208 Vac Grid Support Utility Interactive Inverter | 27.1759 | 208 | 96 | UL | [2/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2025-11-26 |  |  | N | N | 17.602 |  |  | 200 | 775 | 980 | 2.7176 | 5.4352 | 8.1528 | 13.588 | 20.3819 | 27.1759 | 91.6979 | 94.2587 | 94.8166 | 94.924 | 94.3279 | 93.2979 | 94.3515 | 96.5186 | 97.1464 | 97.2571 | 96.7254 | 96.515 | 95.9064 | 96.6495 | 91.4377 | 95.4994 | 96.0111 | 96.3164 | 95.6487 | 95.197 | 95.6339 | 2026-06-01 |  | Y | N | N | N | N | N | Y | N | No Information Submitted
SMA America | STPS60US-20 {480V} | N | Y | N | N | N | N | N | N | 60 kW, 480 Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 60 | 480 | 98 | UL | [2/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 17.33 |  |  | 415 | 775 | 980 | 6.041 | 12.083 | 18.124 | 30.207 | 45.311 | 60.414 | 95.43 | 97.57 | 97.42 | 97.57 | 97.32 | 96.83 | 97.3 | 96.87 | 98.06 | 98.04 | 98.36 | 98.12 | 97.77 | 98.09 | 96.51 | 98.16 | 98.1 | 98.15 | 98.08 | 97.78 | 98.02 | 2024-07-11
SMA America | SI60-US480-20 {480V} | N | Y | N | N | N | N | Y* |  | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 60.4144 | 480 | 98 | UL | [2/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | UL | 2025-11-26 |  |  | N | N | 17.33 |  |  | 415 | 775 | 980 | 6.0414 | 12.0829 | 18.1243 | 30.2072 | 45.3108 | 60.4144 | 95.4301 | 97.5667 | 97.415 | 97.5744 | 97.3247 | 96.8343 | 97.2998 | 96.8663 | 98.0574 | 98.0413 | 98.3586 | 98.1209 | 97.7724 | 98.0905 | 96.5089 | 98.1626 | 98.1004 | 98.1477 | 98.081 | 97.778 | 98.0234 | 2026-06-01 |  | Y | N | N | N | N | N | Y | N | No Information Submitted
SMA America | SCS 2475-US {385V} | N | N | Y | Y | Y | N | N | N | 2475 kVA, 385 Vac, 3 phase Grid Support Utility Interactive Battery Inverter | 2078.89 | 385 | 97 | No Information Submitted | No Information Submitted | UL | [03/25/2020] | [05.01.15.R] | 2021-08-23 | [03/25/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on Eaton 34.5kV transformer. | Y | N | 297 |  |  | 577 | 673 | 950 | 207.889 | 415.778 | 623.667 | 1039.445 | 1559.168 | 2078.89 | 96.63 | 97.68 | 97.8 | 97.69 | 97.33 | 96.68 | 97.42 | 96.07 | 97.38 | 97.58 | 97.53 | 97.21 | 96.57 | 97.25 | 94.45 | 96.53 | 96.96 | 97.05 | 96.73 | 96.18 | 96.69 | 2021-08-23
SMA America | SC 2660 UP-US 600V 2566A {600V} | Y | Y | Y | Y | Y | N | N | N | 2616 kW, 600 Vac, 3 Phase Grid Support Utility Interactive PV Inverter with liquid-immersed distribution transformer. | 2616.157 | 600 | 97.5 | UL | [12/15/2022] | UL | [12/15/2022] | [09.00.35.R] | 2023-06-01 | [12/15/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 252.66 |  |  | 880 | 970 | 1200 | 261.6157 | 523.2314 | 784.8471 | 1308.0785 | 1962.1178 | 2616.157 | 96.7266 | 97.7505 | 97.8883 | 97.6512 | 97.2701 | 96.5949 | 97.3928 | 96.4802 | 97.6455 | 97.8062 | 97.5795 | 97.1869 | 96.4804 | 97.303 | 95.8007 | 97.2842 | 97.5299 | 97.4109 | 97.0243 | 96.3333 | 97.0956 | 2023-06-01
SMA America | SC 2800 UP-US 630V 2566A {630V} | Y | Y | Y | Y | Y | N | N | N | 2747 kW, 600 Vac, 3 Phase Grid Support Utility Interactive PV Inverter with liquid-immersed distribution transformer. | 2747.472 | 630 | 97.5 | UL | [12/15/2022] | UL | [12/15/2022] | [09.00.35.R] | 2023-06-01 | [12/15/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 247.1 |  |  | 921 | 1000 | 1200 | 274.7472 | 549.4944 | 824.2416 | 1373.736 | 2060.604 | 2747.472 | 96.7339 | 97.7847 | 97.9214 | 97.732 | 97.3221 | 96.6649 | 97.4468 | 96.5234 | 97.6802 | 97.8378 | 97.6565 | 97.2468 | 96.562 | 97.3622 | 95.9377 | 97.3937 | 97.6166 | 97.504 | 97.11 | 96.4357 | 97.1871 | 2023-06-01
SMA America | SC 2930 UP-US 660V 2566A {660V} | Y | Y | Y | Y | Y | N | N | N | 2930 KVA, 660 Vac, Grid Support Utility Interactive Inverter connected to grid via a 2630 kVA medium voltage transformer. | 2841.88 | 660 | 97.5 | UL | [12/15/2022] | UL | [12/15/2022] | [09.00.35R] | 2023-02-21 | [12/15/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 247.96 |  |  | 962 | 1030 | 1200 | 284.188 | 568.376 | 852.564 | 1420.94 | 2131.41 | 2841.88 | 96.7417 | 97.8244 | 97.9663 | 97.7423 | 97.3866 | 96.7362 | 97.4944 | 96.5595 | 97.7327 | 97.8875 | 97.6725 | 97.3054 | 96.6327 | 97.4102 | 96.0753 | 97.4928 | 97.7086 | 97.5669 | 97.1962 | 96.5348 | 97.2725 | 2023-02-21
SMA America | SC 3060 UP-US 690V 2566A {690V} | Y | Y | Y | Y | Y | N | N | N | 2618 kW, 600 Vac, 3 Phase Grid Support Utility Interactive PV Inverter with liquid-immersed distribution transformer. | 2951.143 | 690 | 97.5 | UL | [12/15/2022] | UL | [12/15/2022] | [09.00.35.R] | 2023-06-01 | [12/15/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 255.77 |  |  | 1003 | 1062 | 1200 | 295.1143 | 590.2286 | 885.3429 | 1475.5715 | 2213.3573 | 2951.143 | 96.7455 | 97.8341 | 97.9875 | 97.7846 | 97.4312 | 96.797 | 97.5332 | 96.588 | 97.7464 | 97.9211 | 97.7151 | 97.3553 | 96.698 | 97.4548 | 96.2041 | 97.566 | 97.7733 | 97.6338 | 97.271 | 96.6148 | 97.3467 | 2023-06-01
SMA America | SC 4000 UP-US 600V 3850A {600V} | Y | N | Y | Y | Y | N | N | N | 4000 kVA, 600 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter | 3650.134 | 600 | 98.5 | No Information Submitted | No Information Submitted | UL | [09/06/2019] | [06.00.33.R] | 2020-04-21 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 453.5 |  |  | 880 | 970 | 1200 | 365.0134 | 730.0268 | 1095.0402 | 1825.067 | 2737.6005 | 3650.134 | 98.2807 | 98.7001 | 98.7205 | 98.6249 | 98.4911 | 98.1606 | 98.5322 | 98.0525 | 98.5891 | 98.6273 | 98.5552 | 98.3953 | 98.0229 | 98.4341 | 97.3227 | 98.2881 | 98.4129 | 98.4176 | 98.2202 | 97.8437 | 98.2334 | 2020-04-21
SMA America | SC 4200 UP-US 630V 3850A {630V} | Y | N | Y | Y | Y | N | N | N | 4200 kVA, 630 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter | 3832.828 | 630 | 98.5 | No Information Submitted | No Information Submitted | UL | [09/06/2019] | [06.00.33.R] | 2020-04-21 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 451.8 |  |  | 921 | 1001 | 1200 | 383.2828 | 766.5656 | 1149.8484 | 1916.414 | 2874.621 | 3832.828 | 98.2694 | 98.7021 | 98.6674 | 98.6466 | 98.5287 | 98.2119 | 98.5526 | 97.9903 | 98.5997 | 98.6622 | 98.5939 | 98.4546 | 98.0872 | 98.4791 | 97.504 | 98.3658 | 98.3947 | 98.4009 | 98.3081 | 97.9519 | 98.2909 | 2020-04-21
SMA America | SC 4400 UP-US 660V 3850A {660V} | Y | N | Y | Y | Y | N | N | N | 4400 kVA, 660 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter | 4017.113 | 660 | 98.5 | No Information Submitted | No Information Submitted | UL | [09/06/2019] | [06.00.33.R] | 2020-04-21 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 465.17 |  |  | 962 | 1032 | 1200 | 401.7113 | 803.4226 | 1205.1339 | 2008.5565 | 3012.8347 | 4017.113 | 98.287 | 98.7337 | 98.7105 | 98.7078 | 98.6023 | 98.295 | 98.616 | 98.1038 | 98.6371 | 98.6292 | 98.6406 | 98.5024 | 98.149 | 98.5198 | 97.5982 | 98.4496 | 98.5884 | 98.4873 | 98.3886 | 98.0401 | 98.3873 | 2020-04-21
SMA America | SC 4600 UP-US 690V 3850A {690V} | Y | N | Y | Y | Y | N | N | N | 4600 kVA, 690 Vac, 3 phase Grid Support Utility Interactive PV and Battery Inverter | 4198.235 | 690 | 98.5 | No Information Submitted | No Information Submitted | UL | [09/06/2019] | [06.00.33.R] | 2020-04-21 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 471.07 |  |  | 1003 | 1062 | 1200 | 419.8235 | 839.647 | 1259.4705 | 2099.1175 | 3148.6762 | 4198.235 | 98.2728 | 98.7421 | 98.7243 | 98.7352 | 98.6471 | 98.3477 | 98.6497 | 98.1499 | 98.6747 | 98.6863 | 98.6911 | 98.5653 | 98.2147 | 98.5776 | 97.7407 | 98.5298 | 98.644 | 98.5955 | 98.4551 | 98.1264 | 98.466 | 2020-04-21
SolarEdge Technologies Ltd. | SE3000H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.0 kW, 240 Vac HD-Wave technology hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 2.962 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 0 |  |  | 360 | 395 | 480 | 0.3 | 0.6 | 0.9 | 1.6 | 2.1 | 2.8 | 95.67 | 98.01 | 98.63 | 99.01 | 99.19 | 99.19 | 98.89 | 95.39 | 97.88 | 98.54 | 98.96 | 99.16 | 99.16 | 98.83 | 95.93 | 98.04 | 98.57 | 99 | 99.08 | 99.17 | 98.83 | 2024-09-23 | 2025-07-01
SolarEdge Technologies Ltd. | SE3800H-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.25 kW, 208 Vac HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 3.255 | 208 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | N | N | 4.12 |  |  | 360 | 395 | 480 | 0.3255 | 0.651 | 0.9765 | 1.6275 | 2.4413 | 3.255 | 89.795 | 99.3907 | 99.3812 | 99.2769 | 99.0026 | 98.7791 | 98.7455 | 92.1061 | 99.3518 | 99.377 | 99.2454 | 98.986 | 98.7542 | 98.8189 | 95.5802 | 99.4287 | 99.3924 | 99.2524 | 98.9976 | 98.7297 | 98.9699 | 2025-07-01 | 2025-08-01
SolarEdge Technologies Ltd. | NX3800T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.33 kW, 208 Vac Grid Support Utility Interactive Inverter | 3.33 | 208 | 98 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.33296 | 0.66592 | 0.99888 | 1.6648 | 2.4972 | 3.3296 | 93.4328 | 97.002 | 97.904 | 98.587 | 98.9016 | 98.945 | 98.4043 | 93.0028 | 96.7768 | 97.7436 | 98.4956 | 98.8352 | 98.908 | 98.3003 | 91.7688 | 96.19 | 97.312 | 98.2424 | 98.662 | 98.7662 | 98.0178 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE3800H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 3.747 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [04/02/2020] | [2.0.820] | 2018-10-15 | [04/02/2020] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 0 |  |  | 360 | 395 | 480 | 0.3 | 0.8 | 1.2 | 2 | 2.8 | 3.6 | 96.56 | 98.4 | 98.82 | 99.18 | 99.19 | 99.2 | 99 | 96.34 | 98.3 | 98.75 | 99.14 | 99.16 | 99.12 | 98.95 | 96.72 | 98.57 | 98.82 | 99.07 | 99.17 | 99.08 | 98.97 | 2024-09-23 | 2025-07-01
SolarEdge Technologies Ltd. | SE3800A-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 3.79 | 240 | 98 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.507] | 2018-10-15 | [6/7/2017] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 2.24 |  |  | 360 | 400 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.84 | 3.79 | 96.1 | 97.6 | 98 | 98.1 | 98.1 | 98.2 | 98 | 95.7 | 97.3 | 97.8 | 98.1 | 98 | 98.2 | 97.9 | 94.6 | 96.8 | 97.5 | 97.9 | 97.9 | 97.8 | 97.6 | 2024-09-23
SolarEdge Technologies Ltd. | NX3800T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 3.84 kW, 240 Vac Grid Support Utility Interactive Inverter | 3.84 | 240 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 0.38396 | 0.76793 | 1.1519 | 1.9198 | 2.8797 | 3.8396 | 95.8904 | 98.106 | 98.149 | 98.7118 | 98.9438 | 99.0086 | 98.6389 | 95.5838 | 97.9452 | 97.9922 | 98.6262 | 98.8862 | 98.9632 | 98.549 | 94.8538 | 97.5384 | 97.6382 | 98.4694 | 98.7356 | 98.8414 | 98.3382 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | NX5000T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 4.3 kW, 208 Vac Grid Support Utility Interactive Inverter | 4.3 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.43 | 0.86 | 1.29 | 2.15 | 3.225 | 4.3 | 94.33 | 97.39 | 98.15 | 98.73 | 98.92 | 98.94 | 98.53 | 93.96 | 97.19 | 98.01 | 98.64 | 98.87 | 98.91 | 98.44 | 92.9 | 96.67 | 97.64 | 98.42 | 98.72 | 98.78 | 98.2 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE5000H-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4.97 kW, 208 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 4.979 | 208 | 98.5 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 4.51 |  |  | 360 | 395 | 480 | 0.4 | 1 | 1.6 | 2.7 | 3.6 | 4.9 | 96.58 | 98.34 | 98.72 | 98.82 | 98.82 | 98.91 | 98.7 | 96.34 | 98.22 | 98.64 | 98.76 | 98.77 | 98.64 | 98.62 | 95.89 | 97.99 | 98.46 | 98.68 | 98.7 | 98.57 | 98.51 | 2025-07-01
SolarEdge Technologies Ltd. | NX5000T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 4.99 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.99 | 240 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.904 |  |  | 370 | 395 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.749 | 4.999 | 96.96 | 98.28 | 98.53 | 98.88 | 98.98 | 98.97 | 98.79 | 96.72 | 98.14 | 98.42 | 98.81 | 98.93 | 98.93 | 98.72 | 96.13 | 97.79 | 98.16 | 98.69 | 98.82 | 98.84 | 98.56 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | NX5700T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 4.99 kW, 208 Vac Grid Support Utility Interactive Inverter | 4.99 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.49899 | 0.99797 | 1.497 | 2.4949 | 3.7424 | 4.9899 | 95.533 | 97.9198 | 98.4648 | 98.9132 | 98.9548 | 98.9416 | 98.698 | 95.2344 | 97.7554 | 98.356 | 98.8382 | 98.917 | 98.9062 | 98.6272 | 94.3994 | 97.3232 | 98.0848 | 98.6696 | 98.7984 | 98.8096 | 98.4366 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE5700H-US {208V} | Y | Y | N | N | N | N | Y* |  | 4.99 kW, 208 Vac, 1-phase, Grid Support Utility Interactive Inverter | 4.99 | 208 | 98.5 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2019-12-16 |  |  | N | N | 5.71 |  |  | 360 | 395 | 460 | 0.4993 | 0.99859 | 1.4979 | 2.4965 | 3.7447 | 4.993 | 96.0984 | 98.1874 | 98.6054 | 98.7944 | 98.8246 | 98.7232 | 98.646 | 95.7494 | 98.0414 | 98.5188 | 98.746 | 98.7856 | 98.6894 | 98.5818 | 95.305 | 97.886 | 98.391 | 98.6788 | 98.7096 | 98.6182 | 98.483 | 2025-09-22
SolarEdge Technologies Ltd. | SE5000H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 5.052 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 4.52 |  |  | 360 | 395 | 480 | 0.4 | 1 | 1.6 | 2.7 | 3.6 | 4.9 | 96.65 | 98.42 | 98.79 | 99 | 98.97 | 99.11 | 98.84 | 96.38 | 98.28 | 98.7 | 98.94 | 98.92 | 98.86 | 98.76 | 96.03 | 98.07 | 98.57 | 98.87 | 98.87 | 98.81 | 98.68 | 2025-07-01
SolarEdge Technologies Ltd. | SE6000H-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.05 kW, 208 Vac HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 5.054 | 208 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | N | N | 4.52 |  |  | 360 | 395 | 480 | 0.5054 | 1.0108 | 1.5162 | 2.527 | 3.7905 | 5.054 | 96.6546 | 98.421 | 98.7873 | 99.0003 | 98.9676 | 99.1108 | 98.8401 | 96.3757 | 98.2834 | 98.7004 | 98.9384 | 98.9206 | 98.8604 | 98.7612 | 96.0285 | 98.0689 | 98.5658 | 98.8689 | 98.8702 | 98.8054 | 98.6764 | 2025-07-01
SolarEdge Technologies Ltd. | NX6000T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.2 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.2 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.2 |  |  | 370 | 395 | 450 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 95.56 | 97.93 | 98.5 | 98.89 | 98.97 | 98.93 | 98.7 | 95.25 | 97.77 | 98.39 | 98.83 | 98.93 | 98.89 | 98.63 | 94.42 | 97.35 | 98.09 | 98.66 | 98.8 | 98.8 | 98.44 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE5700H-US {240V} | Y | Y | N | N | N | N | Y* | Y | 5.7 kW, 240 Vac, 1-phase, Grid Support Utility Interactive Inverter, with PCS functionality. | 5.7 | 240 | 99 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2023-09-13 | 2023-12-01 |  | N | N | 4.51 |  |  | 360 | 395 | 480 | 0.57 | 1.14 | 1.71 | 2.85 | 4.275 | 5.7 | 97.18 | 98.62 | 98.91 | 98.96 | 98.96 | 99 | 98.87 | 96.96 | 98.52 | 98.83 | 98.9 | 98.91 | 98.97 | 98.8 | 96.66 | 98.33 | 98.71 | 98.84 | 98.86 | 98.72 | 98.72 | 2023-12-01 | 2025-07-01
SolarEdge Technologies Ltd. | NX5700T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.76 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.76 | 240 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 0.57593 | 1.1519 | 1.7278 | 2.8797 | 4.3195 | 5.7593 | 97.1958 | 98.1446 | 98.6468 | 98.9328 | 99.0058 | 98.9938 | 98.8313 | 96.9622 | 98.0012 | 98.549 | 98.8746 | 98.9594 | 98.9646 | 98.7648 | 96.3848 | 97.6476 | 98.313 | 98.7374 | 98.8688 | 98.8804 | 98.6147 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | NX6000T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 6 | 240 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.904 |  |  | 370 | 395 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 97.21 | 98.28 | 98.63 | 98.93 | 99 | 98.98 | 98.83 | 96.98 | 98.15 | 98.53 | 98.87 | 98.96 | 98.95 | 98.77 | 96.42 | 97.81 | 98.29 | 98.74 | 98.86 | 98.86 | 98.62 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE6000H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, 1-phase, HD-Wave technology hybrid Grid Support Utility Interactive Inverter, with PCS functionality. | 6.046 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.525] | 2018-10-15 | [01/17/2018] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 4.52 |  |  | 360 | 395 | 480 | 0.5 | 1.3 | 1.9 | 3 | 4.3 | 5.8 | 97.17 | 98.61 | 98.9 | 98.95 | 98.95 | 98.98 | 98.96 | 96.95 | 98.51 | 98.82 | 98.89 | 98.9 | 98.95 | 98.79 | 96.65 | 98.32 | 98.7 | 98.83 | 98.85 | 98.71 | 98.7 | 2017-07-01 | 2025-07-01
SolarEdge Technologies Ltd. | SE7600H-US {208V} | Y | Y | N | N | N | N | Y* |  | 6.59 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter | 6.59 | 208 | 98.5 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2019-12-16 |  |  | N | N | 5.71 |  |  | 360 | 395 | 460 | 0.65918 | 1.3184 | 1.9775 | 3.2959 | 4.9438 | 6.5918 | 97.0038 | 98.4596 | 98.7174 | 98.8268 | 98.6934 | 98.4912 | 98.6349 | 96.7882 | 98.361 | 98.6352 | 98.7766 | 98.6706 | 98.4698 | 98.5878 | 96.481 | 98.2284 | 98.5526 | 98.6966 | 98.6182 | 98.4124 | 98.5115 | 2025-09-22
SolarEdge Technologies Ltd. | NX7600T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.65 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.65 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.66492 | 1.3298 | 1.9948 | 3.3246 | 4.9869 | 6.6492 | 96.573 | 98.3252 | 98.7826 | 98.9396 | 98.9402 | 98.8222 | 98.7898 | 96.3114 | 98.2062 | 98.7028 | 98.8978 | 98.9112 | 98.7916 | 98.7382 | 95.6876 | 97.8886 | 98.3998 | 98.7664 | 98.8094 | 98.7146 | 98.5756 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE7600H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, with PCS functionality. | 7.616 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [04/02/2020] | [2.0.820] | 2018-10-15 | [04/02/2020] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 4.52 |  |  | 360 | 395 | 480 | 0.7 | 1.6 | 2.4 | 3.6 | 5.5 | 7.3 | 97.72 | 98.8 | 98.97 | 98.97 | 99.04 | 98.73 | 98.94 | 97.52 | 98.7 | 98.91 | 98.93 | 99.02 | 98.69 | 98.89 | 97.24 | 98.57 | 98.83 | 98.87 | 98.75 | 98.71 | 98.71 | 2017-07-01 | 2025-07-01
SolarEdge Technologies Ltd. | SE7600A-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive PV and Battery Inverter | 7.625 | 240 | 97.5 | No Information Submitted | No Information Submitted | Intertek | [6/7/2017] | [2.52.507] | 2018-10-15 | [6/7/2017] | 2020-01-21 | Intertek | 2019-12-16 | 2020-01-21 |  | Y | N | 2.16 |  |  | 360 | 400 | 480 | 0.7625 | 1.525 | 2.288 | 3.813 | 5.719 | 7.625 | 97 | 97.9 | 98 | 97.9 | 97.7 | 97.3 | 97.7 | 96.6 | 97.8 | 97.9 | 97.9 | 97.6 | 97.3 | 97.7 | 95.7 | 97.4 | 97.6 | 97.6 | 97.5 | 97.1 | 97.5 | 2020-01-21
SolarEdge Technologies Ltd. | NX7600T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 7.68 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.68 | 240 | 99 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 0.76789 | 1.5358 | 2.3037 | 3.8394 | 5.7592 | 7.6789 | 97.8732 | 98.55 | 98.832 | 99.0034 | 98.9984 | 98.9066 | 98.9075 | 97.6892 | 98.4318 | 98.7504 | 98.958 | 98.9606 | 98.881 | 98.8536 | 97.2498 | 98.1646 | 98.5614 | 98.8644 | 98.8864 | 98.823 | 98.7381 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | NX9600T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 8.32 kW, 208 Vac Grid Support Utility Interactive Inverter | 8.32 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.8319 | 1.6638 | 2.4957 | 4.1595 | 6.2393 | 8.319 | 97.2646 | 98.5754 | 98.879 | 98.9498 | 98.8478 | 98.673 | 98.7873 | 97.0328 | 98.488 | 98.8118 | 98.9178 | 98.8232 | 98.656 | 98.745 | 96.4846 | 98.2328 | 98.6462 | 98.7732 | 98.7394 | 98.5662 | 98.6111 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | NX10000T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 8.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 8.6 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.85995 | 1.7199 | 2.5799 | 4.2998 | 6.4496 | 8.5995 | 97.3222 | 98.6092 | 98.9072 | 98.9602 | 98.8338 | 98.6492 | 98.7882 | 97.1264 | 98.5116 | 98.8468 | 98.9284 | 98.8138 | 98.6296 | 98.75 | 96.5894 | 98.2678 | 98.6914 | 98.7858 | 98.7288 | 98.535 | 98.618 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE10000H-US {208V} | Y | Y | N | N | N | N | Y* |  | 8.69 kW, 208 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter | 8.69 | 208 | 98.5 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2019-12-16 |  |  | N | N | 5.71 |  |  | 360 | 395 | 460 | 0.86943 | 1.7389 | 2.6083 | 4.3471 | 6.5207 | 8.6943 | 97.7128 | 98.7498 | 98.8938 | 98.8578 | 98.5768 | 98.3014 | 98.6342 | 97.533 | 98.669 | 98.835 | 98.8134 | 98.5516 | 98.2296 | 98.5896 | 97.3006 | 98.5502 | 98.7378 | 98.7388 | 98.509 | 98.176 | 98.5218 | 2025-09-22
SolarEdge Technologies Ltd. | SE9600H-US {240V} | Y | Y | N | N | N | N | N | N | 9.6 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 9.5685 | 240 | 99 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 6 |  |  | 360 | 395 | 460 | 0.95685 | 1.9137 | 2.8705 | 4.7842 | 7.1764 | 9.5685 | 97.9766 | 98.9434 | 99.0536 | 98.9918 | 98.7734 | 98.5294 | 98.8173 | 97.829 | 98.895 | 99.031 | 98.9754 | 98.7742 | 98.5144 | 98.8025 | 97.595 | 98.809 | 98.9796 | 98.9562 | 98.7668 | 98.49 | 98.7735 | 2025-07-01
SolarEdge Technologies Ltd. | SE9600H-US {208V} | Y | Y | N | N | N | N | N | N | 9.57 kW, 208 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter | 9.5783 | 208 | 98.5 | Intertek | [9/23/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.71 |  |  | 360 | 395 | 460 | 0.95783 | 1.9157 | 2.8735 | 4.7892 | 7.1838 | 9.5783 | 97.9964 | 98.9244 | 98.9876 | 98.846 | 98.53 | 98.1958 | 98.6329 | 97.873 | 98.877 | 98.9758 | 98.8386 | 98.5382 | 98.1722 | 98.6258 | 97.6706 | 98.8012 | 98.9366 | 98.8252 | 98.5256 | 98.1514 | 98.5987 | 2025-07-01
SolarEdge Technologies Ltd. | NX9600T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.6 | 240 | 99 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 0.95996 | 1.9199 | 2.8799 | 4.7998 | 7.1997 | 9.5996 | 98.2748 | 98.6916 | 98.9372 | 99.0048 | 98.936 | 98.7794 | 98.9041 | 98.1384 | 98.6026 | 98.8864 | 98.9708 | 98.9134 | 98.7596 | 98.868 | 97.7824 | 98.4554 | 98.7438 | 98.8868 | 98.8568 | 98.7118 | 98.7792 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | NX11500T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 9.98 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.98 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 0.99797 | 1.9959 | 2.9939 | 4.9899 | 7.4848 | 9.9797 | 97.6712 | 98.8168 | 98.937 | 98.9454 | 98.7348 | 98.4884 | 98.7525 | 97.5094 | 98.7378 | 98.891 | 98.9178 | 98.718 | 98.4718 | 98.7211 | 97.04 | 98.432 | 98.743 | 98.8082 | 98.6416 | 98.4134 | 98.6028 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE10000H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 9.994 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.820] | 2021-02-22 | [01/17/2018] | 2021-02-22 | Intertek | 2019-12-16 | 2022-02-22 |  | N | N | 6 |  |  | 360 | 395 | 480 | 0.999 | 1.999 | 2.998 | 4.997 | 7.496 | 9.994 | 97.86 | 98.83 | 98.94 | 99.23 | 98.95 | 98.63 | 98.94 | 97.69 | 98.74 | 98.88 | 99.18 | 98.91 | 98.55 | 98.89 | 97.44 | 98.54 | 98.68 | 98.7 | 98.62 | 98.1 | 98.57 | 2022-02-22 | 2025-07-01
SolarEdge Technologies Ltd. | NX10000T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10 | 240 | 99 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 0.99989 | 1.9998 | 2.9997 | 4.9995 | 7.4992 | 9.9989 | 98.3682 | 98.7656 | 98.981 | 99.0276 | 98.9244 | 98.7572 | 98.9143 | 98.2162 | 98.6898 | 98.9082 | 98.9892 | 98.9104 | 98.7336 | 98.879 | 97.8728 | 98.5094 | 98.7818 | 98.9028 | 98.8538 | 98.6872 | 98.7907 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE11400H-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10.00 kW, 208 Vac, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 10.001 | 208 | 98.5 | Intertek | [9/23/2024] | Intertek | [04/02/2020] | [2.0.820] | 2021-02-22 | [04/02/2020] | 2021-02-22 | Intertek | 2019-12-16 | 2022-02-22 |  | N | N | 5.71 |  |  | 360 | 395 | 480 | 1.0001 | 2.0001 | 3.0002 | 5.0003 | 7.5004 | 10.0006 | 97.7682 | 98.7285 | 98.8322 | 99.0698 | 98.6681 | 98.1747 | 98.7145 | 97.6539 | 98.6608 | 98.771 | 98.9695 | 98.5754 | 98.0908 | 98.6248 | 97.439 | 98.5357 | 98.6979 | 98.696 | 98.62 | 98.0972 | 98.5677 | 2022-02-22 | 2025-07-01
SolarEdge Technologies Ltd. | NX13000T-US {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.2 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.2 | 208 | 98.5 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.64 |  |  | 370 | 395 | 450 | 1.1199 | 2.2399 | 3.3598 | 5.5996 | 8.3994 | 11.1993 | 97.9458 | 98.8688 | 98.9528 | 98.9134 | 98.6726 | 98.319 | 98.7198 | 97.76 | 98.7988 | 98.9108 | 98.8884 | 98.6586 | 98.3134 | 98.6909 | 97.3184 | 98.62 | 98.7836 | 98.8 | 98.561 | 98.2568 | 98.5759 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | SE11400H-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac, HD-Wave technology Grid Support Utility Interactive Inverter, with PCS functionality. | 11.393 | 240 | 99 | Intertek | [9/23/2024] | Intertek | [01/17/2018] | [2.0.820] | 2021-02-22 | [01/17/2018] | 2021-02-22 | Intertek | 2019-12-16 | 2022-02-22 |  | N | N | 6 |  |  | 360 | 395 | 480 | 1.139 | 2.279 | 3.418 | 5.697 | 8.545 | 11.393 | 97.88 | 98.84 | 98.95 | 99.16 | 98.82 | 98.41 | 98.85 | 97.91 | 98.83 | 98.93 | 99.17 | 98.83 | 98.4 | 98.85 | 97.42 | 98.63 | 98.79 | 98.82 | 98.8 | 98.39 | 98.72 | 2022-02-22 | 2025-07-01
SolarEdge Technologies Ltd. | NX11500T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.52 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.52 | 240 | 99 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 1.1519 | 2.3038 | 3.4557 | 5.7595 | 8.6392 | 11.5189 | 97.9908 | 98.8782 | 99.0282 | 99.0236 | 98.868 | 98.6448 | 98.8742 | 97.8258 | 98.7932 | 98.9742 | 98.995 | 98.8484 | 98.623 | 98.8393 | 98.1314 | 98.616 | 98.8468 | 98.908 | 98.7902 | 98.58 | 98.7762 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarEdge Technologies Ltd. | NX13000T-US {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 13 kW, 240 Vac Grid Support Utility Interactive Inverter | 13 | 240 | 99 | Intertek | [2/27/2026] | Intertek | [2/27/2026] | [2.40.5015] | 2026-05-11 | [2/27/2026] | 2026-05-11 | Intertek | 2026-02-23 |  |  | Y | N | 5.9 |  |  | 370 | 395 | 450 | 1.2999 | 2.5998 | 3.8998 | 6.4996 | 9.7494 | 12.9992 | 98.2158 | 98.9684 | 99.0612 | 99.0086 | 98.7758 | 98.4758 | 98.8312 | 98.0694 | 98.9106 | 99.0222 | 98.9846 | 98.7688 | 98.4686 | 98.8086 | 97.7142 | 98.7448 | 98.9074 | 98.9096 | 98.7254 | 98.4376 | 98.7321 | 2026-05-11 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SolarJuice American Inc. | S4A-H60 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 5.57 | 240 | 94 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 25 |  |  | 240 | 335 | 425 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 93.8526 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 94.3396 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888 | 94.1609 | 2021-07-12
SolarJuice American Inc. | S4A-A60 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter | 5.732 | 240 | 94 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 25 |  |  | 360 | 430 | 500 | 0.5732 | 1.1464 | 1.7196 | 2.866 | 4.299 | 5.732 | 86.1104 | 91.3885 | 93.3511 | 94.7498 | 94.8381 | 95.0506 | 94.1302 | 85.9074 | 91.6775 | 93.5459 | 95.0932 | 94.9449 | 95.3118 | 94.3016 | 85.5756 | 91.8187 | 93.6918 | 94.5668 | 94.968 | 95.2094 | 94.2095 | 2021-07-12
SolarJuice American Inc. | S4A-H70 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 6.666 | 240 | 94.5 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 25 |  |  | 290 | 360 | 425 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 94.3168 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 94.5405 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836 | 94.4389 | 2021-07-12
SolarJuice American Inc. | S4A-A70 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 7 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter | 6.68 | 240 | 95 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 25 |  |  | 280 | 390 | 500 | 0.668 | 1.336 | 2.004 | 3.34 | 5.01 | 6.68 | 88.2924 | 93.4839 | 94.8825 | 95.53 | 95.1135 | 94.4759 | 94.7871 | 88.5639 | 92.5762 | 94.6548 | 95.5514 | 95.4278 | 95.2339 | 94.9342 | 87.5631 | 92.1581 | 94.2612 | 95.3928 | 95.2266 | 94.6733 | 94.658 | 2021-07-12
SolarJuice American Inc. | S4A-H76 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 7.642 | 240 | 95.5 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 44 |  |  | 304 | 402 | 500 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 95.4058 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 95.4118 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449 | 96.1997 | 2021-07-12
SolarJuice American Inc. | S4A-A76 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter | 7.832 | 240 | 95.5 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 49.5 |  |  | 320 | 375 | 430 | 0.78321 | 1.5664 | 2.3496 | 3.916 | 5.874 | 7.8321 | 91.4312 | 94.9622 | 95.6242 | 95.751 | 95.4401 | 94.9759 | 95.32 | 92.2952 | 94.8694 | 95.6095 | 95.9358 | 95.7414 | 95.332 | 95.5645 | 92.7618 | 95.0616 | 95.7149 | 95.9028 | 95.7632 | 95.4369 | 95.6153 | 2021-07-12
SolarJuice American Inc. | S4A-H86 {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 8.604 | 240 | 96 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 40 |  |  | 258 | 379 | 500 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 95.2714 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 95.7814 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922 | 96.1906 | 2021-07-12
SolarJuice American Inc. | S4A-A86 {240V} | N | N | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter | 8.613 | 240 | 95.5 | No Information Submitted | No Information Submitted | CSA Group | [05/14/2021] | [V1.07] | 2021-07-12 | [05/14/2021] | 2021-07-12 | CSA Group | 2021-06-22 | 2021-07-12 |  | N | N | 42 |  |  | 363 | 396.5 | 430 | 0.8613 | 1.7226 | 2.5839 | 4.3065 | 6.4597 | 8.613 | 93.0135 | 95.2805 | 95.8088 | 95.9296 | 95.6312 | 95.1894 | 95.5709 | 92.8584 | 95.2474 | 95.8068 | 95.9989 | 95.7474 | 95.3227 | 95.6455 | 92.5757 | 95.1198 | 95.7234 | 95.9883 | 95.8346 | 95.4524 | 95.6683 | 2021-07-12
Sol-Ark | 5K-120V/8K-230V-1P {120V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 120 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 4.7871 | 120 | 96.5 | TUV Rheinland | [7/8/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-01-18 | 2024-05-13 |  | N | N | 11.7 |  |  | 200 | 312.5 | 425 | 0.47871 | 0.95742 | 1.4361 | 2.3936 | 3.5903 | 4.7871 | 94.422 | 96.792 | 97.112 | 96.518 | 95.908 | 95.576 | 96.1487 | 94.832 | 97.148 | 97.55 | 96.838 | 96.532 | 95.88 | 96.6486 | 94.292 | 96.732 | 97.052 | 96.49 | 95.946 | 95.406 | 96.1391 | 2022-11-14 | 2024-05-13
Sol-Ark | 5K-120V/8K-230V-1P {240V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 7.9703 | 240 | 96.5 | TUV Rheinland | [7/8/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-01-18 | 2024-05-13 |  | N | N | 19.3 |  |  | 200 | 312.5 | 425 | 0.79703 | 1.5941 | 2.3911 | 3.9851 | 5.9777 | 7.9703 | 94.432 | 96.79 | 97.304 | 96.606 | 96.184 | 95.546 | 96.3353 | 94.82 | 97.058 | 97.568 | 96.802 | 96.458 | 95.99 | 96.6045 | 94.374 | 96.7 | 97.082 | 96.412 | 95.828 | 95.31 | 96.0607 | 2022-11-14 | 2024-05-13
Sol-Ark | Limitless 10K-LV {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 8.635 | 208 | 96.5 | SGS | [5/26/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.29 |  |  | 250 | 370 | 425 | 0.863 | 1.727 | 2.59 | 4.317 | 6.476 | 8.635 | 93.23 | 95.85 | 97.56 | 97.12 | 96.74 | 96.5 | 96.72 | 93.44 | 95.99 | 97.57 | 97.08 | 96.45 | 96.25 | 96.56 | 93.32 | 95.87 | 97.57 | 96.95 | 96.68 | 96.43 | 96.66 | 2024-08-01
Sol-Ark | Sol-Ark-12K-P {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 8.818 | 208 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-12-23 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.88181 | 1.7636 | 2.6454 | 4.409 | 6.6136 | 8.8181 | 91.4663 | 94.7338 | 95.331 | 97.2779 | 97.1712 | 96.8243 | 96.6054 | 91.6795 | 94.935 | 95.479 | 97.4054 | 97.2156 | 96.9037 | 96.696 | 91.8809 | 94.8955 | 95.3141 | 97.2443 | 96.8807 | 97.0098 | 96.4763 | 2019-12-23 | 2023-04-11
Sol-Ark | Sol-Ark-9k-48-ST {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter | 8.818 | 208 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-12-23 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.88181 | 1.7636 | 2.6454 | 4.409 | 6.6136 | 8.8181 | 91.4663 | 94.7338 | 95.331 | 97.2779 | 97.1712 | 96.8243 | 96.6054 | 91.6795 | 94.935 | 95.479 | 97.4054 | 97.2156 | 96.9037 | 96.696 | 91.8809 | 94.8955 | 95.3141 | 97.2443 | 96.8807 | 97.0098 | 96.4763 | 2019-12-23 | 2023-04-11
Sol-Ark | Sol-Ark-8k-48-ST {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 KW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 8.8181 | 240 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-08-01 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.88181 | 1.7636 | 2.6454 | 4.409 | 6.6136 | 8.8181 | 91.4663 | 94.7338 | 95.331 | 97.2779 | 97.1712 | 96.8243 | 96.6054 | 91.6795 | 94.935 | 95.479 | 97.4054 | 97.2156 | 96.9037 | 96.696 | 91.8809 | 94.8955 | 95.3141 | 97.2443 | 96.8807 | 97.0098 | 96.4763 | 2019-08-01 | 2023-04-11
Sol-Ark | Sol-Ark-12K-P {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 8.982 | 240 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-12-23 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.89822 | 1.7964 | 2.6947 | 4.4911 | 6.7366 | 8.9822 | 91.8174 | 94.8883 | 95.5678 | 97.1321 | 96.9715 | 97.1243 | 96.5341 | 91.6365 | 94.9704 | 95.6697 | 97.5151 | 97.4122 | 97.0522 | 96.8536 | 91.5513 | 95.0486 | 95.8243 | 97.5595 | 97.2251 | 97.0494 | 96.7827 | 2019-12-23 | 2023-04-11
Sol-Ark | Sol-Ark-9k-48-ST {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 8.982 | 240 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-12-23 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.89822 | 1.7964 | 2.6947 | 4.4911 | 6.7366 | 8.9822 | 91.8174 | 94.8883 | 95.5678 | 97.1321 | 96.9715 | 97.1243 | 96.5341 | 91.6365 | 94.9704 | 95.6697 | 97.5151 | 97.4122 | 97.0522 | 96.8536 | 91.5513 | 95.0486 | 95.8243 | 97.5595 | 97.2251 | 97.0494 | 96.7827 | 2019-12-23 | 2023-04-11
Sol-Ark | Sol-Ark-8k-48-ST {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8 KW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 8.9822 | 208 | 96.5 | SGS | [8/8/2022] | SGS | [10/22/2020] | [Ver1585] | 2019-08-01 | [10/09/2019] | 2020-07-21 | PCTEST | 2020-06-11 | 2020-07-21 |  | N | N | 13.4 |  |  | 240 | 370 | 425 | 0.89822 | 1.7964 | 2.6947 | 4.4911 | 6.7366 | 8.9822 | 91.8174 | 94.8883 | 95.5678 | 97.1321 | 96.9715 | 97.1243 | 96.5341 | 91.6365 | 94.9704 | 95.6697 | 97.5151 | 97.4122 | 97.0522 | 96.8536 | 91.5513 | 95.0486 | 95.8243 | 97.5595 | 97.2251 | 97.0494 | 96.7827 | 2019-08-01 | 2023-04-11
Sol-Ark | Limitless 10K-LV {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter | 9.97 | 240 | 96.5 | SGS | [5/26/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 5.29 |  |  | 250 | 370 | 425 | 0.997 | 1.994 | 2.991 | 4.985 | 7.478 | 9.97 | 93.43 | 96.24 | 97.47 | 96.99 | 96.46 | 96.22 | 96.55 | 93.61 | 96.05 | 97.51 | 97.35 | 96.99 | 96.27 | 96.91 | 93.49 | 96.09 | 97.58 | 97.2 | 96.8 | 96.21 | 96.78 | 2024-08-01
Sol-Ark | 12K-2P-LL {240V} | Y | Y | N | N | N | N | Y* |  | 12 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.9628 | 240 | 97 | TUV Rheinland of North America | [5/29/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 46161 |  |  | N | N | 9.45 |  |  | 250 | 337.5 | 425 | 1.1963 | 2.3926 | 3.5888 | 5.9814 | 8.9721 | 11.9628 | 94.45 | 96.14 | 96.65 | 96.83 | 96.76 | 96.58 | 96.63 | 96.43 | 97.6 | 97.91 | 98.02 | 97.67 | 97.55 | 97.71 | 94.82 | 96.68 | 97.18 | 97.52 | 97.51 | 97.31 | 97.31 | 2026-08-11 |  | Y | N | N | N | N | N | N | N | N
Sol-Ark | 12K-2P-LL {208V} | Y | Y | N | N | N | N | Y* |  | 12 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.9853 | 208 | 97.5 | TUV Rheinland of North America | [5/29/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 46161 |  |  | N | N | 8 |  |  | 250 | 337.5 | 425 | 1.1985 | 2.3971 | 3.5956 | 5.9927 | 8.989 | 11.9853 | 94.72 | 96.27 | 96.66 | 96.79 | 96.68 | 96.6 | 96.6 | 96.4 | 97.59 | 97.83 | 97.99 | 97.83 | 97.68 | 97.79 | 94.81 | 96.69 | 97.18 | 97.58 | 97.61 | 97.35 | 97.38 | 2026-08-11 |  | Y | N | N | N | N | N | N | N | N
Sol-Ark | Limitless 15K-LV {208V} | Y | Y | N | N | N | N | Y* | N | 15 kW, 208 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 13.01 | 208 | 96.5 | SGS | [7/27/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-01-12 | No Information Submitted |  | N | N | 21.2 |  |  | 200 | 320 | 425 | 1.3014 | 2.6029 | 3.9043 | 6.5072 | 9.7608 | 13.0145 | 93.374 | 95.8088 | 97.681 | 96.9864 | 96.551 | 96.3162 | 96.6021 | 93.6666 | 95.9928 | 97.712 | 97.172 | 96.6578 | 96.4328 | 96.7281 | 93.469 | 95.9614 | 97.63 | 97.0532 | 96.5632 | 96.3156 | 96.6279 | 2022-08-11 | 2023-02-13
Sol-Ark | Limitless 15K-LV {240V} | Y | Y | N | N | N | N | Y* | N | 15 kW, 240 Vac Grid Support Utility Interactive PV and Battery Inverter with PCS functionality | 15.04 | 240 | 96.5 | SGS | [7/27/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-01-12 | No Information Submitted |  | N | N | 21.2 |  |  | 200 | 320 | 425 | 1.5044 | 3.0087 | 4.5131 | 7.5219 | 11.2828 | 15.0437 | 93.582 | 95.8704 | 97.6968 | 97.062 | 96.661 | 96.4142 | 96.6945 | 93.693 | 96.1402 | 97.7394 | 97.2496 | 96.7728 | 96.4702 | 96.819 | 93.6154 | 95.9584 | 97.6952 | 97.089 | 96.7006 | 96.4 | 96.726 | 2022-08-11 | 2023-02-13
Sol-Ark | Limitless 18K-2P-LV {208V} | Y | Y | N | N | N | N | Y* | N | 18 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 15.5502 | 208 | 97 | TUV Rheinland of North America | [5/8/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-05-06 | No Information Submitted |  | N | N | 1.37 |  |  | 250 | 337.5 | 425 | 1.555 | 3.11 | 4.6651 | 7.7751 | 11.6626 | 15.5502 | 94.24 | 95.4 | 95.96 | 96.512 | 97.268 | 96.914 | 96.7201 | 94.416 | 95.61 | 96.41 | 97.272 | 97.802 | 97.296 | 97.2533 | 94.276 | 95.506 | 96.258 | 96.876 | 97.468 | 97.092 | 96.9539 | 2025-08-21 | 2025-11-03
Sol-Ark | Limitless 18K-2P-LV {240V} | Y | Y | N | N | N | N | Y* | N | 18 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter with PCS functionality. | 17.9442 | 240 | 97 | TUV Rheinland of North America | [5/8/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2025-05-06 | No Information Submitted |  | N | N | 1.37 |  |  | 250 | 337.5 | 425 | 1.7944 | 3.5888 | 5.3833 | 8.9721 | 13.4582 | 17.9442 | 94.422 | 95.664 | 96.208 | 96.748 | 97.318 | 96.952 | 96.8483 | 94.668 | 95.798 | 96.458 | 97.09 | 97.824 | 97.302 | 97.2523 | 94.432 | 95.7 | 96.304 | 96.902 | 97.482 | 97.042 | 96.9857 | 2025-08-21 | 2025-11-03
Sol-Ark | 30K-3P-208V {120V} | Y | Y | N | N | N | N | Y* | Y | 30 kW, 120 Vac Grid Support Interactive Hybrid Inverter with PCS functionality. | 30.025 | 120 | 96.5 | TUV Rheinland of North America | [3/19/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-01-23 | 2024-05-13 |  | N | N | 31.9 |  |  | 270 | 385 | 500 | 3.0025 | 6.005 | 9.0076 | 15.0126 | 22.5189 | 30.0252 | 94.448 | 96.852 | 97.246 | 96.534 | 96.014 | 95.534 | 96.2263 | 94.814 | 97.092 | 97.534 | 96.824 | 96.44 | 95.92 | 96.5935 | 94.344 | 96.68 | 97.14 | 96.444 | 95.836 | 95.342 | 96.078 | 2023-05-22 | 2025-07-11
Sol-Ark | 60K-3P-480V {277V} | Y | Y | N | N | N | N | Y* | Y | 60 kW, 277 Vac Grid Support Interactive Hybrid Inverter with PCS functionality. | 60.05 | 277 | 97.5 | TUV Rheinland of North America | [3/17/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | TUV Rheinland | 2024-01-23 | 2024-05-13 |  | N | N | 5.29 |  |  | 540 | 695 | 850 | 6.005 | 12.01 | 18.015 | 30.025 | 45.0375 | 60.05 | 94.422 | 98.066 | 98.602 | 97.896 | 97.376 | 96.784 | 97.5191 | 94.748 | 98.504 | 98.834 | 98.228 | 97.77 | 97.26 | 97.8842 | 94.32 | 98.036 | 98.376 | 97.826 | 97.196 | 96.688 | 97.3715 | 2024-01-02 | 2025-07-11
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-HYB-3.8K-G2 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 3.805 | 240 | 97 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 175.4 | 337.9 | 499.5 | 0.38047 | 0.76094 | 1.1414 | 1.9023 | 2.8535 | 3.8047 | 92.7832 | 95.3783 | 96.1221 | 96.5347 | 96.5885 | 96.4765 | 96.3029 | 94.0899 | 96.2193 | 96.885 | 97.3248 | 97.4661 | 97.4427 | 97.1681 | 91.4685 | 96.3171 | 97.1281 | 97.4492 | 97.6556 | 97.6619 | 97.2348 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-AC-3.8K-G2 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 3.8 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 3.81 | 240 | 95 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 75.6 | 262.8 | 450 | 0.38096 | 0.76192 | 1.1429 | 1.9048 | 2.8572 | 3.8096 | 89.5518 | 92.8592 | 93.7168 | 94.0193 | 93.779 | 93.4412 | 93.5901 | 88.0285 | 94.0298 | 95.5866 | 96.4637 | 96.7473 | 96.8458 | 96.0688 | 87.5436 | 93.8997 | 95.4778 | 96.3759 | 96.8597 | 97.0133 | 96.0793 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-HYB-5.0K-G2 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 5.003 | 240 | 97.5 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 229.9 | 363.7 | 499.9 | 0.50027 | 1.0005 | 1.5008 | 2.5013 | 3.752 | 5.0027 | 94.4996 | 96.2452 | 96.7656 | 97.0082 | 96.9837 | 96.852 | 96.8198 | 95.7546 | 97.2612 | 97.4657 | 97.7249 | 97.7239 | 97.6405 | 97.5871 | 94.8122 | 97.071 | 97.3678 | 97.6591 | 97.7118 | 97.6279 | 97.5072 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-AC-5.0K-G2 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 5.0 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 5.03 | 240 | 96 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 100.4 | 275.5 | 449.9 | 0.503 | 1.006 | 1.509 | 2.515 | 3.7725 | 5.03 | 91.3524 | 94.1166 | 94.7534 | 95.0269 | 94.8695 | 94.5367 | 94.6936 | 91.1403 | 95.3189 | 96.2129 | 96.6996 | 96.9043 | 96.9328 | 96.4699 | 89.7548 | 95.137 | 96.0905 | 96.6798 | 97.0081 | 97.0805 | 96.449 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-6.0-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Transformerless Hybrid Grid Support Utility Interactive Inverter with PV arc detector | 5.57 | 240 | 94 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2020-11-23 | [10/21/2020] | 2020-11-23 | Intertek | 2020-09-11 | 2020-11-23 |  | N | N | 25 |  |  | 240 | 335 | 425 | 0.575 | 1.15 | 1.725 | 2.875 | 4.3125 | 5.75 | 86.8697 | 91.4943 | 93.1975 | 94.2773 | 94.5286 | 94.4195 | 93.8526 | 86.5347 | 91.7192 | 93.5326 | 94.7608 | 95.116 | 95.1425 | 94.3396 | 85.9441 | 91.0558 | 93.1196 | 94.5569 | 95.0559 | 95.1888 | 94.1609 | 2020-11-23
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Fit-6.0-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Transformerless Bi-directional Grid Support Utility Interactive Battery Inverter | 5.732 | 240 | 94 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2020-11-23 | [10/21/2020] | 2020-11-23 | Intertek | 2020-09-11 | 2020-11-23 |  | N | N | 25 |  |  | 360 | 430 | 500 | 0.5732 | 1.1464 | 1.7196 | 2.866 | 4.299 | 5.732 | 86.1104 | 91.3885 | 93.3511 | 94.7498 | 94.8381 | 95.0506 | 94.1302 | 85.9074 | 91.6775 | 93.5459 | 95.0932 | 94.9449 | 95.3118 | 94.3016 | 85.5756 | 91.8187 | 93.6918 | 94.5668 | 94.968 | 95.2094 | 94.2095 | 2020-11-23
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-HYB-6.0K-G2 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 6.017 | 240 | 97.5 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 277 | 388.3 | 498.7 | 0.60166 | 1.2033 | 1.805 | 3.0083 | 4.5125 | 6.0166 | 95.0593 | 96.7801 | 97.1224 | 97.2712 | 97.1927 | 97.0029 | 97.0853 | 96.3129 | 97.458 | 97.7478 | 97.8566 | 97.7758 | 97.645 | 97.7085 | 94.8068 | 96.9441 | 97.5246 | 97.7657 | 97.6571 | 97.5829 | 97.5106 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-AC-6.0K-G2 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 6.0 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 6.035 | 240 | 96 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 121.1 | 285.1 | 449.9 | 0.60349 | 1.207 | 1.8105 | 3.0174 | 4.5262 | 6.0349 | 92.4354 | 94.7517 | 95.3064 | 95.4957 | 95.3529 | 94.967 | 95.2113 | 92.582 | 95.9751 | 96.5614 | 96.8385 | 96.9642 | 96.915 | 96.6622 | 91.2831 | 95.6242 | 96.3268 | 96.8112 | 97.0461 | 97.0813 | 96.6106 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-HYB-7.6K-G2 {208V} | Y | Y | Y | Y | Y | Y | N |  | 7.6 kW, 208 Vac Grid Support Utility-interactive Inverter | 6.6364 | 208 | 97.5 | CSA Group | [12/9/2024] | CSA Group | [12/9/2024] | [V1.05, V1.03, V1.10] | 2025-09-22 | [12/9/2024] | 2025-09-22 | No Information Submitted | No Information Submitted |  |  | N | N | 5.44 |  |  | 235 | 360 | 440 | 0.66364 | 1.3273 | 1.9909 | 3.3182 | 4.9773 | 6.6364 | 95.5469 | 96.9555 | 97.2605 | 97.4473 | 96.9905 | 96.707 | 97.0452 | 96.695 | 97.8863 | 97.9782 | 97.9395 | 97.7927 | 97.5992 | 97.7969 | 96.1754 | 97.2803 | 97.9229 | 97.937 | 97.7703 | 97.6911 | 97.7314 | 2025-09-22 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-7.0-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7.0 kW, 240 Vac Transformerless Hybrid Grid Support Utility Interactive Inverter with PV arc detector | 6.666 | 240 | 94.5 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2020-11-23 | [10/21/2020] | 2020-11-23 | Intertek | 2020-09-11 | 2020-11-23 |  | N | N | 25 |  |  | 290 | 360 | 425 | 0.6666 | 1.3332 | 1.9998 | 3.333 | 4.9995 | 6.666 | 88.1925 | 92.48 | 93.8642 | 94.7282 | 94.8593 | 94.6616 | 94.3168 | 87.895 | 92.5522 | 93.9857 | 94.9393 | 95.146 | 95.0843 | 94.5405 | 87.1883 | 91.8403 | 93.6653 | 94.8124 | 95.1882 | 95.1836 | 94.4389 | 2020-11-23
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Fit-7.0-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 7.0 kW, 240 Vac Transformerless Bi-directional Grid Support Utility Interactive Battery Inverter | 6.68 | 240 | 95 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2020-11-23 | [10/21/2020] | 2020-11-23 | Intertek | 2020-09-11 | 2020-11-23 |  | N | N | 25 |  |  | 280 | 390 | 500 | 0.668 | 1.336 | 2.004 | 3.34 | 5.01 | 6.68 | 88.2924 | 93.4839 | 94.8825 | 95.53 | 95.1135 | 94.4759 | 94.7871 | 88.5639 | 92.5762 | 94.6548 | 95.5514 | 95.4278 | 95.2339 | 94.9342 | 87.5631 | 92.1581 | 94.2612 | 95.3928 | 95.2266 | 94.6733 | 94.658 | 2020-11-23
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-HYB-7.6K-G2 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 7.593 | 240 | 97.5 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 234.1 | 365.5 | 498.4 | 0.75932 | 1.5186 | 2.278 | 3.7966 | 5.6949 | 7.5932 | 95.5301 | 96.9355 | 97.2078 | 97.319 | 96.9534 | 96.7056 | 96.9905 | 96.6677 | 97.8357 | 97.9705 | 97.937 | 97.774 | 97.5335 | 97.7786 | 96.0575 | 97.25 | 97.8206 | 97.8742 | 97.7481 | 97.6184 | 97.6843 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-AC-7.6K-G2 {240V} | N | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Grid support utility-interactive Power Conversion System, with Backup Interface (BI), A1-BI-200-G2. Capable of PCS funcitonality | 7.601 | 240 | 96.5 | CSA Group | [12/9/2024] | CSA Group | [4/26/2022] | [V1.05, V1.03, V1.10] | 2022-09-01 | [4/26/2022] | 2022-09-01 | CSA Group | 2022-06-09 | 2022-09-01 |  | N | N | 1.2 |  |  | 149.7 | 300.1 | 449.8 | 0.76005 | 1.5201 | 2.2801 | 3.8003 | 5.7004 | 7.6005 | 93.371 | 95.3712 | 95.8107 | 95.8958 | 95.6855 | 95.3202 | 95.6182 | 94.124 | 96.454 | 96.8095 | 97.0054 | 96.9852 | 96.8122 | 96.8187 | 93.4413 | 96.1689 | 96.7056 | 96.9797 | 97.0796 | 97.0065 | 96.819 | 2022-09-01 | 2026-01-12
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-7.6-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 7.642 | 240 | 95.5 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2019-06-01 | [10/21/2020] | 2021-01-21 | Intertek | 2020-09-11 | 2021-01-21 |  | N | N | 44 |  |  | 304 | 402 | 500 | 0.76415 | 1.5283 | 2.2925 | 3.8208 | 5.7311 | 7.6415 | 91.7074 | 94.5729 | 95.3432 | 95.7328 | 95.6501 | 95.3856 | 95.4058 | 90.5573 | 94.4837 | 95.2373 | 95.7522 | 95.7552 | 95.573 | 95.4118 | 93.4546 | 95.5643 | 96.1659 | 96.4887 | 96.3651 | 96.1449 | 96.1997 | 2019-06-03 | 2021-01-21
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Fit-7.6-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter | 7.832 | 240 | 95.5 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2019-06-01 | [10/21/2020] | 2021-01-21 | Intertek | 2020-09-11 | 2021-01-21 |  | N | N | 49.5 |  |  | 320 | 375 | 430 | 0.78321 | 1.5664 | 2.3496 | 3.916 | 5.874 | 7.8321 | 91.4312 | 94.9622 | 95.6242 | 95.751 | 95.4401 | 94.9759 | 95.32 | 92.2952 | 94.8694 | 95.6095 | 95.9358 | 95.7414 | 95.332 | 95.5645 | 92.7618 | 95.0616 | 95.7149 | 95.9028 | 95.7632 | 95.4369 | 95.6153 | 2019-06-03 | 2021-01-21
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Hybrid-8.6-US {240V} | Y | N | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, hybrid PV and Battery Grid Support Utility Interactive Inverter with PV arc detector | 8.604 | 240 | 96 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2019-06-01 | [10/21/2020] | 2021-01-21 | Intertek | 2020-09-11 | 2021-01-21 |  | N | N | 40 |  |  | 258 | 379 | 500 | 0.86044 | 1.7209 | 2.5813 | 4.3022 | 6.4533 | 8.6044 | 92.6993 | 94.5399 | 95.2978 | 95.6136 | 95.4241 | 94.9404 | 95.2714 | 92.8441 | 95.2894 | 95.9701 | 96.1825 | 95.8716 | 95.5293 | 95.7814 | 93.6941 | 95.7768 | 96.2745 | 96.5194 | 96.2968 | 95.8922 | 96.1906 | 2019-06-03 | 2021-01-21
SolaX Power Network Technology (Zhe jiang) Co., Ltd. | A1-Fit-8.6-US {240V} | N | N | Y | Y | Y | Y | Y* | Y | 8.6 kW, 240 Vac, 1-phase, transformerless, bidirectional, battery Grid Support Utility Interactive Inverter | 8.613 | 240 | 95.5 | No Information Submitted | No Information Submitted | CSA Group | [10/21/2020] | [V1.07, V1.03] | 2019-06-01 | [10/21/2020] | 2021-01-21 | Intertek | 2020-09-11 | 2021-01-21 |  | N | N | 42 |  |  | 363 | 396.5 | 430 | 0.8613 | 1.7226 | 2.5839 | 4.3065 | 6.4597 | 8.613 | 93.0135 | 95.2805 | 95.8088 | 95.9296 | 95.6312 | 95.1894 | 95.5709 | 92.8584 | 95.2474 | 95.8068 | 95.9989 | 95.7474 | 95.3227 | 95.6455 | 92.5757 | 95.1198 | 95.7234 | 95.9883 | 95.8346 | 95.4524 | 95.6683 | 2019-06-03 | 2021-01-21
SPITZER ENERGY COMPANY | SPZ 7.5KW-LV {208V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter | 5.02 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 92.68 | 95.27 | 95.93 | 96.35 | 96.16 | 95.99 | 95.98 | 93.57 | 95.86 | 96.53 | 97.03 | 97.08 | 96.97 | 96.8 | 93.73 | 95.93 | 96.5 | 96.81 | 96.9 | 96.81 | 96.65 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 7.5KW-LV {240V} | Y | Y | N | N | N | N | Y* | Y | 5 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 5.04 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.504 | 1.008 | 1.512 | 2.52 | 3.78 | 5.04 | 92.99 | 95.51 | 96.13 | 96.56 | 96.34 | 96.22 | 96.18 | 93.67 | 95.99 | 96.75 | 97.31 | 97.43 | 97.38 | 97.1 | 93.79 | 96.14 | 96.61 | 96.98 | 97.24 | 97.24 | 96.92 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 9KW-LV {208V} | Y | Y | N | N | N | N | Y* | Y | 6 kW, 208, Grid Support Utility Interactive PV and Battery Inverter | 6.124 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.612 | 1.225 | 1.837 | 3.062 | 4.593 | 6.124 | 91.51 | 94.38 | 95.44 | 96.15 | 96.2 | 96.02 | 95.81 | 93.61 | 95.95 | 96.7 | 97.16 | 97.14 | 97.02 | 96.88 | 93.01 | 95.45 | 96.32 | 96.9 | 96.93 | 96.76 | 96.61 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 9KW-LV {240V} | Y | Y | N | N | N | N | Y* | Y | 6 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 6.149 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 19.2 |  |  | 200 | 360 | 480 | 0.615 | 1.23 | 1.845 | 3.075 | 4.612 | 6.149 | 91.6 | 94.45 | 95.46 | 96.26 | 96.41 | 96.35 | 95.97 | 93.87 | 96.14 | 96.88 | 97.38 | 97.49 | 97.42 | 97.18 | 92.69 | 95.45 | 96.41 | 97.1 | 97.3 | 97.27 | 96.87 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 12KW-LV-A {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 7.647 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.529 | 2.294 | 3.824 | 5.735 | 7.647 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 89.75 | 96.08 | 96.79 | 97.16 | 96.97 | 96.77 | 96.65 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 12KW-LV-A {208V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter | 7.648 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.765 | 1.53 | 2.294 | 3.824 | 5.736 | 7.648 | 92.95 | 95.54 | 96.21 | 96.65 | 96.45 | 96.19 | 96.26 | 93.74 | 96.07 | 96.79 | 97.16 | 96.97 | 96.77 | 96.8 | 94.06 | 96.23 | 96.77 | 97.12 | 96.91 | 96.7 | 96.78 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 12KW-LV-B {240V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 8.047 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.805 | 1.609 | 2.414 | 4.024 | 6.035 | 8.047 | 92.95 | 95.55 | 96.22 | 96.65 | 96.45 | 96.19 | 96.27 | 93.75 | 96.08 | 96.8 | 97.17 | 96.97 | 96.77 | 96.81 | 94.07 | 96.24 | 96.77 | 97.12 | 96.91 | 96.65 | 96.78 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 12KW-LV-B {208V} | Y | Y | N | N | N | N | Y* | Y | 8 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter | 8.06 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 17.78 |  |  | 200 | 360 | 480 | 0.806 | 1.612 | 2.418 | 4.03 | 6.045 | 8.06 | 92.85 | 95.45 | 96.11 | 96.55 | 96.35 | 96.09 | 96.17 | 93.65 | 95.98 | 96.69 | 97.06 | 96.87 | 96.67 | 96.71 | 93.97 | 96.14 | 96.67 | 97.02 | 96.81 | 96.55 | 96.68 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 15KW-LV-B {240V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 10.14 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.028 | 3.042 | 5.07 | 7.605 | 10.14 | 93.05 | 95.58 | 96.24 | 96.66 | 96.45 | 96.2 | 96.28 | 93.72 | 96.07 | 96.82 | 97.15 | 96.96 | 96.78 | 96.8 | 94.05 | 96.25 | 96.79 | 97.12 | 96.92 | 96.66 | 96.79 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 15KW-LV {240V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 240 Vac, Grid Support Utility Interactive PV and Battery Inverter | 10.147 | 240 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.015 | 2.029 | 3.044 | 5.074 | 7.61 | 10.147 | 93 | 95.58 | 96.22 | 96.66 | 96.46 | 96.2 | 96.28 | 93.79 | 96.1 | 96.81 | 97.16 | 96.97 | 96.77 | 96.81 | 94.11 | 96.27 | 96.78 | 97.13 | 96.92 | 96.66 | 96.79 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 15KW-LV {208V} | Y | Y | N | N | N | N | Y* | Y | 10 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter | 10.186 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.89 | 95.48 | 96.13 | 96.56 | 96.36 | 96.1 | 96.18 | 93.7 | 96.01 | 96.71 | 97.07 | 96.88 | 96.67 | 96.72 | 94.02 | 96.16 | 96.68 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-08-01 | 2025-01-13
SPITZER ENERGY COMPANY | SPZ 15KW-LV-B {208V} | Y | Y | N | N | N | N | Y* | Y | 11.4 kW, 208 Vac, Grid Support Utility Interactive PV and Battery Inverter | 10.186 | 208 | 96.5 | SGS | [6/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2024-09-29 | 2025-01-13 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.019 | 2.037 | 3.056 | 5.093 | 7.639 | 10.186 | 92.91 | 95.48 | 96.12 | 96.56 | 96.36 | 96.1 | 96.18 | 93.66 | 96.02 | 96.72 | 97.07 | 96.88 | 96.68 | 96.72 | 94.07 | 96.17 | 96.67 | 96.99 | 96.82 | 96.56 | 96.68 | 2024-08-01 | 2025-01-13
SRNE Solar Co.,Ltd | HEBP4880U240-Pro {208V} | Y | Y | N | N | N | N | N | N | 8.8 kW, 208 Vac, Grid Support Utility Interactive Inverter | 8.8085 | 208 | 96 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.88085 | 1.7617 | 2.6426 | 4.4043 | 6.6064 | 8.8085 | 94.444 | 95.624 | 96.816 | 96.49 | 97.126 | 95.666 | 96.6999 | 94.382 | 95.75 | 96.022 | 96.526 | 97.2 | 95.958 | 96.6698 | 93.96 | 94.784 | 96.388 | 96.654 | 96.84 | 95.102 | 96.4418 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-8K-UPRO {208V} | Y | Y | N | N | N | N | N | N | 8.8 kW, 208 Vac, Grid Support Utility Interactive Inverter | 8.8085 | 208 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.88085 | 1.7617 | 2.6426 | 4.4043 | 6.6064 | 8.8085 | 94.444 | 95.624 | 96.816 | 96.49 | 97.126 | 95.666 | 96.6999 | 94.382 | 95.75 | 96.022 | 96.526 | 97.2 | 95.958 | 96.6698 | 93.96 | 94.784 | 96.388 | 96.654 | 96.84 | 95.102 | 96.4418 | 2025-06-23
SRNE Solar Co.,Ltd | HESP4880U200-H {208V} | Y | Y | N | N | N | N | N | N | 8 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 8.809 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.881 | 1.762 | 2.643 | 4.404 | 6.606 | 8.809 | 94.44 | 95.62 | 96.82 | 96.49 | 97.13 | 95.67 | 96.7 | 94.38 | 95.75 | 96.02 | 96.53 | 97.2 | 95.96 | 96.67 | 93.96 | 94.78 | 96.39 | 96.65 | 96.84 | 95.1 | 96.44 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-8K-UP {208V} | Y | Y | N | N | N | N | N | N | 8 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 8.809 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.881 | 1.762 | 2.643 | 4.404 | 6.606 | 8.809 | 94.44 | 95.62 | 96.82 | 96.49 | 97.13 | 95.67 | 96.7 | 94.38 | 95.75 | 96.02 | 96.53 | 97.2 | 95.96 | 96.67 | 93.96 | 94.78 | 96.39 | 96.65 | 96.84 | 95.1 | 96.44 | 2024-03-11
SRNE Solar Co.,Ltd | HEBP4880U240-Pro {240V} | Y | Y | N | N | N | N | N | N | 8.8 kW, 240 Vac, Grid Support Utility Interactive Inverter | 8.8096 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.88096 | 1.7619 | 2.6429 | 4.4048 | 6.6072 | 8.8096 | 94.272 | 95.424 | 96.778 | 96.326 | 97.096 | 95.646 | 96.6271 | 93.65 | 95.692 | 96.638 | 96.466 | 97.23 | 96.198 | 96.7268 | 94.002 | 95.676 | 96.698 | 96.354 | 96.548 | 95.556 | 96.3302 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-8K-UPRO {240V} | Y | Y | N | N | N | N | N | N | 8.8 kW, 240 Vac, Grid Support Utility Interactive Inverter | 8.8096 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.88096 | 1.7619 | 2.6429 | 4.4048 | 6.6072 | 8.8096 | 94.272 | 95.424 | 96.778 | 96.326 | 97.096 | 95.646 | 96.6271 | 93.65 | 95.692 | 96.638 | 96.466 | 97.23 | 96.198 | 96.7268 | 94.002 | 95.676 | 96.698 | 96.354 | 96.548 | 95.556 | 96.3302 | 2025-06-23
SRNE Solar Co.,Ltd | HESP4880U200-H {240V} | Y | Y | N | N | N | N | N | N | 8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 8.81 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.881 | 1.762 | 2.643 | 4.405 | 6.607 | 8.81 | 94.27 | 95.42 | 96.78 | 96.33 | 97.1 | 95.65 | 96.63 | 93.65 | 95.69 | 96.64 | 96.47 | 97.23 | 96.2 | 96.73 | 94 | 95.68 | 96.7 | 96.35 | 96.55 | 95.56 | 96.33 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-8K-UP {240V} | Y | Y | N | N | N | N | N | N | 8 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 8.81 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.881 | 1.762 | 2.643 | 4.405 | 6.607 | 8.81 | 94.27 | 95.42 | 96.78 | 96.33 | 97.1 | 95.65 | 96.63 | 93.65 | 95.69 | 96.64 | 96.47 | 97.23 | 96.2 | 96.73 | 94 | 95.68 | 96.7 | 96.35 | 96.55 | 95.56 | 96.33 | 2024-03-11
SRNE Solar Co.,Ltd | HEBP48100U240-Pro {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac, Grid Support Utility Interactive Inverter | 10.0057 | 208 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.5 |  |  | 275 | 362.5 | 450 | 1.0006 | 2.0011 | 3.0017 | 5.0028 | 7.5043 | 10.0057 | 93.636 | 96.268 | 96.57 | 96.558 | 97.164 | 94.944 | 96.6685 | 94.79 | 96.362 | 96.58 | 96.79 | 97.524 | 95.16 | 96.9709 | 93.936 | 96.22 | 96.374 | 96.486 | 96.948 | 95.296 | 96.5426 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-10K-UPRO {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac, Grid Support Utility Interactive Inverter | 10.0057 | 208 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.5 |  |  | 275 | 362.5 | 450 | 1.0006 | 2.0011 | 3.0017 | 5.0028 | 7.5043 | 10.0057 | 93.636 | 96.268 | 96.57 | 96.558 | 97.164 | 94.944 | 96.6685 | 94.79 | 96.362 | 96.58 | 96.79 | 97.524 | 95.16 | 96.9709 | 93.936 | 96.22 | 96.374 | 96.486 | 96.948 | 95.296 | 96.5426 | 2025-06-23
SRNE Solar Co.,Ltd | HESP48100U200-H {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.006 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.5 |  |  | 275 | 362.5 | 450 | 1.001 | 2.001 | 3.002 | 5.003 | 7.504 | 10.006 | 93.64 | 96.27 | 96.57 | 96.56 | 97.16 | 94.94 | 96.67 | 94.79 | 96.36 | 96.58 | 96.79 | 97.52 | 95.16 | 96.97 | 93.94 | 96.22 | 96.37 | 96.49 | 96.95 | 95.3 | 96.54 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-10K-UP {208V} | Y | Y | N | N | N | N | N | N | 10 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.006 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 72.5 |  |  | 275 | 362.5 | 450 | 1.001 | 2.001 | 3.002 | 5.003 | 7.504 | 10.006 | 93.64 | 96.27 | 96.57 | 96.56 | 97.16 | 94.94 | 96.67 | 94.79 | 96.36 | 96.58 | 96.79 | 97.52 | 95.16 | 96.97 | 93.94 | 96.22 | 96.37 | 96.49 | 96.95 | 95.3 | 96.54 | 2024-03-11
SRNE Solar Co.,Ltd | HESP48100U200-H {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 10.008 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.6 |  |  | 275 | 362.5 | 450 | 1.001 | 2.002 | 3.002 | 5.004 | 7.506 | 10.008 | 92.88 | 96.19 | 96.28 | 96.51 | 97.09 | 94.83 | 96.55 | 93.18 | 96.37 | 96.91 | 96.71 | 97.52 | 95.05 | 96.92 | 93.25 | 96.29 | 96.9 | 97.02 | 96.94 | 95.28 | 96.69 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-10K-UP {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 10.008 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.6 |  |  | 275 | 362.5 | 450 | 1.001 | 2.002 | 3.002 | 5.004 | 7.506 | 10.008 | 92.88 | 96.19 | 96.28 | 96.51 | 97.09 | 94.83 | 96.55 | 93.18 | 96.37 | 96.91 | 96.71 | 97.52 | 95.05 | 96.92 | 93.25 | 96.29 | 96.9 | 97.02 | 96.94 | 95.28 | 96.69 | 2024-03-11
SRNE Solar Co.,Ltd | HEBP48100U240-Pro {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac, Grid Support Utility Interactive Inverter | 10.0082 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.6 |  |  | 275 | 362.5 | 450 | 1.0008 | 2.0016 | 3.0025 | 5.0041 | 7.5061 | 10.0082 | 92.884 | 96.19 | 96.28 | 96.506 | 97.094 | 94.834 | 96.5462 | 93.182 | 96.368 | 96.912 | 96.706 | 97.522 | 95.052 | 96.9226 | 93.246 | 96.288 | 96.896 | 97.016 | 96.938 | 95.276 | 96.6861 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-10K-UPRO {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac, Grid Support Utility Interactive Inverter | 10.0082 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.6 |  |  | 275 | 362.5 | 450 | 1.0008 | 2.0016 | 3.0025 | 5.0041 | 7.5061 | 10.0082 | 92.884 | 96.19 | 96.28 | 96.506 | 97.094 | 94.834 | 96.5462 | 93.182 | 96.368 | 96.912 | 96.706 | 97.522 | 95.052 | 96.9226 | 93.246 | 96.288 | 96.896 | 97.016 | 96.938 | 95.276 | 96.6861 | 2025-06-23
SRNE Solar Co.,Ltd | HEBP48114U240-Pro {240V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 240 Vac, Grid Support Utility Interactive Inverter | 10.0082 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73.7 |  |  | 275 | 362.5 | 450 | 1.0008 | 2.0016 | 3.0025 | 5.0041 | 7.5062 | 10.0082 | 94.646 | 95.758 | 95.334 | 96.51 | 97.434 | 95.878 | 96.7148 | 94.21 | 94.914 | 95.268 | 96.412 | 97.364 | 95.408 | 96.5661 | 94.976 | 94.772 | 95.296 | 96.478 | 97.2 | 95.4 | 96.5195 | 2025-06-23
SRNE Solar Co.,Ltd | HEBP48114U240-Pro {208V} | Y | Y | N | N | N | N | N | N | 10.4 kW, 208 Vac, Grid Support Utility Interactive Inverter | 10.009 | 208 | 97 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 73 |  |  | 275 | 362.5 | 450 | 1.0009 | 2.0018 | 3.0027 | 5.0045 | 7.5067 | 10.009 | 94.448 | 95.466 | 96.09 | 96.296 | 97.494 | 95.424 | 96.7472 | 94.858 | 96.006 | 96.29 | 96.748 | 97.216 | 95.398 | 96.7609 | 95.01 | 96.252 | 96.378 | 96.514 | 97.308 | 95.266 | 96.7828 | 2025-06-23
SRNE Solar Co.,Ltd | HESP48120U200-H {208V} | Y | Y | N | N | N | N | N | N | 12 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.397 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.04 | 2.079 | 3.119 | 5.199 | 7.798 | 10.397 | 95.11 | 95.71 | 96.53 | 96.55 | 96.71 | 95.27 | 96.47 | 95.33 | 96.1 | 96.62 | 96.92 | 97.48 | 95.26 | 96.99 | 95.04 | 95.77 | 96.6 | 96.55 | 96.67 | 95.19 | 96.45 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-12K-UP {208V} | Y | Y | N | N | N | N | N | N | 12 kW, 208 Vac Grid Support Utility Interactive Hybrid Inverter | 10.397 | 208 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.04 | 2.079 | 3.119 | 5.199 | 7.798 | 10.397 | 95.11 | 95.71 | 96.53 | 96.55 | 96.71 | 95.27 | 96.47 | 95.33 | 96.1 | 96.62 | 96.92 | 97.48 | 95.26 | 96.99 | 95.04 | 95.77 | 96.6 | 96.55 | 96.67 | 95.19 | 96.45 | 2024-03-11
SRNE Solar Co.,Ltd | HEBP48120U240-Pro {208V} | Y | Y | N | N | N | N | N | N | 10.4 kW, 208 Vac, Grid Support Utility Interactive Inverter | 10.3972 | 208 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.0397 | 2.0794 | 3.1192 | 5.1986 | 7.7979 | 10.3972 | 95.11 | 95.714 | 96.534 | 96.55 | 96.714 | 95.27 | 96.4716 | 95.33 | 96.102 | 96.616 | 96.924 | 97.478 | 95.264 | 96.9928 | 95.036 | 95.774 | 96.604 | 96.55 | 96.668 | 95.186 | 96.4515 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-12K-UPRO {208V} | Y | Y | N | N | N | N | N | N | 10.4 kW, 208 Vac, Grid Support Utility Interactive Inverter | 10.3972 | 208 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.0397 | 2.0794 | 3.1192 | 5.1986 | 7.7979 | 10.3972 | 95.11 | 95.714 | 96.534 | 96.55 | 96.714 | 95.27 | 96.4716 | 95.33 | 96.102 | 96.616 | 96.924 | 97.478 | 95.264 | 96.9928 | 95.036 | 95.774 | 96.604 | 96.55 | 96.668 | 95.186 | 96.4515 | 2025-06-23
SRNE Solar Co.,Ltd | HEBP48120U240-Pro {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac, Grid Support Utility Interactive Inverter | 11.9957 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.1996 | 2.3991 | 3.5987 | 5.9979 | 8.9968 | 11.9957 | 95.452 | 95.688 | 96.376 | 96.392 | 96.504 | 95.226 | 96.3183 | 95.568 | 96.168 | 96.69 | 96.874 | 97.428 | 95.228 | 96.9757 | 95.526 | 95.868 | 96.596 | 96.456 | 96.536 | 95.324 | 96.392 | 2025-06-23
SRNE Solar Co.,Ltd | SEI-12K-UPRO {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac, Grid Support Utility Interactive Inverter | 11.9957 | 240 | 96.5 | Intertek | [3/31/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.1996 | 2.3991 | 3.5987 | 5.9979 | 8.9968 | 11.9957 | 95.452 | 95.688 | 96.376 | 96.392 | 96.504 | 95.226 | 96.3183 | 95.568 | 96.168 | 96.69 | 96.874 | 97.428 | 95.228 | 96.9757 | 95.526 | 95.868 | 96.596 | 96.456 | 96.536 | 95.324 | 96.392 | 2025-06-23
SRNE Solar Co.,Ltd | HESP48120U200-H {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 11.996 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.2 | 2.399 | 3.599 | 5.998 | 8.997 | 11.996 | 95.45 | 95.69 | 96.38 | 96.39 | 96.5 | 95.23 | 96.32 | 95.57 | 96.17 | 96.69 | 96.87 | 97.43 | 95.23 | 96.98 | 95.53 | 95.87 | 96.6 | 96.46 | 96.54 | 95.32 | 96.39 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-12K-UP {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter | 11.996 | 240 | 96.5 | Intertek | [1/25/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.2 | 2.399 | 3.599 | 5.998 | 8.997 | 11.996 | 95.45 | 95.69 | 96.38 | 96.39 | 96.5 | 95.23 | 96.32 | 95.57 | 96.17 | 96.69 | 96.87 | 97.43 | 95.23 | 96.98 | 95.53 | 95.87 | 96.6 | 96.46 | 96.54 | 95.32 | 96.39 | 2024-03-11
SRNE Solar Co.,Ltd | SEI-14K-U3P {208V} | Y | Y | N | N | N | N | N |  | 14 kW, 208 Vac Grid Support Utility Interactive Inverter | 14.0494 | 208 | 96.5 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.17 |  |  | 135 | 330 | 500 | 1.4049 | 2.8099 | 4.2148 | 7.0247 | 10.5371 | 14.0494 | 90.7592 | 94.8305 | 96.3293 | 96.9509 | 96.4563 | 94.4185 | 96.1338 | 91.2047 | 95.1283 | 96.8233 | 97.229 | 97.5506 | 97.0686 | 96.9967 | 93.7014 | 96.4506 | 96.8803 | 97.3064 | 97.0258 | 96.7317 | 96.8909 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HESP48140UH3 {208V} | Y | Y | N | N | N | N | N |  | 14 kW, 208 Vac Grid Support Utility Interactive Inverter | 14.0776 | 208 | 96.5 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.25 |  |  | 135 | 330 | 500 | 1.4078 | 2.8155 | 4.2233 | 7.0388 | 10.5582 | 14.0776 | 90.7593 | 94.8303 | 96.3294 | 96.9509 | 96.4563 | 94.4184 | 96.1338 | 91.2045 | 95.1283 | 96.8233 | 97.229 | 97.5506 | 97.0686 | 96.9967 | 93.2023 | 96.184 | 96.8767 | 97.2949 | 97.1327 | 96.7992 | 96.9147 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48150U320-H {208V} | Y | Y | N | N | N | N | N |  | 15 kW, 208 Vac Grid Support Utility Interactive Inverter | 14.3465 | 208 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.2 |  |  | 135 | 330 | 500 | 1.4347 | 2.8693 | 4.304 | 7.1733 | 10.7599 | 14.3465 | 92.8428 | 95.1741 | 95.8783 | 95.9649 | 96.6641 | 96.1379 | 96.1693 | 94.6874 | 96.3353 | 96.7393 | 96.8266 | 96.585 | 95.2127 | 96.4973 | 95.0317 | 96.4069 | 96.6815 | 96.6871 | 96.3717 | 95.8276 | 96.3961 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-15K-UBP {208V} | Y | Y | N | N | N | N | N |  | 15 kW, 208 Vac Grid Support Utility Interactive Inverter | 14.3489 | 208 | 97 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.4 |  |  | 135 | 330 | 500 | 1.4349 | 2.8698 | 4.3047 | 7.1744 | 10.7617 | 14.3489 | 92.75 | 95.0789 | 95.7825 | 95.8689 | 96.5675 | 96.0418 | 96.0731 | 94.7822 | 96.4317 | 96.8362 | 96.9235 | 96.6817 | 95.1175 | 96.5843 | 96.6056 | 97.9388 | 98.2142 | 98.0917 | 97.7736 | 95.7317 | 97.7527 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48150U320-H {240V} | Y | Y | N | N | N | N | N |  | 15 kW, 240 Vac Grid Support Utility Interactive Inverter | 14.72 | 240 | 96 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 30.7 |  |  | 135 | 330 | 500 | 1.472 | 2.944 | 4.416 | 7.36 | 11.04 | 14.72 | 92.7794 | 94.9734 | 95.6173 | 95.7338 | 96.3459 | 96.0725 | 95.9049 | 93.2574 | 94.7699 | 95.3153 | 95.5413 | 95.5009 | 95.2129 | 95.3464 | 94.8106 | 95.9755 | 96.2892 | 96.3862 | 96.0842 | 95.8115 | 96.1022 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-15K-UBP {240V} | Y | Y | N | N | N | N | N |  | 15 kW, 240 Vac Grid Support Utility Interactive Inverter | 14.72 | 240 | 96 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 30.7 |  |  | 135 | 330 | 500 | 1.472 | 2.944 | 4.416 | 7.36 | 11.04 | 14.72 | 92.7794 | 94.9734 | 95.6173 | 95.7338 | 96.3459 | 96.0725 | 95.9049 | 93.2574 | 94.7699 | 95.3153 | 95.5413 | 95.5009 | 95.2129 | 95.3464 | 94.8106 | 95.9755 | 96.2892 | 96.3862 | 96.0842 | 95.8115 | 96.1022 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48160U340-H {208V} | Y | Y | N | N | N | N | N |  | 16 kW, 208 Vac Grid Support Utility Interactive Inverter | 15.2514 | 208 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.3 |  |  | 150 | 330 | 500 | 1.5251 | 3.0503 | 4.5754 | 7.6257 | 11.4385 | 15.2514 | 92.9262 | 95.2756 | 95.9085 | 95.9546 | 96.3526 | 96.1306 | 96.0137 | 94.1462 | 95.758 | 96.2135 | 96.5445 | 96.5139 | 96.2114 | 96.3366 | 95.6495 | 96.9287 | 97.3307 | 97.243 | 97.0512 | 96.7694 | 97.0487 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-16K-UBP {208V} | Y | Y | N | N | N | N | N |  | 16 kW, 208 Vac Grid Support Utility Interactive Inverter | 15.2564 | 208 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.2 |  |  | 150 | 330 | 500 | 1.5256 | 3.0513 | 4.5769 | 7.6282 | 11.4423 | 15.2564 | 92.8333 | 95.1803 | 95.8126 | 95.8587 | 96.2562 | 96.0345 | 95.9177 | 94.0521 | 95.6623 | 96.1173 | 96.4479 | 96.4174 | 96.1152 | 96.2403 | 95.5539 | 96.8317 | 97.2334 | 97.1457 | 96.9541 | 96.6726 | 96.9517 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48160U340-H {240V} | Y | Y | N | N | N | N | N |  | 16 kW, 240 Vac Grid Support Utility Interactive Inverter | 16.0066 | 240 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 30.7 |  |  | 150 | 330 | 500 | 1.6007 | 3.2013 | 4.802 | 8.0033 | 12.005 | 16.0066 | 92.7875 | 95.0323 | 95.7511 | 95.7573 | 96.1756 | 95.9166 | 95.8312 | 94.1692 | 95.7223 | 96.2244 | 96.5323 | 96.4723 | 96.2198 | 96.3129 | 95.7303 | 96.9006 | 97.338 | 97.2328 | 97.0333 | 96.8243 | 97.0426 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-16K-UBP {240V} | Y | Y | N | N | N | N | N |  | 16 kW, 240 Vac Grid Support Utility Interactive Inverter | 16.0066 | 240 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 30.7 |  |  | 150 | 330 | 500 | 1.6007 | 3.2013 | 4.802 | 8.0033 | 12.005 | 16.0066 | 92.7875 | 95.0323 | 95.7511 | 95.7573 | 96.1756 | 95.9166 | 95.8312 | 94.1692 | 95.7223 | 96.2244 | 96.5323 | 96.4723 | 96.2198 | 96.3129 | 95.7303 | 96.9006 | 97.338 | 97.2328 | 97.0333 | 96.8243 | 97.0426 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-16K-U3P {208V} | Y | Y | N | N | N | N | N |  | 16 kW, 208 Vac Grid Support Utility Interactive Inverter | 16.0641 | 208 | 97 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.19 |  |  | 150 | 330 | 500 | 1.6064 | 3.2128 | 4.8192 | 8.0321 | 12.0481 | 16.0641 | 92.6948 | 95.5918 | 96.6001 | 97.0214 | 97.164 | 96.6119 | 96.7814 | 91.4358 | 94.6242 | 96.7517 | 97.4231 | 97.2836 | 96.827 | 96.8593 | 94.6103 | 96.5373 | 97.1228 | 97.4928 | 97.1187 | 96.8162 | 97.0532 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HESP48160UH3 {208V} | Y | Y | N | N | N | N | N |  | 16 kW, 208 Vac Grid Support Utility Interactive Inverter | 16.0963 | 208 | 97 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.26 |  |  | 150 | 330 | 500 | 1.6096 | 3.2193 | 4.8289 | 8.0481 | 12.0722 | 16.0963 | 92.6949 | 95.5917 | 96.6001 | 97.0216 | 97.164 | 96.6114 | 96.7814 | 91.4358 | 94.6242 | 96.7517 | 97.4232 | 97.2835 | 96.827 | 96.8593 | 94.6086 | 96.537 | 97.1227 | 97.4928 | 97.1187 | 96.8162 | 97.0531 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48180U380-H {208V} | Y | Y | N | N | N | N | N |  | 18 kW, 208 Vac Grid Support Utility Interactive Inverter | 17.0533 | 208 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.3 |  |  | 160 | 330 | 500 | 1.7053 | 3.4107 | 5.116 | 8.5267 | 12.79 | 17.0533 | 93.161 | 95.3666 | 96.0198 | 96.1669 | 95.8692 | 95.3463 | 95.7902 | 94.9542 | 96.6859 | 97.0572 | 97.2953 | 97.0991 | 96.7228 | 97.01 | 95.6412 | 96.9487 | 97.2956 | 97.2485 | 96.718 | 96.692 | 96.8659 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-18K-UBP {208V} | Y | Y | N | N | N | N | N |  | 18 kW, 208 Vac Grid Support Utility Interactive Inverter | 17.0558 | 208 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 39.4 |  |  | 160 | 330 | 500 | 1.7056 | 3.4112 | 5.1167 | 8.5279 | 12.7918 | 17.0558 | 93.0907 | 95.2806 | 95.9282 | 96.2794 | 95.7305 | 95.2509 | 95.7174 | 94.7822 | 96.4317 | 96.8362 | 96.9235 | 96.6817 | 96.6261 | 96.6598 | 96.6056 | 97.9388 | 98.2142 | 98.0917 | 97.7736 | 96.5954 | 97.7959 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HEBP48180U380-H {240V} | Y | Y | N | N | N | N | N |  | 18 kW, 240 Vac Grid Support Utility Interactive Inverter | 17.944 | 240 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 35.6 |  |  | 160 | 330 | 500 | 1.7944 | 3.5888 | 5.3832 | 8.972 | 13.458 | 17.944 | 93.1331 | 95.349 | 96.0269 | 96.2345 | 95.9259 | 95.4615 | 95.8391 | 94.8594 | 96.478 | 96.848 | 97.1595 | 97.1259 | 96.8312 | 96.9618 | 95.7636 | 96.9224 | 97.2501 | 97.2045 | 97.0659 | 96.6714 | 97.0381 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-18K-UBP {240V} | Y | Y | N | N | N | N | N |  | 18 kW, 240 Vac Grid Support Utility Interactive Inverter | 17.944 | 240 | 96.5 | Intertek | [5/15/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 30.7 |  |  | 160 | 330 | 500 | 1.7944 | 3.5888 | 5.3832 | 8.972 | 13.458 | 17.944 | 93.1331 | 95.349 | 96.0269 | 96.2345 | 95.9259 | 95.4615 | 95.8391 | 94.8594 | 96.478 | 96.848 | 97.1595 | 97.1259 | 96.8312 | 96.9618 | 95.7636 | 96.9224 | 97.2501 | 97.2045 | 97.0659 | 96.6714 | 97.0381 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | SEI-18K-U3P {208V} | Y | Y | N | N | N | N | N |  | 18 kW, 208 Vac Grid Support Utility Interactive Inverter | 18.1348 | 208 | 97 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.19 |  |  | 160 | 330 | 500 | 1.8135 | 3.627 | 5.4405 | 9.0674 | 13.6011 | 18.1348 | 91.7859 | 95.455 | 96.451 | 96.7238 | 97.2908 | 96.939 | 96.7414 | 92.6187 | 95.4457 | 96.4775 | 97.2559 | 97.4663 | 97.102 | 96.9903 | 94.4793 | 96.7393 | 97.3627 | 97.561 | 97.4288 | 96.9581 | 97.2726 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SRNE Solar Co.,Ltd | HESP48180UH3 {208V} | Y | Y | N | N | N | N | N |  | 18 kW, 208 Vac Grid Support Utility Interactive Inverter | 18.1711 | 208 | 97 | Intertek | [5/14/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 37.27 |  |  | 160 | 330 | 500 | 1.8171 | 3.6342 | 5.4513 | 9.0856 | 13.6284 | 18.1711 | 91.7861 | 95.4552 | 96.451 | 96.7238 | 97.2908 | 96.8162 | 96.7353 | 92.6187 | 95.4457 | 96.4776 | 97.2558 | 97.4663 | 97.102 | 96.9903 | 94.4812 | 96.7399 | 97.3627 | 97.561 | 97.4287 | 96.9581 | 97.2727 | 2026-09-21 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Star Charge Americas Corp. | SI403LULA00 {208V} | Y | Y | N | N | N | N | Y* | Y | 3.3 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 3.315 | 208 | 97 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 19.05 |  |  | 180 | 360 | 480 | 0.332 | 0.663 | 0.995 | 1.658 | 2.487 | 3.315 | 93.55 | 95.65 | 96.44 | 96.92 | 97.03 | 96.92 | 96.72 | 93.35 | 96.57 | 97.23 | 97.73 | 97.75 | 97.67 | 97.45 | 91.22 | 95.28 | 96.58 | 97.5 | 97.69 | 97.64 | 97.13 | 2025-02-21 | 2025-05-21
Star Charge Americas Corp. | SI403LULA00 {240V} | Y | Y | N | N | N | N | Y* | Y | 3.8 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 3.811 | 240 | 96 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 6.32 |  |  | 180 | 360 | 480 | 0.381 | 0.762 | 1.143 | 1.906 | 2.858 | 3.811 | 89.26 | 93.78 | 94.99 | 96.03 | 96.47 | 96.5 | 95.78 | 88.92 | 94.16 | 95.63 | 96.76 | 97.18 | 97.31 | 96.43 | 86.74 | 92.94 | 94.96 | 96.5 | 97.09 | 97.27 | 96.1 | 2025-02-21 | 2025-05-21
Star Charge Americas Corp. | SI803LULA00 {208V} | Y | Y | N | N | N | N | Y* | Y | 6.6 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 6.635 | 208 | 97.5 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 6.635 |  |  | 260 | 360 | 480 | 0.664 | 1.327 | 1.991 | 3.318 | 4.976 | 6.635 | 96.26 | 97.26 | 97.33 | 97.31 | 97 | 96.55 | 97.07 | 96.46 | 97.57 | 97.76 | 97.65 | 97.36 | 96.97 | 97.42 | 95.17 | 97.16 | 97.6 | 97.62 | 97.36 | 96.98 | 97.33 | 2025-02-21 | 2025-05-21
Star Charge Americas Corp. | SI803LULA00 {240V} | Y | Y | N | N | N | N | Y* | Y | 7.6 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 7.641 | 240 | 97 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 6.25 |  |  | 260 | 360 | 480 | 0.764 | 1.528 | 2.292 | 3.82 | 5.73 | 7.641 | 94.03 | 96.04 | 96.62 | 96.96 | 96.8 | 96.5 | 96.65 | 94.02 | 96.36 | 97 | 97.3 | 97.17 | 96.96 | 97 | 92.82 | 95.95 | 96.82 | 97.26 | 97.18 | 97 | 96.91 | 2025-02-21 | 2025-05-21
Star Charge Americas Corp. | SI104LULA00 {208V} | Y | Y | N | N | N | N | Y* | Y | 8.3 kW, 208 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 8.304 | 208 | 97 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 19 |  |  | 320 | 360 | 480 | 0.83 | 1.661 | 2.491 | 4.152 | 6.228 | 8.304 | 96.98 | 97.55 | 97.62 | 97.4 | 96.91 | 96.43 | 97.11 | 96.72 | 97.65 | 97.7 | 97.48 | 97.01 | 96.55 | 97.19 | 95.87 | 97.41 | 97.62 | 97.47 | 97.02 | 96.57 | 97.14 | 2025-02-21 | 2025-05-21
Star Charge Americas Corp. | SI104LULA00 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.5 kW, 240 Vac, Transformerless Grid Support Utility Interactive Inverter with PCS functionality. | 9.582 | 240 | 97 | CSA Group | [8/1/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-08-09 | 2025-02-21 |  | N | N | 6.26 |  |  | 320 | 360 | 480 | 0.958 | 1.916 | 2.875 | 4.791 | 7.187 | 9.582 | 94.99 | 96.65 | 97.09 | 97.18 | 96.9 | 96.54 | 96.87 | 94.88 | 96.75 | 97.17 | 97.26 | 97 | 96.67 | 96.96 | 94.07 | 96.48 | 97.07 | 97.26 | 97.04 | 96.72 | 96.93 | 2025-02-21 | 2025-05-21
Star Charge Americas Corp. | SI125TULT10 {480V} | N | Y | N | N | N | N | Y* | Y | 125 kW, 480 Vac, Bi-directional Transformerless Grid Support Utility Interactive Inverter | 124.346 | 480 | 99 | CSA Group | [11/15/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-04 | 2025-02-03 |  | N | N | 0.32 |  |  | 750 | 840 | 1050 | 12.4346 | 24.8692 | 37.3038 | 62.173 | 93.2595 | 124.346 | 98.9359 | 99.4463 | 99.3152 | 99.1854 | 98.9366 | 98.5688 | 99.0414 | 98.4422 | 99.0214 | 99.1218 | 99.0517 | 98.8252 | 98.5742 | 98.8903 | 96.7749 | 98.289 | 98.6017 | 98.6792 | 98.5501 | 98.2172 | 98.4827 | 2025-02-03
Star Charge Americas Corp. | SI125TULT00 {480V} | N | Y | N | N | N | N | Y* | Y | 125 kW, 480 Vac, Bi-directional Transformerless Grid Support Utility Interactive Inverter | 124.382 | 480 | 99 | CSA Group | [11/15/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-04 | 2025-02-03 |  | N | N | 0.33 |  |  | 750 | 820 | 1000 | 12.4382 | 24.8764 | 37.3146 | 62.191 | 93.2865 | 124.382 | 98.9407 | 99.2874 | 99.0477 | 99.0224 | 98.8713 | 98.5691 | 98.9327 | 98.5677 | 99.0719 | 99.1541 | 99.0701 | 98.8555 | 98.4899 | 98.9174 | 97.1991 | 98.4817 | 98.6615 | 98.6539 | 98.3667 | 98.2598 | 98.4161 | 2025-02-03
Star Charge Americas Corp. | SI135TULT00 {480V} | N | Y | N | N | N | N | Y* | Y | 135 kW, 480 Vac, Bi-directional Transformerless Grid Support Utility Interactive Inverter | 133.1476 | 480 | 98.5 | CSA Group | [11/15/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-04 | 2025-02-03 |  | N | N | 1.78 |  |  | 810 | 880 | 1050 | 13.3148 | 26.6295 | 39.9443 | 66.5738 | 99.8607 | 133.1476 | 98.6983 | 98.7433 | 98.8678 | 98.7225 | 98.4817 | 98.0158 | 98.577 | 99.1454 | 98.7679 | 99.0498 | 98.772 | 98.6289 | 98.1263 | 98.712 | 98.8318 | 98.3189 | 98.2127 | 98.3201 | 98.0647 | 97.9558 | 98.1741 | 2025-02-03
Star Charge Americas Corp. | SI135TULT10 {480V} | N | Y | N | N | N | N | Y* | Y | 135 kW, 480 Vac, Bi-directional Transformerless Grid Support Utility Interactive Inverter | 134.2882 | 480 | 98.5 | CSA Group | [11/15/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-04 | 2025-02-03 |  | N | N | 0.32 |  |  | 810 | 880 | 1050 | 13.4288 | 26.8576 | 40.2865 | 67.1441 | 100.7162 | 134.2882 | 98.679 | 99.1227 | 99.1732 | 99.0486 | 98.8058 | 98.4254 | 98.8926 | 98.2848 | 98.9302 | 99.0373 | 98.9576 | 98.6759 | 98.3293 | 98.7582 | 97.0609 | 98.4019 | 98.6615 | 98.7008 | 98.421 | 98.1149 | 98.4379 | 2025-02-03
Sun Gold Power Inc | SGN7.6K1HB-48 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 7.6472 | 240 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.76472 | 1.5294 | 2.2942 | 3.8236 | 5.7354 | 7.6472 | 92.9526 | 95.5516 | 96.215 | 96.6536 | 96.4528 | 96.189 | 96.2682 | 89.7494 | 96.0782 | 96.7932 | 97.1622 | 96.9742 | 96.771 | 96.648 | 94.069 | 96.2392 | 96.7722 | 97.1198 | 96.913 | 96.6498 | 96.7789 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGN7.6K1HB-48 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.6 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 7.648 | 208 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 15 |  |  | 200 | 360 | 480 | 0.7648 | 1.5296 | 2.2944 | 3.824 | 5.736 | 7.648 | 92.946 | 95.544 | 96.21 | 96.648 | 96.448 | 96.186 | 96.2631 | 93.74 | 96.074 | 96.788 | 97.158 | 96.97 | 96.766 | 96.8034 | 94.064 | 96.234 | 96.766 | 97.116 | 96.906 | 96.704 | 96.7759 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGS-8K12MAX {208V} | Y | Y | N | N | N | N | N |  | 8.8 kW, 208 Vac Grid Support Utility Interactive Inverter | 8.81 | 208 | 96.5 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 72.3 |  |  | 275 | 362.5 | 450 | 0.88085 | 1.7617 | 2.6426 | 4.4043 | 6.6064 | 8.8085 | 94.444 | 95.624 | 96.816 | 96.49 | 97.126 | 95.666 | 96.6999 | 94.382 | 95.75 | 96.022 | 96.526 | 97.2 | 95.958 | 96.6698 | 93.96 | 94.784 | 96.388 | 96.654 | 96.84 | 95.102 | 96.4418 | 2025-09-22
Sun Gold Power Inc | SGS-8K12MAX {240V} | Y | Y | N | N | N | N | N |  | 8.8 kW, 240 Vac Grid Support Utility Interactive Inverter | 8.81 | 240 | 96.5 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 73.1 |  |  | 275 | 362.5 | 450 | 0.881 | 1.762 | 2.643 | 4.405 | 6.607 | 8.81 | 94.27 | 95.42 | 96.78 | 96.33 | 97.1 | 95.65 | 96.63 | 93.65 | 95.69 | 96.64 | 96.47 | 97.23 | 96.2 | 96.73 | 94 | 95.68 | 96.7 | 96.35 | 96.55 | 95.56 | 96.33 | 2025-09-22
Sun Gold Power Inc | SGS-10K15MAX {208V} | Y | Y | N | N | N | N | N |  | 10 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.01 | 208 | 97 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 73 |  |  | 275 | 362.5 | 450 | 1.0009 | 2.0018 | 3.0027 | 5.0045 | 7.5067 | 10.009 | 94.448 | 95.466 | 96.09 | 96.296 | 97.494 | 95.424 | 96.7472 | 94.858 | 96.006 | 96.29 | 96.748 | 97.216 | 95.398 | 96.7609 | 95.01 | 96.252 | 96.378 | 96.514 | 97.308 | 95.266 | 96.7828 | 2025-09-22
Sun Gold Power Inc | SGS-10K15MAX {240V} | Y | Y | N | N | N | N | N |  | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.01 | 240 | 96.5 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 73.7 |  |  | 275 | 362.5 | 450 | 1.0008 | 2.0016 | 3.0025 | 5.0041 | 7.5062 | 10.0082 | 94.646 | 95.758 | 95.334 | 96.51 | 97.434 | 95.878 | 96.7148 | 94.21 | 94.914 | 95.268 | 96.412 | 97.364 | 95.408 | 96.5661 | 94.976 | 94.772 | 95.296 | 96.478 | 97.2 | 95.4 | 96.5195 | 2025-09-22
Sun Gold Power Inc | SGN11.4KHB-48 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 10.1396 | 240 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 16.67 |  |  | 200 | 360 | 480 | 1.014 | 2.0279 | 3.0419 | 5.0698 | 7.6047 | 10.1396 | 93.0477 | 95.5809 | 96.2415 | 96.6629 | 96.4516 | 96.2021 | 96.2786 | 93.7158 | 96.0665 | 96.8163 | 97.1487 | 96.9642 | 96.7822 | 96.8013 | 94.0472 | 96.2511 | 96.7916 | 97.1155 | 96.9244 | 96.6588 | 96.7866 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGN10KHB-48 {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 10.1472 | 240 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 18 |  |  | 200 | 360 | 480 | 1.0147 | 2.0294 | 3.0442 | 5.0736 | 7.6104 | 10.1472 | 92.9963 | 95.5759 | 96.2237 | 96.6613 | 96.4562 | 96.1983 | 96.2761 | 93.7907 | 96.1027 | 96.8102 | 97.1618 | 96.9743 | 96.7739 | 96.8131 | 94.1119 | 96.2672 | 96.7835 | 97.1258 | 96.9159 | 96.6586 | 96.7866 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGN10KHB-48 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 10.1858 | 208 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.0186 | 2.0372 | 3.0557 | 5.0929 | 7.6393 | 10.1858 | 92.8933 | 95.4787 | 96.1281 | 96.5592 | 96.3579 | 96.0975 | 96.177 | 93.6955 | 96.0051 | 96.7063 | 97.0717 | 96.8789 | 96.675 | 96.7174 | 94.0173 | 96.1625 | 96.6817 | 96.9927 | 96.8158 | 96.5601 | 96.6795 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGN11.4KHB-48 {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 10.1858 | 208 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2024-08-01 | 2025-01-07 |  | N | N | 16.94 |  |  | 200 | 360 | 480 | 1.0186 | 2.0372 | 3.0557 | 5.0929 | 7.6393 | 10.1858 | 92.9095 | 95.4795 | 96.1203 | 96.5624 | 96.3577 | 96.1012 | 96.1775 | 93.6611 | 96.0245 | 96.7245 | 97.0669 | 96.879 | 96.6799 | 96.7185 | 94.0672 | 96.1747 | 96.6706 | 96.9939 | 96.8177 | 96.5602 | 96.682 | 2025-02-03 | 2025-09-02
Sun Gold Power Inc | SGS-12K18MAX {208V} | Y | Y | N | N | N | N | N |  | 12 kW, 208 Vac Grid Support Utility Interactive Inverter | 10.4 | 208 | 96.5 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 71.2 |  |  | 275 | 362.5 | 450 | 1.0397 | 2.0794 | 3.1192 | 5.1986 | 7.7979 | 10.3972 | 95.11 | 95.714 | 96.534 | 96.55 | 96.714 | 95.27 | 96.4716 | 95.33 | 96.102 | 96.616 | 96.924 | 97.478 | 95.264 | 96.9928 | 95.036 | 95.774 | 96.604 | 96.55 | 96.668 | 95.186 | 96.4515 | 2025-09-22
Sun Gold Power Inc | SGN-11K15PRO {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 11.5669 | 240 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2025-06-17 |  |  | N | N | 19 |  |  | 200 | 360 | 480 | 1.1567 | 2.3134 | 3.4701 | 5.7834 | 8.6752 | 11.5669 | 93.0675 | 95.5749 | 96.2997 | 96.6409 | 96.4392 | 96.2088 | 96.2752 | 93.6781 | 96.0439 | 96.7972 | 97.1353 | 96.9536 | 96.7793 | 96.7878 | 94.0465 | 96.3229 | 96.8228 | 97.1182 | 96.9286 | 96.6545 | 96.7965 | 2025-09-02
Sun Gold Power Inc | SGN-11K15PRO {208V} | Y | Y | Y | Y | Y | Y | Y* |  | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive PV and Battery Inverter | 11.6088 | 208 | 96.5 | SGS | [7/4/2025] | SGS | [7/4/2025] | [051001] | 2025-09-02 | [7/4/2025] | 2025-09-02 | SGS | 2025-06-17 |  |  | N | N | 19 |  |  | 200 | 360 | 480 | 1.1609 | 2.3218 | 3.4827 | 5.8044 | 8.7066 | 11.6088 | 92.8881 | 95.4935 | 96.1138 | 96.5693 | 96.353 | 96.1025 | 96.1756 | 93.6426 | 96.0296 | 96.7159 | 97.0645 | 96.8809 | 96.677 | 96.7174 | 94.0961 | 96.1711 | 96.6734 | 96.9968 | 96.8241 | 96.5565 | 96.6871 | 2025-09-02
Sun Gold Power Inc | SGS-12K18MAX {240V} | Y | Y | N | N | N | N | N |  | 12 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.99 | 240 | 96.5 | Intertek | [8/1/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 74.3 |  |  | 275 | 362.5 | 450 | 1.1996 | 2.3991 | 3.5987 | 5.9979 | 8.9968 | 11.9957 | 95.452 | 95.688 | 96.376 | 96.392 | 96.504 | 95.226 | 96.3183 | 95.568 | 96.168 | 96.69 | 96.874 | 97.428 | 95.228 | 96.9757 | 95.526 | 95.868 | 96.596 | 96.456 | 96.536 | 95.324 | 96.392 | 2025-09-22
Sungrow Power Supply Co., Ltd. | SC60HV {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 66 kW, 480 Vac, Bi-directional, Stand-Alone or Grid Support Utility Interactive Energy Storage Inverter | 66 | 480 | 98 | CSA Group | [9/14/2022] | CSA Group | [06/14/2019] | [MDSP_AGATE-S_V11_V01_A] | 2019-08-01 | [06/14/2019] | 2020-10-12 | CSA Group | 2020-07-22 | 2020-10-12 |  | N | N | 0.26 |  |  | 700 | 850 | 1300 | 6.6281 | 13.2561 | 19.8842 | 33.1404 | 49.7105 | 66.2807 | 97.3638 | 98.2989 | 98.5712 | 98.5281 | 98.3286 | 98.1691 | 98.3516 | 96.7215 | 97.825 | 98.1342 | 98.1458 | 98.0383 | 97.8359 | 97.9989 | 94.5379 | 96.5379 | 97.2009 | 97.5021 | 97.4648 | 97.3043 | 97.2695 | 2019-08-01 | 2023-02-13
Sungrow Power Supply Co., Ltd. | SC75HV {600V} | N | N | Y | Y | Y | Y | Y* | Y | 82.5 kW, 600 Vac, Bi-directional, Stand-Alone or Grid Support Utility Interactive Energy Storage Inverter | 82.5 | 600 | 98 | No Information Submitted | No Information Submitted | CSA Group | [06/14/2019] | [MDSP_AGATE-S_V11_V01_A] | 2019-08-01 | [06/14/2019] | 2020-10-12 | CSA Group | 2020-07-22 | 2020-10-12 |  | N | N | 5.35 |  |  | 870 | 1000 | 1300 | 8.2568 | 16.5137 | 24.7705 | 41.2842 | 61.9263 | 82.5684 | 97.5289 | 98.3356 | 98.5333 | 98.5931 | 98.4281 | 98.2689 | 98.4268 | 96.8742 | 97.9804 | 98.2077 | 98.2667 | 98.1351 | 97.9228 | 98.1027 | 94.7732 | 97.15 | 97.6049 | 97.8392 | 97.7759 | 97.5738 | 97.6071 | 2019-08-01 | 2020-10-12
Sungrow Power Supply Co., Ltd. | SC125CX-US {480V} | N | Y | N | N | N | N | Y |  | 125 kW, 480 Vac, Bi-directional, Grid Support Utility Interactive Energy Storage Inverter | 125.3848 | 480 | 98.5 | CSA Group | [8/12/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-08-13 |  |  | N | N | 18.9 |  |  | 767 | 850 | 935 | 12.5385 | 25.077 | 37.6154 | 62.6924 | 94.0386 | 125.3848 | 97.7709 | 98.457 | 98.6002 | 98.6577 | 98.5705 | 98.4431 | 98.5483 | 97.6241 | 98.345 | 98.527 | 98.5873 | 98.5162 | 98.412 | 98.483 | 97.3747 | 98.1542 | 98.3389 | 98.424 | 98.3674 | 98.2762 | 98.321 | 2025-11-21
Sungrow Power Supply Co., Ltd. | SC125HX-US {690V} | N | Y | N | N | N | N | Y |  | 127 kW, 690 Vac, Bi-directional, Grid Support Utility Interactive Energy Storage Inverter | 127.3734 | 690 | 98.5 | CSA Group | [4/29/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2025-04-28 |  |  | N | N | 4.62 |  |  | 1000 | 1250 | 1500 | 12.7373 | 25.4747 | 38.212 | 63.6867 | 95.5301 | 127.3734 | 98.0458 | 98.7508 | 98.917 | 98.9724 | 98.8268 | 98.4598 | 98.8148 | 95.9976 | 98.0028 | 98.418 | 98.6833 | 98.5921 | 98.5297 | 98.454 | 95.6508 | 97.4887 | 98.0882 | 98.3498 | 98.3189 | 98.2389 | 98.1455 | 2025-11-21
Sungrow Power Supply Co., Ltd. | SC210HX-US {690V} | N | Y | N | N | N | N | Y* | Y | 210 kW, 690 Vac Grid Support Utility Interactive Storage Inverter, bi-directional for use with battery management system | 212.078 | 690 | 98.5 | CSA Group | [1/11/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-01-12 | 2024-10-21 |  | N | N | 5.33 |  |  | 1000 | 1250 | 1500 | 21.208 | 42.416 | 63.623 | 106.039 | 159.059 | 212.078 | 98.29 | 98.79 | 98.99 | 98.93 | 98.83 | 98.72 | 98.84 | 97.02 | 98.08 | 98.46 | 98.66 | 98.6 | 98.54 | 98.5 | 95.7 | 97.48 | 98.06 | 98.38 | 98.33 | 98.23 | 98.16 | 2024-10-21
Sungrow Power Supply Co., Ltd. | SG250HX-US {800V} | Y | N | Y | Y | Y | Y | Y* | Y | 250 kW, 800 Vac, 3-phase, Transformerless Grid Support Utility Interactive Battery and Solar Inverter | 226.997 | 800 | 98.5 | No Information Submitted | No Information Submitted | CSA Group | [08/04/2020] | [MDSP_DIAMOND-S_V11_V01_A] | 2020-09-21 | [08/04/2020] | 2021-02-22 | CSA Group | 2020-12-07 | 2021-02-22 |  | N | N | 5.21 |  |  | 860 | 1080 | 1300 | 22.6997 | 45.3994 | 68.0992 | 113.4986 | 170.2479 | 226.9972 | 97.0577 | 98.2506 | 98.469 | 98.5708 | 98.4621 | 98.262 | 98.409 | 98.195 | 98.7627 | 98.9461 | 99.0101 | 98.869 | 98.6779 | 98.8661 | 97.9983 | 98.6612 | 98.8997 | 98.9478 | 98.8178 | 98.632 | 98.805 | 2020-09-21 | 2021-02-22
Sungrow Power Supply Co., Ltd. | SC250KU {480V} | N | N | Y | Y | Y | Y | Y* | Y | 250 kW, 480 Vac Grid Support Utility Interactive Storage Inverter, bi-directional for use with battery management system | 250 | 480 | 96 | No Information Submitted | No Information Submitted | CSA Group | [05/11/2018];[04/29/2019] | [DSP_SC250-V13_V1_B_M];[DSP_SC250-V13_V1_C_M] | 2019-02-01 | [04/29/2019] | 2021-09-13 | CSA Group | 2021-08-11 | 2021-09-13 |  | N | N | 93.64 |  |  | 500 | 675 | 850 | 25.329 | 50.6581 | 75.9871 | 126.6452 | 189.9678 | 253.2904 | 95.0019 | 96.5561 | 96.9221 | 96.7419 | 96.3008 | 95.8054 | 96.404 | 94.0209 | 96.3064 | 96.5163 | 96.3454 | 96.1902 | 95.7691 | 96.1599 | 92.8571 | 94.8975 | 96.0999 | 96.0222 | 95.9534 | 95.5741 | 95.7898 | 2019-02-01 | 2021-09-13
Sungrow Power Supply Co., Ltd. | SC430HX-US {690V} | N | Y | N | N | N | N | Y* |  | 430 kW, 690 Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 430.6 | 690 | 99 | CSA Group | [1/27/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-01-07 |  |  | N | N | 74.71 |  |  | 1100 | 1300 | 1500 | 43.06 | 86.12 | 129.18 | 215.3 | 322.95 | 430.6 | 98.77 | 99.15 | 99.25 | 99.25 | 99.17 | 99.04 | 99.17 | 98.07 | 98.76 | 98.97 | 99.06 | 99 | 98.89 | 98.95 | 97.28 | 98.35 | 98.52 | 98.87 | 98.85 | 98.76 | 98.72 | 2026-10-01 |  | Y | N | N | N | N | N | Y | N | No Information Submitted
Sungrow Power Supply Co., Ltd. | SC450HX-US {690V} | N | Y | N | N | N | N | Y* |  | 450 kW, 690 Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 452.492 | 690 | 99 | CSA Group | [1/27/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2026-01-07 |  |  | N | N | 74.23 |  |  | 1100 | 1300 | 1500 | 45.249 | 90.498 | 135.747 | 226.246 | 339.369 | 452.492 | 98.71 | 99.09 | 99.19 | 99.19 | 99.11 | 98.99 | 99.12 | 98.01 | 98.69 | 98.91 | 99 | 98.95 | 98.84 | 98.9 | 97.18 | 98.27 | 98.61 | 98.79 | 98.77 | 98.68 | 98.66 | 2026-10-01 |  | Y | N | N | N | N | N | Y | N | No Information Submitted
Sungrow Power Supply Co., Ltd. | SC1000KU {540V} | Y | N | Y | Y | N | N | N | N | 1000 kW, 540 Vac Grid Support Utility Interactive Storage Inverter, bi-directional for use with battery management system, intended to be used in conjunction with a 1000 KVA (min) rated isolation transformer | 1001.306 | 540 | 96.5 | No Information Submitted | No Information Submitted | CSA Group | [09/19/2019] | [DSP_SC1000KU_V1_B_M] | 2019-02-01 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 1 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216. | N | N | 83.7646 |  |  | 810 | 1005 | 1200 | 100.1306 | 200.2612 | 300.3918 | 500.653 | 750.9795 | 1001.306 | 94.9956 | 96.8144 | 97.2437 | 97.3155 | 97.0286 | 96.6633 | 97.0044 | 94.2811 | 96.3444 | 96.9047 | 97.0479 | 96.8017 | 96.439 | 96.7239 | 93.6894 | 95.9275 | 96.5802 | 96.8324 | 96.5978 | 96.1882 | 96.4746 | 2019-02-01
Sungrow Power Supply Co., Ltd. | SG3150UD-MV-US {600V} | Y | Y | N | N | N | N | Y* | Y | 3150 kW, 600 Vac Hybrid Grid Support Utility Interactive Inverter connects to the grid via a 3150 kVA medium voltage transformer. (Made up of three SG1050UD-US installed together, each rated max output power = 1053). | 1053 | 600 | 97.5 | SGS | [6/15/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-05-17 | 2024-04-02 | Submitted performance data is the same as SG1050UD-US. Efficiency data inclusive of transformer effect based on Medium-Voltage Transformers DOE Table. | N | N | 124.76 |  |  | 875 | 1100 | 1438 | 105.344 | 210.687 | 316.031 | 526.718 | 790.078 | 1053.437 | 96.97 | 97.92 | 98.13 | 97.99 | 97.64 | 97.04 | 97.73 | 96.68 | 97.88 | 98 | 97.89 | 97.6 | 97 | 97.65 | 96.14 | 97.57 | 97.82 | 97.74 | 97.47 | 96.9 | 97.49 | 2024-04-02 | 2024-04-11
Sungrow Power Supply Co., Ltd. | SG4400UD-MV-US {645V} | Y | Y | N | N | N | N | Y* | Y | 4400 kW, 645 Vac Hybrid Grid Support Utility Interactive Inverter connects to the grid via a 4400 kVA medium voltage transformer. (Made up of four SG1100UD-US installed together, each rated max output power = 1103). | 1103 | 645 | 97.5 | SGS | [6/15/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | SGS | 2023-05-17 | 2024-04-02 | Submitted performance data is the same as SG1100UD-US. Efficiency data inclusive of transformer effect based on Medium-Voltage Transformers DOE Table. | N | N | 128.74 |  |  | 915 | 1100 | 1449 | 110.306 | 220.612 | 330.918 | 551.529 | 827.294 | 1103.059 | 97 | 97.92 | 98.2 | 98.07 | 97.75 | 97.17 | 97.82 | 96.83 | 97.89 | 98.13 | 97.99 | 97.68 | 97.11 | 97.75 | 96.5 | 97.57 | 97.81 | 97.82 | 97.53 | 96.98 | 97.56 | 2024-04-02 | 2024-04-11
Sungrow Power Supply Co., Ltd. | SC1200UD-US {480V} | N | Y | Y | Y | Y | Y | Y* | Y | 1200 kVA, 480 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter | 1203.052 | 480 | 98.5 | SGS | [1/30/2022] | SGS | [1/30/2022] | [DSP-Udseries-V1-A] | 2021-05-03 | [12/30/2020] | 2021-05-03 | SGS | 2021-09-14 | 2021-09-21 |  | N | N | 146.929 |  |  | 700 | 900 | 1500 | 120.3052 | 240.6104 | 360.9156 | 601.526 | 902.289 | 1203.052 | 98.4881 | 98.7829 | 98.7942 | 98.6273 | 98.3268 | 98.0578 | 98.4618 | 98.1743 | 98.5753 | 98.598 | 98.4816 | 98.2181 | 97.9451 | 98.3215 | 97.2336 | 98.0029 | 98.2153 | 98.2283 | 98.015 | 97.7698 | 98.0397 | 2021-05-03 | 2023-02-13
Sungrow Power Supply Co., Ltd. | SC1375UD-US {550V} | N | Y | Y | Y | Y | Y | Y* | Y | 1375 kVA, 550 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter | 1378.936 | 550 | 98.5 | SGS | [1/30/2022] | SGS | [1/30/2022] | [DSP-Udseries-V1-A] | 2021-05-03 | [12/30/2020] | 2021-05-03 | SGS | 2021-09-14 | 2021-09-21 |  | N | N | 144.254 |  |  | 800 | 975 | 1500 | 137.8936 | 275.7872 | 413.6808 | 689.468 | 1034.202 | 1378.936 | 98.4972 | 98.8173 | 98.8873 | 98.7562 | 98.5195 | 98.2335 | 98.6131 | 98.2871 | 98.7125 | 98.7893 | 98.6739 | 98.4481 | 98.1471 | 98.5282 | 97.6928 | 98.3328 | 98.4872 | 98.4032 | 98.2035 | 98.0163 | 98.2562 | 2021-05-03 | 2023-02-13
Sungrow Power Supply Co., Ltd. | SC1575UD-US {630V} | N | Y | Y | Y | Y | Y | Y* | Y | 1575 kVA, 630 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter | 1582.996 | 630 | 98.5 | SGS | [1/30/2022] | SGS | [1/30/2022] | [DSP-Udseries-V1-A] | 2021-05-03 | [12/30/2020] | 2021-05-03 | SGS | 2021-09-14 | 2021-09-21 |  | N | N | 144.104 |  |  | 915 | 1062 | 1500 | 158.2996 | 316.5992 | 474.8988 | 791.498 | 1187.247 | 1582.996 | 98.5171 | 98.8728 | 98.9565 | 98.8432 | 98.6696 | 98.308 | 98.7264 | 98.2726 | 98.7726 | 98.8628 | 98.7828 | 98.5989 | 98.2712 | 98.6484 | 97.8901 | 98.4771 | 98.6428 | 98.5894 | 98.4413 | 98.1299 | 98.4607 | 2021-05-03 | 2023-02-13
Sungrow Power Supply Co., Ltd. | SC1725UD-US {690V} | N | Y | Y | Y | Y | Y | Y* | Y | 1725 kVA, 690 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter | 1728.406 | 690 | 98.5 | SGS | [1/30/2022] | SGS | [1/30/2022] | [DSP-Udseries-V1-A] | 2021-05-03 | [12/30/2020] | 2021-05-03 | SGS | 2021-09-14 | 2021-09-21 |  | N | N | 141.725 |  |  | 1000 | 1125 | 1500 | 172.8406 | 345.6812 | 518.5218 | 864.203 | 1296.3045 | 1728.406 | 98.5057 | 98.8927 | 99.016 | 98.9552 | 98.7298 | 98.4459 | 98.7964 | 98.2439 | 98.782 | 98.9046 | 98.8565 | 98.6774 | 98.346 | 98.7136 | 97.958 | 98.595 | 98.7454 | 98.7257 | 98.5906 | 98.2302 | 98.5945 | 2021-05-03 | 2023-02-13
Sungrow Power Supply Co., Ltd. | SC2000UD-US {800V} | N | Y | Y | Y | Y | Y | Y* | Y | 2000 kVA, 800 Vac, Bi-directional, Grid Support Utility Interactive Inverter with a 2014 kVA liquid immersed distribution transformer | 2014.87 | 800 | 98 | SGS | [1/30/2022] | SGS | [1/30/2022] | [DSP-UDseries-V1-A] | 2023-08-01 | [1/30/2022] | 2023-08-01 | SGS | 2023-06-07 | 2023-08-01 | Efficiency data inclusive of transformer effect based on 2014 kVA Liquid-immersed distribution transformer DOE Tables. | N | N | 157.7 |  |  | 1150 | 1250 | 1500 | 201.487 | 402.974 | 604.461 | 1007.435 | 1511.153 | 2014.87 | 97.42 | 98.38 | 98.55 | 98.55 | 98.24 | 97.83 | 98.3 | 97.32 | 98.33 | 98.5 | 98.47 | 98.16 | 97.8 | 98.22 | 96.96 | 98.09 | 98.36 | 98.38 | 98.09 | 97.72 | 98.12 | 2023-08-01
Sungrow Power Supply Co., Ltd. | SC2500U {550V} | N | N | Y | Y | Y | N | N | N | 2500 Kva, 550 Vac, Bi-directional, Grid Support Utility Interactive Battery Inverter | 2507.194 | 550 | 97.5 | No Information Submitted | No Information Submitted | CSA Group | [10/30/2019] | [DSP_SC2500U_V11_V1_A, LCD_SC2500U_V1_A] | 2020-01-02 | [10/30/2019] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 2500 kVA Medium-Voltage Dry-Type Distribution Transformers Table in DOE216. | N | N | 62.8 |  |  | 800 | 975 | 1500 | 250.7194 | 501.4388 | 752.1582 | 1253.597 | 1880.3955 | 2507.194 | 96.1656 | 97.496 | 97.8461 | 97.9177 | 97.6547 | 97.324 | 97.6489 | 96.0246 | 97.2391 | 97.7308 | 97.8521 | 97.5444 | 97.19 | 97.5376 | 95.4326 | 96.8219 | 97.3458 | 97.4664 | 97.1968 | 96.9426 | 97.1693 | 2020-01-02 | 2020-03-23
Sungrow Power Supply Co., Ltd. | SC2500UD-US {900V} | N | Y | Y | Y | Y | Y | Y* | Y | 2500 kVA, 900 Vac, Bi-directional, Grid Support Utility Interactive Inverter with a 2507 kVA liquid immersed distribution transformer. | 2507.23 | 900 | 98.5 | SGS | [1/30/2022] | SGS | [1/30/2022] | [DSP-UDseries-V1-A] | 2023-08-01 | [1/30/2022] | 2023-08-01 | SGS | 2023-06-07 | 2023-08-01 | Efficiency data inclusive of transformer effect based on 2507 kVA Liquid-immersed distribution transformer DOE Tables. | N | N | 169.9 |  |  | 1300 | 1350 | 1500 | 250.723 | 501.446 | 752.169 | 1253.615 | 1880.423 | 2507.23 | 97.8 | 98.53 | 98.61 | 98.58 | 98.32 | 97.79 | 98.37 | 97.72 | 98.49 | 98.58 | 98.55 | 98.31 | 97.78 | 98.35 | 97.58 | 98.35 | 98.52 | 98.51 | 98.25 | 97.73 | 98.29 | 2023-08-01
SunPluto Energy Inc | SP-SHD-7.6kW {240V} | Y | Y | N | N | N | N | N |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.5716 | 240 | 97 | Intertek | [4/27/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.938 |  |  | 144 | 410 | 550 | 0.75716 | 1.5143 | 2.2715 | 3.7858 | 5.6787 | 7.5716 | 92.671 | 93.9896 | 96.2481 | 96.7433 | 97.2278 | 97.292 | 96.6675 | 93.4521 | 95.8866 | 96.6336 | 97.1282 | 97.4397 | 97.1679 | 97.0268 | 92.8839 | 93.7396 | 95.8119 | 96.6727 | 97.5145 | 97.4143 | 96.7545 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y | No Information Submitted | No Information Submitted
SunPluto Energy Inc | SP-SHD-9.6kW {240V} | Y | Y | N | N | N | N | N |  | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.6605 | 240 | 97 | Intertek | [4/27/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 11.042 |  |  | 180 | 410 | 550 | 0.96605 | 1.9321 | 2.8981 | 4.8302 | 7.2454 | 9.6605 | 95.0181 | 95.7295 | 96.3315 | 97.1202 | 97.4251 | 96.8625 | 97.0206 | 94.6952 | 96.336 | 96.9007 | 97.251 | 97.4323 | 97.0366 | 97.1463 | 93.2296 | 95.1704 | 96.2911 | 97.2355 | 97.5393 | 97.148 | 97.0153 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y | No Information Submitted | No Information Submitted
SunPluto Energy Inc | SP-SHD-11.4kW {240V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.2567 | 240 | 97 | Intertek | [4/27/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.379 |  |  | 210 | 410 | 550 | 1.1257 | 2.2513 | 3.377 | 5.6283 | 8.4425 | 11.2567 | 95.4762 | 96.2795 | 96.6426 | 97.2608 | 97.4924 | 96.3559 | 97.1437 | 95.0276 | 96.6282 | 97.1093 | 97.5876 | 97.296 | 96.8654 | 97.1892 | 93.3197 | 95.8013 | 96.6312 | 97.5435 | 97.358 | 96.479 | 97.0264 | 2026-10-01 |  | Y | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Y | No Information Submitted | No Information Submitted
Suzhou Ample ESS Co., Ltd | AP-L8K-SPUS {240V} | Y | Y | N | N | N | N | N |  | 7.98 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.9814 | 240 | 96 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.39 |  |  | 108 | 380 | 480 | 0.79814 | 1.5963 | 2.3944 | 3.9907 | 5.986 | 7.9814 | 90.9385 | 94.1039 | 94.9752 | 95.083 | 95.0387 | 94.6196 | 94.8087 | 92.1593 | 95.6656 | 96.6163 | 96.6433 | 97.0374 | 96.9779 | 96.6374 | 92.4438 | 95.9014 | 96.6012 | 97.0486 | 97.2916 | 97.2167 | 96.8905 | 2026-03-23 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Suzhou Ample ESS Co., Ltd | AP-L10K-SPUS {240V} | Y | Y | N | N | N | N | N |  | 10.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.0109 | 240 | 96 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.12 |  |  | 135 | 380 | 480 | 1.0011 | 2.0022 | 3.0033 | 5.0055 | 7.5082 | 10.0109 | 92.0512 | 94.9782 | 94.9328 | 95.3714 | 95.3991 | 94.9543 | 95.1601 | 93.0994 | 96.2304 | 96.2761 | 96.8719 | 97.0247 | 96.9062 | 96.7001 | 93.6663 | 96.3246 | 96.5808 | 97.0256 | 97.1253 | 97.0288 | 96.8558 | 2026-03-23 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Suzhou Ample ESS Co., Ltd | AP-L12K-SPUS {240V} | Y | Y | N | N | N | N | N |  | 12.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 12.0145 | 240 | 96.5 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.39 |  |  | 161 | 380 | 480 | 1.2014 | 2.4029 | 3.6043 | 6.0072 | 9.0109 | 12.0145 | 93.1006 | 95.228 | 95.5523 | 95.8393 | 95.6025 | 95.1408 | 95.5043 | 94.3433 | 96.5994 | 96.675 | 97.0511 | 96.9701 | 96.7737 | 96.8183 | 95.2452 | 96.8669 | 96.9412 | 97.2998 | 97.1893 | 96.9458 | 97.0767 | 2026-03-23 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
Suzhou Ample ESS Co., Ltd | AP-L15K-SPUS {240V} | Y | Y | N | N | N | N | N |  | 15.01 kW, 240 Vac Grid Support Utility Interactive Inverter | 15.0148 | 240 | 96.5 | CSA Group | [11/26/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 10.08 |  |  | 202 | 380 | 480 | 1.5015 | 3.003 | 4.5045 | 7.5074 | 11.2611 | 15.0148 | 94.5483 | 95.5289 | 96.0138 | 96.1843 | 95.8054 | 95.25 | 95.8181 | 95.5893 | 96.5176 | 96.9793 | 97.101 | 96.8732 | 96.5137 | 96.8467 | 96.0793 | 96.8399 | 97.2558 | 97.3226 | 96.9795 | 96.6351 | 97.0245 | 2026-03-23 |  | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted
SYL (NINGBO) Battery Co., Ltd | SP135UHL {480V} | N | Y | N | N | N | N | Y* |  | 135 kW, 480 Vac, Grid Support Utility Interactive Inverter | 134.536 | 480 | 97 | CSA Group | [11/24/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 23.99 |  |  | 720 | 900 | 1300 | 13.454 | 26.907 | 40.361 | 67.268 | 100.902 | 134.536 | 97.5 | 97.94 | 97.89 | 98.02 | 97.94 | 97.8 | 97.93 | 96.53 | 97.66 | 97.9 | 97.73 | 97.67 | 97.45 | 97.65 | 90.33 | 94.22 | 95.21 | 96.18 | 96.46 | 96.39 | 95.89 | 2026-01-12
SYL (NINGBO) Battery Co., Ltd | SP1750UHL {690V} | N | Y | N | N | N | N | Y* | Y | 1750 kW, 690 Vac, Grid Support Utility Interactive Inverter | 1751.5088 | 690 | 98.5 | CSA Group | [12/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2024-12-27 | No Information Submitted |  | N | N | 119.44 |  |  | 1000 | 1150 | 1500 | 175.1509 | 350.3018 | 525.4526 | 875.7544 | 1313.6316 | 1751.5088 | 98.2359 | 99.0203 | 99.0408 | 98.9456 | 98.76 | 98.4333 | 98.8084 | 98.221 | 98.8315 | 98.8864 | 98.8298 | 98.673 | 98.277 | 98.7016 | 98.4476 | 98.6293 | 98.669 | 98.6577 | 98.5302 | 98.7791 | 98.5877 | 2025-03-03
Tabuchi Electric Co., Ltd. | THD-S55P3BB-US {240V} | Y | N | Y | Y | Y | N | N | N | 5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 3.3 kW Discharge Rate/20 kWh Storage Capacity | 5.5189 | 240 | 94.5 | No Information Submitted | No Information Submitted | Intertek | [9/20/2017] | [4.1] | 2018-10-15 | [9/20/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 10.1 |  |  | 240 | 380 | 520 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.3 | 93.3 | 94.3 | 94.7 | 94.1 | 94.2 | 94 | 89.7 | 93.7 | 94.7 | 95.4 | 95.5 | 95.4 | 95.1 | 88.8 | 93.1 | 94.3 | 95.1 | 95.2 | 94.9 | 94.7 | 2017-12-15 | 2018-10-15
Tabuchi Electric Co., Ltd. | THD-S55P3B-US {240V} | Y | N | Y | Y | Y | N | N | N | 5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 2 kW Discharge Rate/10 kWh Storage Capacity | 5.5189 | 240 | 94.5 | No Information Submitted | No Information Submitted | Intertek | [9/20/2017] | [4.1] | 2018-10-15 | [9/20/2017] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 10.1 |  |  | 240 | 380 | 520 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.3 | 93.3 | 94.3 | 94.7 | 94.1 | 94.2 | 94 | 89.7 | 93.7 | 94.7 | 95.4 | 95.5 | 95.4 | 95.1 | 88.8 | 93.1 | 94.3 | 95.1 | 95.2 | 94.9 | 94.7 | 2017-12-15 | 2018-10-15
Tabuchi Electric Co., Ltd. | THE-S55P3BB-USW {240V} | Y | N | Y | Y | Y | N | N | N | 5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 4.0 kW Discharge Rate/20 kWh Storage Capacity | 5.5189 | 240 | 94.5 | No Information Submitted | No Information Submitted | Intertek | [04/26/2018] | [4.11] | 2018-10-15 | [04/26/2018] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 10.1 |  |  | 240 | 380 | 520 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.326 | 93.286 | 94.304 | 94.656 | 94.048 | 94.174 | 93.9857 | 89.688 | 93.666 | 94.706 | 95.44 | 95.498 | 95.41 | 95.0624 | 88.78 | 93.076 | 94.276 | 95.094 | 95.166 | 94.922 | 94.6719 | 2018-06-01 | 2018-10-15
Tesla Inc. | 1707000-XX-Y {240V, 10kW} | Y | Y | N | N | N | N | Y | N | 10 kW, 240 Vac Grid Support Utility Interactive Powerwall 3 Integrated Energy Storage System Inverter, where XX are numbers and Y is a letter | 9.991 | 240 | 96.2 | Intertek | [4/26/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2020-03-20 | No Information Submitted | This component is specific to an energy storage system (1707000-xx-y) and is not available as an individual unit. | N | N | 0.11 |  |  | 270 | 375 | 480 | 0.999 | 1.998 | 2.997 | 4.995 | 7.493 | 9.991 | 94.49 | 94.53 | 95.49 | 97.6 | 97.4 | 96.78 | 96.92 | 94.48 | 94.72 | 94.73 | 96.44 | 97 | 95.25 | 96.31 | 91.41 | 92.53 | 94.39 | 95.75 | 96.1 | 94.97 | 95.4 | 2024-08-01
Tesla Inc. | 1707000-XX-Y {240V, 11.5kW} | Y | Y | N | N | N | N | Y | N | 11.5 kW, 240 Vac Grid Support Utility Interactive Powerwall 3 Integrated Energy Storage System Inverter, where XX are numbers and Y is a letter | 11.508 | 240 | 97.5 | Intertek | [3/23/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2020-03-20 | No Information Submitted | This component is specific to an energy storage system (1707000-xx-y) and is not available as an individual unit. | N | N | 0.29 |  |  | 270 | 375 | 480 | 1.1508 | 2.3016 | 3.4524 | 5.754 | 8.631 | 11.508 | 94.2008 | 96.0606 | 96.991 | 97.8448 | 97.659 | 96.72 | 97.3526 | 92.3243 | 94.3963 | 96.7175 | 97.3893 | 98.2249 | 97.2062 | 97.3901 | 92.093 | 95.365 | 96.6821 | 97.177 | 98.2476 | 97.2883 | 97.3966 | 2024-01-11
Tigo Energy, Inc | TSI-3.0K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 2.626 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 2.626 | 208 | 96.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.576 |  |  | 125 | 380 | 480 | 0.26259 | 0.52518 | 0.78777 | 1.3129 | 1.9694 | 2.6259 | 91.2934 | 93.7087 | 95.2183 | 95.8997 | 95.8355 | 95.6645 | 95.4784 | 93.5823 | 95.3477 | 96.9042 | 97.2283 | 97.3991 | 97.0876 | 97.033 | 92.5038 | 95.6858 | 96.4301 | 96.8779 | 96.8499 | 96.9624 | 96.579 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-3.0K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.095 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.095 | 240 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.593 |  |  | 125 | 380 | 480 | 0.30951 | 0.61902 | 0.92853 | 1.5475 | 2.3213 | 3.0951 | 92.5494 | 94.742 | 95.5187 | 96.466 | 96.3778 | 96.1735 | 96.0481 | 94.9531 | 96.9774 | 97.284 | 97.7821 | 97.7609 | 97.4493 | 97.5411 | 93.2489 | 95.9992 | 96.7283 | 97.2156 | 97.3487 | 97.3889 | 97.0169 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-3.8K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.324 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 3.324 | 208 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.576 |  |  | 160 | 380 | 480 | 0.33238 | 0.66477 | 0.99715 | 1.6619 | 2.4929 | 3.3238 | 91.7552 | 94.4271 | 95.625 | 96.3968 | 96.3716 | 96.2365 | 95.9987 | 92.8401 | 95.7332 | 97.3293 | 97.2908 | 97.7747 | 97.4727 | 97.3051 | 92.8717 | 95.7668 | 96.7784 | 97.4953 | 97.5884 | 97.4672 | 97.1859 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-3.8K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 3.888 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 3.888 | 240 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.593 |  |  | 160 | 380 | 480 | 0.38882 | 0.77764 | 1.1665 | 1.9441 | 2.9162 | 3.8882 | 92.9226 | 95.0495 | 95.9079 | 96.5875 | 96.7318 | 96.456 | 96.3523 | 95.8681 | 97.43 | 97.8567 | 98.062 | 98.0583 | 97.9727 | 97.9116 | 93.4977 | 96.4887 | 97.1935 | 97.6687 | 97.7381 | 97.6144 | 97.4199 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-5.0K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4.28 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 4.28 | 208 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.576 |  |  | 210 | 380 | 480 | 0.42805 | 0.85609 | 1.2841 | 2.1402 | 3.2104 | 4.2805 | 93.9969 | 95.6291 | 96.5292 | 97.277 | 96.8685 | 96.4968 | 96.7182 | 95.6415 | 97.3556 | 97.7545 | 97.9536 | 97.7989 | 97.5872 | 97.707 | 95.0137 | 96.8034 | 97.3434 | 97.6629 | 97.6924 | 97.3985 | 97.478 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-5.0K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 4.943 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 4.943 | 240 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.593 |  |  | 210 | 380 | 480 | 0.49432 | 0.98864 | 1.483 | 2.4716 | 3.7074 | 4.9432 | 94.2674 | 96.0279 | 96.6177 | 96.9688 | 96.7976 | 96.4626 | 96.6555 | 95.8274 | 97.6476 | 97.9929 | 98.1977 | 98.0262 | 97.7757 | 97.9388 | 95.1548 | 97.2155 | 97.7005 | 97.9802 | 97.817 | 97.6089 | 97.6903 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-6.0K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.143 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 5.143 | 208 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.576 |  |  | 170 | 380 | 480 | 0.51426 | 1.0285 | 1.5428 | 2.5713 | 3.8569 | 5.1426 | 93.4812 | 95.1436 | 95.9216 | 96.4143 | 96.4086 | 96.2016 | 96.1607 | 95.7404 | 97.2023 | 97.6753 | 97.7276 | 97.7059 | 97.2003 | 97.5777 | 94.531 | 96.5287 | 97.1839 | 97.4841 | 97.5 | 97.1255 | 97.2727 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-6.0K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 5.918 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 5.918 | 240 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.593 |  |  | 170 | 380 | 480 | 0.59178 | 1.1836 | 1.7753 | 2.9589 | 4.4383 | 5.9177 | 93.4931 | 95.0713 | 96.0091 | 96.5068 | 96.5375 | 96.277 | 96.2595 | 96.2836 | 97.6235 | 97.995 | 98.0323 | 97.7405 | 97.6407 | 97.7632 | 95.2829 | 97.0935 | 97.4899 | 97.8279 | 97.6998 | 97.4333 | 97.5612 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-7.6K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 6.58 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter | 6.58 | 208 | 97 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.576 |  |  | 212 | 380 | 480 | 0.65804 | 1.3161 | 1.9741 | 3.2902 | 4.9353 | 6.5804 | 93.7826 | 95.5421 | 96.606 | 96.8324 | 96.8224 | 96.4415 | 96.5939 | 95.6144 | 97.208 | 97.6283 | 97.7129 | 97.8083 | 97.3895 | 97.628 | 94.0659 | 96.3435 | 97.3147 | 97.3793 | 97.4451 | 97.2215 | 97.2142 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-8.2K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.2 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 7.166 | 208 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.71659 | 1.4332 | 2.1498 | 3.5829 | 5.3744 | 7.1659 | 93.818 | 95.9467 | 96.5916 | 96.9394 | 96.8921 | 96.7981 | 96.691 | 95.2258 | 97.2231 | 97.7432 | 97.9238 | 97.8229 | 97.7412 | 97.6966 | 93.7147 | 96.5216 | 97.2952 | 97.7041 | 97.7221 | 97.6373 | 97.4425 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-7.6K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 7.524 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter | 7.524 | 240 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 1.593 |  |  | 212 | 380 | 480 | 0.75242 | 1.5048 | 2.2573 | 3.7621 | 5.6431 | 7.5242 | 94.8321 | 96.2443 | 96.9372 | 97.1359 | 97.0549 | 96.4681 | 96.899 | 96.1031 | 97.82 | 98.0103 | 98.1875 | 98.0302 | 97.4081 | 97.9421 | 95.2191 | 97.2034 | 97.6838 | 97.8749 | 97.7927 | 97.3782 | 97.6437 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-9.0K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 7.874 | 208 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.78742 | 1.5748 | 2.3623 | 3.9371 | 5.9056 | 7.8742 | 93.9829 | 96.0797 | 96.6986 | 97.0304 | 96.9127 | 96.7846 | 96.7465 | 95.5872 | 97.3526 | 97.782 | 97.9238 | 97.7705 | 97.6713 | 97.6909 | 94.5847 | 96.692 | 97.396 | 97.712 | 97.6675 | 97.5806 | 97.4678 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-8.2K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 8.2 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 8.251 | 240 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.82514 | 1.6503 | 2.4754 | 4.1257 | 6.1886 | 8.2514 | 93.9258 | 96.1247 | 96.8143 | 97.2666 | 97.2617 | 97.0721 | 97.0092 | 95.5722 | 97.4863 | 97.9916 | 98.2391 | 98.1842 | 98.0166 | 98.0249 | 93.7743 | 96.6734 | 97.4868 | 97.9609 | 97.966 | 97.9229 | 97.673 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-10.0K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 8.76 | 208 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.87595 | 1.7519 | 2.6278 | 4.3797 | 6.5696 | 8.7595 | 94.7147 | 96.1872 | 96.7641 | 96.9456 | 96.7226 | 96.627 | 96.6625 | 96.1898 | 97.4947 | 97.8331 | 97.8547 | 97.653 | 97.5442 | 97.6451 | 94.884 | 96.9958 | 97.5353 | 97.726 | 97.6134 | 97.5151 | 97.4827 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-9.0K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 9 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 9.063 | 240 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 0.90625 | 1.8125 | 2.7188 | 4.5312 | 6.7969 | 9.0625 | 94.2384 | 96.2702 | 96.908 | 97.3235 | 97.2 | 97.0403 | 97.018 | 95.9482 | 97.6026 | 98.0707 | 98.2515 | 98.1428 | 97.9914 | 98.0346 | 94.3716 | 96.8985 | 97.6347 | 98.0229 | 98.0409 | 97.9412 | 97.7795 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-11.4K-US {208V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 208 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 10.04 | 208 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.004 | 2.008 | 3.0119 | 5.0199 | 7.5298 | 10.0398 | 95.0284 | 96.5616 | 97.0154 | 97.1814 | 96.9023 | 96.8567 | 96.8802 | 95.703 | 97.5294 | 97.8587 | 97.8733 | 97.7607 | 97.7179 | 97.7001 | 95.102 | 97.007 | 97.5024 | 97.6871 | 97.6273 | 97.6013 | 97.4916 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-10.0K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 10.082 | 240 | 97.5 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.0082 | 2.0164 | 3.0246 | 5.041 | 7.5615 | 10.082 | 95.1276 | 96.4976 | 97.0675 | 97.3296 | 97.1985 | 96.9229 | 97.0787 | 96.3253 | 97.7618 | 98.1384 | 98.2919 | 98.1462 | 97.9316 | 98.0731 | 95.0134 | 97.1984 | 97.7803 | 98.0517 | 98.0092 | 97.8719 | 97.8234 | 2022-02-01 | 2023-10-11
Tigo Energy, Inc | TSI-11.4K-US {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 11.4 kW, 240 Vac Hybrid Grid Support Utility Interactive Inverter with PCS Functionality | 11.52 | 240 | 98 | Intertek | [8/2/2022] | Intertek | [11/09/2021] | [UE1.0] | 2022-02-01 | [11/09/2021] | 2022-02-01 | Intertek | 2021-11-09 | 2022-02-01 |  | N | N | 10 |  |  | 250 | 380 | 480 | 1.152 | 2.304 | 3.456 | 5.76 | 8.64 | 11.52 | 95.3626 | 96.9572 | 97.4775 | 97.685 | 97.5433 | 97.3539 | 97.4392 | 96.5819 | 98.0275 | 98.3999 | 98.5274 | 98.4351 | 98.2539 | 98.3467 | 95.457 | 97.1914 | 97.7448 | 97.9708 | 97.8318 | 97.6582 | 97.7149 | 2022-02-01 | 2023-10-11
TRUMPF Hüttinger GmbH + Co. KG | TruConvert AC 3025 {480V} | N | N | Y | Y | Y | N | N | N | 25 kVA, 240 Vac, Grid Support Utility Interactive Inverter | 24.9679 | 480 | 97 | No Information Submitted | No Information Submitted | CSA Group | [2/15/2023] | [V01.34.00, V04.33.00] | 2023-07-11 | [2/15/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 10 |  |  | 784 | 867 | 950 | 2.4968 | 4.9936 | 7.4904 | 12.4839 | 18.7259 | 24.9679 | 94.746 | 96.626 | 97.152 | 97.448 | 97.464 | 97.38 | 97.2684 | 93.6 | 95.974 | 96.7 | 97.136 | 97.216 | 97.1491 | 96.9272 | 92.74 | 95.482 | 96.348 | 96.9201 | 97.006 | 96.956 | 96.6597 | 2023-07-11
Trystar, LLC | OZPCS-EP40-000 {208V} | N | Y | N | N | N | N | Y* | N | 40 kW, 208 Vac,Grid Support Utility Interactive Battery Inverter | 17.2299 | 208 | 94 | Intertek | [2/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2024-05-01 | No Information Submitted |  | N | N | 8.96 |  |  | 550 | 700 | 820 | 1.723 | 3.446 | 5.169 | 8.615 | 12.9224 | 17.2299 | 82.6298 | 90.9814 | 92.9335 | 93.787 | 93.8731 | 93.8065 | 93.1446 | 86.0293 | 91.7996 | 93.9314 | 95.0444 | 94.6718 | 94.3031 | 94.1534 | 87.9392 | 92.467 | 94.6258 | 95.3766 | 94.9661 | 94.7158 | 94.5929 | 2024-06-21
Trystar, LLC | OZPCS-RS40-BB1 {208V} | N | Y | N | N | N | N | Y* | N | 40 kVA, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 17.2299 | 208 | 94 | Intertek | [2/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2024-05-01 | No Information Submitted |  | N | N | 8.96 |  |  | 550 | 700 | 820 | 1.723 | 3.446 | 5.169 | 8.615 | 12.9224 | 17.2299 | 82.6298 | 90.9814 | 92.9335 | 93.787 | 93.8731 | 93.8065 | 93.1446 | 86.0293 | 91.7996 | 93.9314 | 95.0444 | 94.6718 | 94.3031 | 94.1534 | 87.9392 | 92.467 | 94.6258 | 95.3766 | 94.9661 | 94.7158 | 94.5929 | 2024-08-12
Trystar, LLC | OZPCS-RS40-FB1 {208V} | N | Y | N | N | N | N | Y* | N | 40 kVA, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 17.2299 | 208 | 94 | Intertek | [2/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2024-05-01 | No Information Submitted |  | N | N | 8.96 |  |  | 550 | 700 | 820 | 1.723 | 3.446 | 5.169 | 8.615 | 12.9224 | 17.2299 | 82.6298 | 90.9814 | 92.9335 | 93.787 | 93.8731 | 93.8065 | 93.1446 | 86.0293 | 91.7996 | 93.9314 | 95.0444 | 94.6718 | 94.3031 | 94.1534 | 87.9392 | 92.467 | 94.6258 | 95.3766 | 94.9661 | 94.7158 | 94.5929 | 2024-08-12
Trystar, LLC | OZPCS-RS40-Fxx {208V} | N | N | Y | Y | Y | Y | Y* | Y | 40 kVA, 208V, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, where xx = 00 or 01 | 17.515 | 208 | 93 | No Information Submitted | No Information Submitted | Intertek | [08/18/2021] | [Rev 6.1.3.0] | 2020-07-13 | [08/18/2021] | 2021-10-11 | Intertek | 2021-08-23 | 2021-10-11 | Formerly Oztek Corp., OZPCS-RS40-Fxx {208V} | N | N | 202.52 |  |  | 550 | 700 | 820 | 1.7515 | 3.5031 | 5.2546 | 8.7576 | 13.1365 | 17.5153 | 78.6327 | 88.4861 | 91.0734 | 92.8547 | 93.527 | 93.4074 | 92.2376 | 82.2755 | 90.3116 | 92.0493 | 93.7198 | 93.9528 | 93.9222 | 93.0248 | 84.9647 | 91.7444 | 92.925 | 94.1354 | 94.5961 | 94.2114 | 93.7518 | 2020-07-13 | 2024-04-02
Trystar, LLC | OZPCS-RS40-Bxx {208V} | N | N | Y | Y | Y | Y | Y* | Y | 40 kVA, 208V, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, where xx = 00 or 01 | 17.516 | 208 | 93.5 | No Information Submitted | No Information Submitted | Intertek | [08/18/2021] | [Rev 6.1.3.0] | 2020-07-13 | [08/18/2021] | 2021-10-11 | Intertek | 2021-08-23 | 2021-10-11 | Formerly Oztek Corp., OZPCS-RS40-Bxx {208V} | N | N | 191.36 |  |  | 550 | 700 | 820 | 1.7516 | 3.5032 | 5.2549 | 8.7581 | 13.1371 | 17.5162 | 78.1631 | 89.2647 | 91.741 | 93.2416 | 93.8382 | 93.6886 | 92.5981 | 81.2625 | 90.4785 | 92.8298 | 93.9721 | 94.3908 | 94.2223 | 93.3864 | 84.6425 | 92.0011 | 93.4073 | 94.6493 | 94.8884 | 94.5526 | 94.0894 | 2020-07-13 | 2024-04-02
Trystar, LLC | OZPCS-RS35-FB0 {240V} | N | Y | N | N | N | N | Y* | N | 24 kVA, 240 Vac, Bi-directional Transformerless Grid Support Utility Interactive Battery Inverter | 23.4463 | 240 | 95 | Bureau Veritas | [5/27/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Bureau Veritas Consumer Products Services | 2025-04-16 | No Information Submitted |  | N | N | 1.41 |  |  | 400 | 600 | 800 | 2.3446 | 4.6893 | 7.0339 | 11.7231 | 17.5847 | 23.4463 | 93.116 | 95.522 | 96.14 | 96.36 | 96.122 | 95.758 | 96.0057 | 88.828 | 93.234 | 94.558 | 95.326 | 95.368 | 95.13 | 94.8818 | 84.788 | 90.99 | 93.026 | 94.34 | 94.644 | 94.628 | 93.8083 | 2025-06-23
Trystar, LLC | OZPCS-RS35-FB1 {240V} | N | Y | N | N | N | N | Y* | N | 24 kVA, 240 Vac, Bi-directional Transformerless Grid Support Utility Interactive Battery Inverter | 23.4463 | 240 | 95 | Bureau Veritas | [5/27/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Bureau Veritas Consumer Products Services | 2025-04-16 | No Information Submitted |  | N | N | 1.41 |  |  | 400 | 600 | 800 | 2.3446 | 4.6893 | 7.0339 | 11.7231 | 17.5847 | 23.4463 | 93.116 | 95.522 | 96.14 | 96.36 | 96.122 | 95.758 | 96.0057 | 88.828 | 93.234 | 94.558 | 95.326 | 95.368 | 95.13 | 94.8818 | 84.788 | 90.99 | 93.026 | 94.34 | 94.644 | 94.628 | 93.8083 | 2025-06-23
Trystar, LLC | OZPCS-RS35-FB0 {208V} | N | Y | N | N | N | N | Y* | N | 35 kVA, 208 Vac, Bi-directional Transformerless Grid Support Utility Interactive Battery Inverter | 34.3317 | 208 | 95 | Bureau Veritas | [5/27/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Bureau Veritas Consumer Products Services | 2025-04-16 | No Information Submitted |  | N | N | 2.14 |  |  | 400 | 600 | 800 | 3.4332 | 6.8663 | 10.2995 | 17.1658 | 25.7487 | 34.3317 | 94.02 | 95.864 | 96.3 | 96.344 | 96.046 | 95.632 | 96.0282 | 89.814 | 93.742 | 94.896 | 95.498 | 95.546 | 95.25 | 95.1236 | 86.122 | 91.634 | 93.378 | 94.586 | 94.832 | 94.738 | 94.0929 | 2025-06-23
Trystar, LLC | OZPCS-RS35-FB1 {208V} | N | Y | N | N | N | N | Y* | N | 35 kVA, 208 Vac, Bi-directional Transformerless Grid Support Utility Interactive Battery Inverter | 34.3317 | 208 | 95 | Bureau Veritas | [5/27/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Bureau Veritas Consumer Products Services | 2025-04-16 | No Information Submitted |  | N | N | 2.14 |  |  | 400 | 600 | 800 | 3.4332 | 6.8663 | 10.2995 | 17.1658 | 25.7487 | 34.3317 | 94.02 | 95.864 | 96.3 | 96.344 | 96.046 | 95.632 | 96.0282 | 89.814 | 93.742 | 94.896 | 95.498 | 95.546 | 95.25 | 95.1236 | 86.122 | 91.634 | 93.378 | 94.586 | 94.832 | 94.738 | 94.0929 | 2025-06-23
Trystar, LLC | OZPCS-EP40-000 {480V} | N | Y | N | N | N | N | Y* | N | 40 kW, 480 Vac,Grid Support Utility Interactive Battery Inverter | 39.54 | 480 | 97 | Intertek | [2/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2024-05-01 | No Information Submitted |  | N | N | 25.79 |  |  | 550 | 700 | 820 | 3.954 | 7.908 | 11.862 | 19.77 | 29.655 | 39.54 | 92.7224 | 95.5095 | 96.1882 | 96.6919 | 96.6106 | 96.3158 | 96.3517 | 94.5887 | 96.4696 | 97.0807 | 97.1781 | 97.0791 | 96.8473 | 96.9584 | 95.476 | 97.0257 | 97.576 | 97.4427 | 97.3493 | 97.0857 | 97.2918 | 2024-06-21
Trystar, LLC | OZPCS-RS40-BB1 {480V} | N | Y | N | N | N | N | Y* | N | 40 kVA, 480 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 39.54 | 480 | 97 | Intertek | [2/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2024-05-01 | No Information Submitted |  | N | N | 25.79 |  |  | 550 | 700 | 820 | 3.954 | 7.908 | 11.862 | 19.77 | 29.655 | 39.54 | 92.7224 | 95.5095 | 96.1882 | 96.6919 | 96.6106 | 96.3158 | 96.3517 | 94.5887 | 96.4696 | 97.0807 | 97.1781 | 97.0791 | 96.8473 | 96.9584 | 95.476 | 97.0257 | 97.576 | 97.4427 | 97.3493 | 97.0857 | 97.2918 | 2024-08-12
Trystar, LLC | OZPCS-RS40-FB1 {480V} | N | Y | N | N | N | N | Y* | N | 40 kVA, 480 Vac, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter | 39.54 | 480 | 97 | Intertek | [2/27/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Intertek | 2024-05-01 | No Information Submitted |  | N | N | 25.79 |  |  | 550 | 700 | 820 | 3.954 | 7.908 | 11.862 | 19.77 | 29.655 | 39.54 | 92.7224 | 95.5095 | 96.1882 | 96.6919 | 96.6106 | 96.3158 | 96.3517 | 94.5887 | 96.4696 | 97.0807 | 97.1781 | 97.0791 | 96.8473 | 96.9584 | 95.476 | 97.0257 | 97.576 | 97.4427 | 97.3493 | 97.0857 | 97.2918 | 2024-08-12
Trystar, LLC | OZPCS-RS40-Fxx {480V} | N | N | Y | Y | Y | Y | Y* | Y | 40 kVA, 480V, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, where xx = 00 or 01 | 39.894 | 480 | 96 | No Information Submitted | No Information Submitted | Intertek | [08/18/2021] | [Rev 6.1.3.0] | 2020-07-13 | [08/18/2021] | 2021-10-11 | Intertek | 2021-08-23 | 2021-10-11 | Formerly Oztek Corp., OZPCS-RS40-Fxx {480V} | N | N | 1105.1 |  |  | 550 | 700 | 820 | 3.9894 | 7.9789 | 11.9683 | 19.9472 | 29.9208 | 39.8944 | 88.2974 | 93.8846 | 95.1099 | 96.1351 | 96.3208 | 96.2069 | 95.688 | 90.2558 | 94.5724 | 96.0317 | 96.673 | 96.7941 | 96.8675 | 96.3082 | 91.3166 | 95.037 | 96.3475 | 97.0717 | 97.18 | 97.0126 | 96.7073 | 2020-07-13 | 2024-04-02
Trystar, LLC | OZPCS-RS40-Bxx {480V} | N | N | Y | Y | Y | Y | Y* | Y | 40 kVA, 480V, Bi-directional, Transformerless Grid Support Utility Interactive Battery Inverter, where xx = 00 or 01 | 39.913 | 480 | 96.5 | No Information Submitted | No Information Submitted | Intertek | [08/18/2021] | [Rev 6.1.3.0] | 2020-07-13 | [08/18/2021] | 2021-10-11 | Intertek | 2021-08-23 | 2021-10-11 | Formerly Oztek Corp., OZPCS-RS40-Bxx {480V} | N | N | 1066.26 |  |  | 550 | 700 | 820 | 3.9913 | 7.9826 | 11.9739 | 19.9565 | 29.9347 | 39.913 | 89.3471 | 94.177 | 95.7028 | 96.5763 | 96.7765 | 96.5956 | 96.1694 | 91.2397 | 94.7757 | 96.2649 | 97.0519 | 97.2428 | 97.1237 | 96.7159 | 92.4802 | 95.5723 | 96.7908 | 97.4192 | 97.5042 | 97.4004 | 97.098 | 2020-07-13 | 2024-04-02
Univix Power Solutions | UVX5KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 5.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 5 | 240 | 97 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-14 |  |  | N | N | 22.6 |  |  | 180 | 360 | 430 | 0.50897 | 1.0179 | 1.5269 | 2.5448 | 3.8172 | 5.0897 | 94.5721 | 95.7324 | 96.199 | 96.9205 | 97.1879 | 96.5929 | 96.8059 | 95.3063 | 96.2687 | 96.6896 | 97.405 | 97.7767 | 97.0844 | 97.3593 | 95.1065 | 95.9659 | 96.7169 | 97.1871 | 97.6379 | 96.8477 | 97.2084 | 2025-09-11
Univix Power Solutions | UVX6KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 6.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 6 | 240 | 97 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-14 |  |  | N | N | 22.99 |  |  | 200 | 360 | 430 | 0.61172 | 1.2234 | 1.8352 | 3.0586 | 4.5879 | 6.1172 | 94.7309 | 95.9167 | 96.2983 | 97.0306 | 97.2104 | 96.6573 | 96.8717 | 95.4385 | 96.4205 | 96.8113 | 97.5204 | 97.9205 | 97.3246 | 97.4993 | 95.0737 | 96.0519 | 96.3668 | 97.2284 | 97.6482 | 96.9604 | 97.1891 | 2025-09-11
Univix Power Solutions | UVX7.6KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.6 | 240 | 97 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-14 |  |  | N | N | 30.71 |  |  | 220 | 360 | 430 | 0.77647 | 1.5529 | 2.3294 | 3.8824 | 5.8235 | 7.7647 | 94.704 | 95.6896 | 96.2301 | 96.8168 | 97.2671 | 96.6847 | 96.8376 | 95.6279 | 96.3707 | 96.8002 | 97.4326 | 97.9295 | 97.2381 | 97.4851 | 95.2316 | 96.1461 | 96.6907 | 97.0141 | 97.5326 | 97.0789 | 97.1386 | 2025-09-11
Univix Power Solutions | UVX8KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 8.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 8 | 240 | 97.5 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-14 |  |  | N | N | 17.4 |  |  | 250 | 360 | 430 | 0.80842 | 1.6168 | 2.4252 | 4.0421 | 6.0631 | 8.0842 | 93.9828 | 95.4242 | 96.3466 | 97.3564 | 97.9158 | 96.8513 | 97.2749 | 93.9512 | 95.642 | 96.5865 | 97.2694 | 97.927 | 97.0134 | 97.3091 | 94.069 | 95.4947 | 96.4256 | 97.322 | 97.6876 | 96.993 | 97.1703 | 2025-09-11
Univix Power Solutions | UVX10KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 10.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 10 | 240 | 97 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-14 |  |  | N | N | 33.64 |  |  | 280 | 360 | 430 | 1.018 | 2.035 | 3.053 | 5.088 | 7.632 | 10.177 | 94.69 | 95.94 | 96.4 | 96.8 | 97.34 | 96.75 | 96.91 | 95.39 | 96.33 | 96.85 | 97.45 | 97.97 | 97.37 | 97.51 | 94.93 | 95.96 | 96.65 | 97.01 | 97.56 | 97.03 | 97.12 | 2025-09-11
Univix Power Solutions | UVX12KLNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 12.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 12 | 240 | 96 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-15 |  |  | N | N | 13.202 |  |  | 200 | 360 | 430 | 1.2214 | 2.4427 | 3.6641 | 6.1068 | 9.1601 | 12.2135 | 93.588 | 95.318 | 95.52 | 95.804 | 95.494 | 95.612 | 95.4831 | 94.262 | 96.132 | 96.662 | 96.872 | 96.622 | 96.294 | 96.544 | 94.002 | 96.18 | 96.74 | 96.876 | 96.678 | 96.362 | 96.5793 | 2025-09-11
Univix Power Solutions | UVX16LNA {240V} | Y | Y | Y | Y | Y | Y | Y* |  | 16.0 kW, 240 Vac Grid Support Utility Interactive Inverter | 16 | 240 | 96 | SGS | [5/28/205] | SGS | [5/28/205] | [V1.04.06(DSP), V1.03.06(ARM)] | 2025-09-11 | [5/14/205] | 2025-09-11 | SGS | 2025-05-15 |  |  | N | N | 20.465 |  |  | 220 | 360 | 430 | 1.6199 | 3.2398 | 4.8596 | 8.0994 | 12.1491 | 16.1988 | 93.662 | 95.358 | 95.802 | 95.93 | 95.51 | 96.18 | 95.5852 | 94.188 | 96.06 | 96.548 | 96.876 | 96.636 | 96.35 | 96.5348 | 94.088 | 95.998 | 96.536 | 96.946 | 96.692 | 96.25 | 96.5657 | 2025-09-11
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 6KW {240V} | Y | Y | Y | Y | Y | N | N | N | 6 kW, 240 Vac Split Phase, Transformerless Grid Support Utility Interactive Inverter | 6 | 240 | 90.5 | Intertek | [11/18/2024] | Intertek | [11/18/2024] | [V01.14] | 2025-05-01 | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 15 |  |  | 250 | 370 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 80.54 | 88.08 | 90.48 | 91.91 | 92.06 | 91.51 | 91.15 | 76.64 | 86.18 | 89.25 | 91.47 | 92.15 | 92.15 | 90.74 | 75.32 | 84.7 | 88.23 | 90.81 | 91.67 | 91.76 | 90.08 | 2025-05-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 6KW {120V} | Y | Y | Y | Y | Y | N | N | N | 6 kW, 120 Vac Split Phase, Transformerless Grid Support Utility Interactive Inverter | 6.0177 | 120 | 93.5 | Intertek | [11/18/2024] | Intertek | [11/18/2024] | [V01.14] | 2023-05-11 | [8/19/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 43 |  |  | 250 | 370 | 500 | 0.60177 | 1.2035 | 1.8053 | 3.0088 | 4.5132 | 6.0177 | 84.5455 | 90.3878 | 92.4318 | 93.9429 | 94.4517 | 94.3979 | 93.5003 | 83.7684 | 90.3217 | 92.4553 | 94.1133 | 94.8535 | 94.8931 | 93.7422 | 80.8311 | 88.8891 | 90.9986 | 93.3728 | 94.0658 | 94.308 | 92.7761 | 2023-05-22 | 2025-05-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP 12KW Optimum {120V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 120 Vac Grid Support Utility Interactive Inverter | 9.0186 | 120 | 95.5 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-06-03 | [3/13/2024] | 2024-06-03 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-06-03 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP 12KW Optimum {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.0186 | 240 | 95.5 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-06-11 | [3/13/2024] | 2024-06-11 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-06-11 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 12KW {120V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 120 Vac Grid Support Utility Interactive Inverter | 9.0186 | 120 | 95.5 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-06-03 | [3/13/2024] | 2024-06-03 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-06-03 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 12KW {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.0186 | 240 | 95.5 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-06-11 | [3/13/2024] | 2024-06-11 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 0.90186 | 1.8037 | 2.7056 | 4.5093 | 6.764 | 9.0186 | 91.582 | 92.866 | 94.596 | 95.812 | 95.446 | 95.614 | 95.3577 | 92.09 | 93.34 | 94.958 | 96.246 | 96.376 | 96.09 | 95.841 | 89.336 | 92.066 | 93.56 | 95.2 | 95.95 | 95.686 | 95.0337 | 2024-06-11 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP 12KW Premium {120V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 120 Vac Grid Support Utility Interactive Inverter | 10.029 | 120 | 95 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-08-12 | [5/20/2024] | 2024-08-12 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 1.0029 | 2.0058 | 3.0087 | 5.0145 | 7.5217 | 10.029 | 90.8464 | 94.1071 | 94.9509 | 95.2844 | 95.0472 | 94.9427 | 94.8652 | 91.4204 | 94.5211 | 95.4529 | 95.936 | 95.4773 | 95.0275 | 95.3381 | 88.6076 | 93.0581 | 94.426 | 95.1626 | 95.1729 | 94.8367 | 94.6959 | 2024-08-12 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP 12KW Premium {240V} | Y | Y | Y | Y | Y | Y | Y* | Y | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 10.029 | 240 | 95 | Intertek | [9/10/2024] | Intertek | [9/10/2024] | [36-004641-xxG] | 2024-08-12 | [5/20/2024] | 2024-08-12 | CSA Group | 2024-09-04 | 2024-11-01 |  | N | N | 4 |  |  | 285 | 360 | 500 | 1.0029 | 2.0058 | 3.0087 | 5.0145 | 7.5217 | 10.029 | 90.8464 | 94.1071 | 94.9509 | 95.2844 | 95.0472 | 94.9427 | 94.8652 | 91.4204 | 94.5211 | 95.4529 | 95.936 | 95.4773 | 95.0275 | 95.3381 | 88.6076 | 93.0581 | 94.426 | 95.1626 | 95.1729 | 94.8367 | 94.6959 | 2024-08-12 | 2024-11-01
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 15KW {240V} | Y | Y | Y | Y | Y | N | N |  | 15 kW, 240 Vac Grid Support Utility Interactive Inverter | 14.79 | 240 | 97 | Intertek/ETL | [5/29/2026] | Intertek/ETL | [5/29/2026] | [36-105771, 36-105772] | 2026-07-13 | [5/29/2026] | 2026-07-13 | No Information Submitted | No Information Submitted |  |  | N | N | 42 |  |  | 150 | 360 | 450 | 1.479 | 2.958 | 4.437 | 7.395 | 11.093 | 14.79 | 90.78 | 94.72 | 95.88 | 96.41 | 96.25 | 96.04 | 95.94 | 93.68 | 98.03 | 97.76 | 97.98 | 97.68 | 98.02 | 97.63 | 94.61 | 96.87 | 97.77 | 98.11 | 98.25 | 98.11 | 97.94 | 2026-07-13 |  | N | N | N | Y | N | N | N | N | N
VOLTRONIC POWER TECHNOLOGY (SHENZHEN) CORP. | InfiniSolar WP LV 15KW {120V} | Y | Y | Y | Y | Y | N | N |  | 15 kW, 120 Vac Grid Support Utility Interactive Inverter | 15.036 | 120 | 96 | Intertek/ETL | [5/29/2026] | Intertek/ETL | [5/29/2026] | [36-105771, 36-105772] | 2026-07-13 | [5/29/2026] | 2026-07-13 | No Information Submitted | No Information Submitted |  |  | N | N | 42 |  |  | 150 | 360 | 450 | 1.504 | 3.007 | 4.511 | 7.518 | 11.277 | 15.036 | 90.72 | 94.02 | 94.9 | 95.17 | 94.88 | 94.64 | 94.72 | 91.1 | 96.38 | 96.66 | 96.72 | 96.67 | 96.24 | 96.42 | 94.65 | 95.93 | 96.37 | 96.53 | 96.4 | 96.23 | 96.32 | 2026-07-13 |  | N | N | N | Y | N | N | N | N | N
Wanbang Digital Energy Co., Ltd. | SI104LULA00 {208V} | Y | Y | N | N | N | N | Y* | Y | 8.3 kW, 208 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 8.323 | 208 | 97 | CSA Group | [9/7/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-14 | 2024-02-21 |  | N | N | 5.03 |  |  | 320 | 360 | 480 | 0.832 | 1.665 | 2.497 | 4.162 | 6.243 | 8.323 | 96.79 | 97.5 | 97.58 | 97.36 | 96.96 | 96.44 | 97.11 | 96.6 | 97.58 | 97.65 | 97.43 | 97.04 | 96.56 | 97.18 | 95.8 | 97.36 | 97.57 | 97.42 | 97.01 | 96.57 | 97.11 | 2024-02-21
Wanbang Digital Energy Co., Ltd. | SI104LULA00 {240V} | Y | Y | N | N | N | N | Y* | Y | 9.6 kW, 240 Vac, Bi-directional, Transformerless Grid Support Utility Interactive PV and Battery Inverter | 9.58 | 240 | 97 | CSA Group | [9/7/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | CSA Group | 2023-09-14 | 2024-02-21 |  | N | N | 5.42 |  |  | 320 | 360 | 480 | 0.958 | 1.916 | 2.874 | 4.79 | 7.185 | 9.58 | 95.07 | 96.6 | 97.07 | 97.19 | 96.95 | 96.55 | 96.9 | 94.86 | 96.68 | 97.15 | 97.26 | 97.05 | 96.69 | 96.98 | 94.02 | 96.48 | 97.07 | 97.26 | 97.08 | 96.74 | 96.94 | 2024-02-21
WSTECH GmbH | APS800-ES-1-440-5 {440V} | N | N | Y | Y | Y | N | N | N | 800 kW, 440 Vac, Grid Support Utility Interactive Centeral Battery Inverter | 814.167 | 440 | 97.5 | No Information Submitted | No Information Submitted | MET | [10/12/2020] | [APU V3130 APMC V2040] | 2020-11-12 | [10/12/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 1000 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE216. | N | N | 91.4 |  |  | 648 | 1000 | 1500 | 81.4167 | 162.8334 | 244.2501 | 407.0835 | 610.6252 | 814.1669 | 96.8994 | 97.9207 | 98.1472 | 98.0855 | 97.7317 | 97.3005 | 97.8104 | 97.156 | 97.9031 | 98.0845 | 97.9812 | 97.697 | 97.2751 | 97.7708 | 96.5182 | 97.3518 | 97.6259 | 97.6679 | 97.3419 | 96.9571 | 97.3927 | 2020-11-12
WSTECH GmbH | APS870-ES-1-480-5 {480V} | N | N | Y | Y | Y | Y | N | N | 870 kW, 480 Vac, Grid Support Utility Interactive Centeral Battery Inverter | 872.029 | 480 | 98 | No Information Submitted | No Information Submitted | MET | [04/08/2021] | [APU V3130 APMC V2050] | 2021-07-01 | [04/08/2021] | 2021-07-01 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 91.402 |  |  | 770 | 1000 | 1470 | 87.2029 | 174.4058 | 261.6087 | 436.0145 | 654.0218 | 872.029 | 97.0815 | 98.1883 | 98.4162 | 98.4017 | 98.1322 | 97.7562 | 98.1648 | 95.7664 | 97.2807 | 97.8339 | 98.0408 | 97.8593 | 97.5271 | 97.7651 | 96.9374 | 97.6397 | 97.8465 | 97.7946 | 97.5592 | 97.1756 | 97.6031 | 2021-07-01
WSTECH GmbH | APS1600-ES-2-440-5 {440V} | N | N | Y | Y | Y | N | N | N | 1600 kW, 440 Vac, Grid Support Utility Interactive Centeral Battery Inverter | 1626.952 | 440 | 98 | No Information Submitted | No Information Submitted | MET | [10/12/2020] | [APU V3130 APMC V2040] | 2020-11-12 | [10/12/2020] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE216. | N | N | 91.4 |  |  | 648 | 1000 | 1500 | 162.6952 | 325.3904 | 488.0856 | 813.476 | 1220.214 | 1626.952 | 98.0396 | 98.5839 | 98.6684 | 98.5329 | 98.2151 | 97.8585 | 98.3298 | 96.9836 | 97.9106 | 98.1157 | 98.1085 | 97.8527 | 97.453 | 97.8861 | 96.318 | 97.3792 | 97.6608 | 97.7017 | 97.437 | 97.0028 | 97.4501 | 2020-11-12
WSTECH GmbH | APS1740-ES-2-480-5 {480V} | N | N | Y | Y | Y | Y | N | N | 1735 kW, 480 Vac, Grid Support Utility Interactive Centeral Battery Inverter | 1735.36 | 480 | 97.5 | No Information Submitted | No Information Submitted | MET | [04/08/2021] | [APU V3130 APMC V2050] | 2021-07-01 | [04/08/2021] | 2021-07-01 | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 91.402 |  |  | 770 | 1000 | 1470 | 173.536 | 347.0721 | 520.6081 | 867.6802 | 1301.5204 | 1735.3605 | 96.2018 | 97.6354 | 98.0243 | 98.1239 | 97.9169 | 97.5975 | 97.8746 | 95.6963 | 97.2746 | 97.7805 | 97.9519 | 97.7577 | 97.4332 | 97.6784 | 94.3845 | 96.4707 | 97.0706 | 97.4161 | 97.3403 | 97.06 | 97.1481 | 2021-07-01
Xiamen Kehua Digital Energy Tech Co., Ltd | iStoragE2A 7600 {240V} | Y | Y | N | N | N | N | N | N | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.581 | 240 | 97 | Intertek | [10/18/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.7581 | 1.5162 | 2.2743 | 3.7905 | 5.6858 | 7.581 | 94.2651 | 95.2225 | 96.163 | 96.9234 | 97.1125 | 97.0636 | 96.748 | 95.2164 | 96.1836 | 96.7935 | 97.3649 | 97.6024 | 97.5348 | 97.2857 | 94.8243 | 95.8334 | 96.5515 | 97.2034 | 97.4231 | 97.3541 | 97.0855 | 2023-01-23
Xiamen Kehua Digital Energy Tech Co., Ltd | iStoragE2A 9600 {240V} | Y | Y | N | N | N | N | N | N | 9.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.5733 | 240 | 97 | Intertek | [10/18/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.95733 | 1.9147 | 2.872 | 4.7866 | 7.1799 | 9.5733 | 94.324 | 95.4338 | 96.4736 | 97.0126 | 97.0914 | 97.0133 | 96.8032 | 95.7635 | 96.4127 | 97.0422 | 97.4839 | 97.5735 | 97.4048 | 97.352 | 94.8907 | 95.9847 | 96.8438 | 97.3145 | 97.3946 | 97.234 | 97.133 | 2023-01-23
Xiamen Kehua Digital Energy Tech Co., Ltd | iStoragE2A 10000 {240V} | Y | Y | N | N | N | N | N | N | 10 kW, 240 Vac Grid Support Utility Interactive Inverter | 9.9563 | 240 | 97 | Intertek | [10/18/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 0.99563 | 1.9913 | 2.9869 | 4.9782 | 7.4672 | 9.9563 | 94.3337 | 95.6136 | 96.5122 | 97.0308 | 97.0728 | 96.9826 | 96.8097 | 95.7935 | 96.475 | 97.0733 | 97.5049 | 97.543 | 97.3726 | 97.3468 | 95.184 | 96.0843 | 96.883 | 97.3434 | 97.3652 | 97.2134 | 97.1439 | 2023-01-23
Xiamen Kehua Digital Energy Tech Co., Ltd | iStoragE2A 11400 {240V} | Y | Y | N | N | N | N | N | N | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.3705 | 240 | 97 | Intertek | [10/18/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.1371 | 2.2741 | 3.4112 | 5.6853 | 8.5279 | 11.3705 | 94.3642 | 96.055 | 96.9052 | 97.1019 | 97.0437 | 96.9028 | 96.8756 | 95.8125 | 96.7944 | 97.3353 | 97.6036 | 97.4725 | 97.2634 | 97.3728 | 95.284 | 96.5532 | 97.1622 | 97.414 | 97.3038 | 97.0831 | 97.1806 | 2023-01-23
Xiamen Kehua Digital Energy Tech Co., Ltd | iStoragE2A 12000 {240V} | Y | Y | N | N | N | N | N | N | 12 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.9682 | 240 | 97 | Intertek | [10/18/2022] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 2.5 |  |  | 300 | 370 | 440 | 1.1968 | 2.3936 | 3.5905 | 5.9841 | 8.9761 | 11.9682 | 94.3841 | 96.0625 | 96.9237 | 97.1216 | 97.0131 | 96.8713 | 96.8654 | 95.8343 | 96.815 | 97.3428 | 97.6232 | 97.4548 | 97.223 | 97.3683 | 95.3154 | 96.5735 | 97.1839 | 97.4422 | 97.282 | 97.04 | 97.1777 | 2023-01-23
Xiamen Kehua Digital Energy Tech Co., Ltd | BCS75K-B-HM-US X2 {480V} | N | Y | N | N | N | N | N | N | 75 kW, 480 Vac Grid Support Utility Interactive Battey Inverter | 75.0844 | 480 | 98.5 | Intertek | [1/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 62.1 |  |  | 720 | 1080 | 1450 | 7.5084 | 15.0169 | 22.5253 | 37.5422 | 56.3133 | 75.0844 | 98.338 | 98.64 | 98.8 | 98.632 | 98.56 | 98.426 | 98.5923 | 98.05 | 98.54 | 98.75 | 98.56 | 98.45 | 98.34 | 98.4921 | 97.56 | 98.34 | 98.65 | 98.5 | 98.4 | 98.28 | 98.4084 | 2024-03-21
Xiamen Kehua Digital Energy Tech Co., Ltd | BCS100K-B-HM-US X2 {480V} | N | Y | N | N | N | N | N | N | 100 kW, 480 Vac Grid Support Utility Interactive Battey Inverter | 100.073 | 480 | 98.5 | Intertek | [1/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 60.8 |  |  | 720 | 1010 | 1300 | 10.007 | 20.015 | 30.022 | 50.036 | 75.055 | 100.073 | 98.23 | 98.43 | 98.8 | 98.75 | 98.5 | 98.35 | 98.57 | 98.1 | 98.37 | 98.74 | 98.65 | 98.46 | 98.23 | 98.5 | 97.89 | 98.3 | 98.64 | 98.53 | 98.4 | 98.13 | 98.42 | 2024-03-21
Xiamen Kehua Digital Energy Tech Co., Ltd | BCS125K-B-HM-US X2 {480V} | N | Y | N | N | N | N | N | N | 125 kW, 480 Vac Grid Support Utility Interactive Battey Inverter | 125.015 | 480 | 98.5 | Intertek | [1/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 60 |  |  | 720 | 1010 | 1300 | 12.502 | 25.003 | 37.505 | 62.508 | 93.761 | 125.015 | 98.37 | 98.64 | 98.8 | 98.65 | 98.54 | 98.47 | 98.59 | 98.29 | 98.54 | 98.7 | 98.54 | 98.47 | 98.38 | 98.5 | 97.88 | 98.44 | 98.64 | 98.44 | 98.4 | 98.27 | 98.41 | 2024-03-21
Xiamen Kehua Digital Energy Tech Co., Ltd | BCS150K-B-HM-US X2 {600V} | N | Y | N | N | N | N | N | N | 150 kW, 600 Vac Grid Support Utility Interactive Battey Inverter | 150.015 | 600 | 98.5 | Intertek | [1/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 62.4 |  |  | 920 | 1185 | 1450 | 15.002 | 30.003 | 45.005 | 75.008 | 112.511 | 150.015 | 98.34 | 98.65 | 98.8 | 98.65 | 98.52 | 98.44 | 98.58 | 98.27 | 98.56 | 98.71 | 98.52 | 98.45 | 98.34 | 98.49 | 97.79 | 98.43 | 98.62 | 98.47 | 98.42 | 98.3 | 98.42 | 2024-03-21
Xiamen Kehua Digital Energy Tech Co., Ltd | BCS175K-B-HM-US X2 {600V} | N | Y | N | N | N | N | N | N | 175 kW, 600 Vac Grid Support Utility Interactive Battey Inverter | 175.017 | 600 | 98.5 | Intertek | [1/16/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 64.4 |  |  | 920 | 1185 | 1450 | 17.502 | 35.003 | 52.505 | 87.509 | 131.263 | 175.017 | 98.34 | 98.64 | 98.8 | 98.65 | 98.55 | 98.42 | 98.59 | 98.09 | 98.51 | 98.72 | 98.55 | 98.45 | 98.35 | 98.49 | 97.75 | 98.33 | 98.63 | 98.47 | 98.41 | 98.27 | 98.41 | 2024-03-21
Xiamen Kehua Digital Energy Tech Co.,Ltd. | BCS500K-S-HLC {690V} | N | Y | N | N | N | N | N |  | 498 kW, 690 Vac Grid Support Utility Interactive Inverter Energy Storage Converter | 498.247 | 690 | 98.5 | TUV Rheinland of North America | [05/20/2026] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 997 |  |  | 1060 | 1280 | 1500 | 49.825 | 99.649 | 149.474 | 249.123 | 373.685 | 498.247 | 98.07 | 97.68 | 98.48 | 98.78 | 98.76 | 98.35 | 98.63 | 97.02 | 96.88 | 97.85 | 98.51 | 98.51 | 98.06 | 98.27 | 95.66 | 96.15 | 97.39 | 98.19 | 98.22 | 97.82 | 97.89 | 2026-08-11 |  | N | N | N | N | N | Y | N | N | No Information Submitted
Yaskawa Solectria Solar | XGI 1500-125/125-3S {600V} | Y | Y | N | N | N | N | N | Y | 125 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 125 | 600 | 98.5 | TUV Rheinland of North America | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-06-11 |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 12.5111 | 25.0222 | 37.5333 | 62.5555 | 93.8333 | 125.111 | 97.8024 | 98.2426 | 98.5526 | 98.7074 | 98.7076 | 98.8392 | 98.6361 | 97.3452 | 97.8518 | 98.2734 | 98.4604 | 98.5148 | 98.4916 | 98.3933 | 97.1044 | 97.4718 | 98.1588 | 98.6012 | 98.396 | 98.369 | 98.3114 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500-166/166-3S {600V} | Y | Y | N | N | N | N | N | Y | 166 kW, 600 Vac, Grid-Support Utility Interactive Inverter | 166 | 600 | 98.5 | TUV Rheinland of North America | [1/30/2023] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2024-06-11 |  | N | N | 0.33 |  |  | 860 | 1000 | 1250 | 16.6009 | 33.2018 | 49.8028 | 83.0046 | 124.5069 | 166.0092 | 97.973 | 98.9236 | 99.2198 | 98.9218 | 98.8862 | 98.7352 | 98.8915 | 97.9882 | 98.0974 | 98.4554 | 98.6134 | 98.5788 | 98.4484 | 98.517 | 97.5094 | 97.6668 | 97.8232 | 98.1354 | 98.104 | 97.9988 | 98.026 | 2024-06-11
Yaskawa Solectria Solar | XGI 1500-0.50MW-600 {600V} | Y | Y | N | N | N | N | N | Y | 500 kW, 600Vac Grid Support Utility Interactive Inverter | 500 | 600 | 98.5 | TUV Rheinland of North America | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-05-12 |  | N | N | 36.85 |  |  | 860 | 1100 | 1250 | 50.496 | 100.992 | 151.488 | 252.48 | 378.72 | 504.96 | 97 | 98.58 | 98.9 | 99.07 | 99.2 | 99.11 | 99.01 | 92.95 | 96.46 | 97.78 | 98.29 | 98.55 | 98.5 | 98.07 | 91.08 | 95.9 | 96.98 | 98.06 | 98.4 | 98.52 | 97.74 | 2025-05-12
Yaskawa Solectria Solar | XGI 1500-0.75MW-600 {600V} | Y | Y | N | N | N | N | N | Y | 750 kW, 600Vac Grid Support Utility Interactive Inverter | 750 | 600 | 98.5 | TUV Rheinland of North America | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-05-12 |  | N | N | 36.85 |  |  | 860 | 1100 | 1250 | 75.341 | 150.683 | 226.024 | 376.707 | 565.061 | 753.414 | 96.15 | 97.89 | 98.54 | 98.98 | 99.09 | 99.05 | 98.82 | 92.88 | 96.93 | 97.71 | 98.27 | 98.54 | 98.59 | 98.08 | 91.68 | 96.58 | 97.56 | 98.03 | 98.45 | 98.56 | 97.89 | 2025-05-12
Yaskawa Solectria Solar | XGI 1500-0.85MW-600 {600V} | Y | Y | N | N | N | N | N | Y | 850 kW, 600Vac Grid Support Utility Interactive Inverter | 850 | 600 | 98.5 | TUV Rheinland of North America | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-05-12 |  | N | N | 36.85 |  |  | 860 | 1100 | 1250 | 85.335 | 170.67 | 256.004 | 426.674 | 640.011 | 853.348 | 96.54 | 98.26 | 98.81 | 99.09 | 99.14 | 99.07 | 98.94 | 93.23 | 97 | 97.98 | 98.42 | 98.62 | 98.58 | 98.2 | 90.95 | 95.79 | 97.4 | 97.98 | 98.3 | 98.35 | 97.71 | 2025-05-12
Yaskawa Solectria Solar | XGI 1500-0.99MW-600 {600V} | Y | Y | N | N | N | N | N | Y | 999 kW, 600Vac Grid Support Utility Interactive Inverter | 999 | 600 | 98.5 | TUV Rheinland of North America | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-05-12 |  | N | N | 36.85 |  |  | 860 | 1100 | 1250 | 99.969 | 199.938 | 299.906 | 499.844 | 749.766 | 999.688 | 96.96 | 98.22 | 98.75 | 99.07 | 99.09 | 98.96 | 98.91 | 94.3 | 97.15 | 98.02 | 98.51 | 98.58 | 98.47 | 98.25 | 92.65 | 96.26 | 97.33 | 98.04 | 98.21 | 98.17 | 97.74 | 2025-05-12
Yaskawa Solectria Solar | XGI 1500-1MW-600 {600V} | Y | Y | N | N | N | N | N | Y | 1000 kW, 600Vac Grid Support Utility Interactive Inverter | 1000 | 600 | 98.5 | TUV Rheinland of North America | [3/13/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | 2025-05-12 |  | N | N | 36.85 |  |  | 860 | 1100 | 1250 | 100.21 | 200.42 | 300.629 | 501.049 | 751.574 | 1002.098 | 96.96 | 98.22 | 98.75 | 99.07 | 99.09 | 98.96 | 98.91 | 94.3 | 97.15 | 98.02 | 98.51 | 98.58 | 98.47 | 98.25 | 92.65 | 96.26 | 97.33 | 98.04 | 98.21 | 98.17 | 97.74 | 2025-05-12
Zhejiang Hyxi Technology Co., Ltd | HYX-H-HSPA {240V} | Y | Y | N | N | N | N | N | N | 11.5kW, 240Vac Grid Support Utility Interactive Inverter | 11.147 | 240 | 96 | TUV Rheinland of North America | [1/5/2025] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  | N | N | 3.05 |  |  | 200 | 350 | 500 | 1.115 | 2.229 | 3.344 | 5.573 | 8.36 | 11.147 | 93.87 | 95.67 | 96.07 | 96.19 | 95.74 | 97.45 | 95.88 | 93.82 | 95.7 | 96.17 | 96.23 | 95.9 | 95.57 | 95.89 | 93.86 | 95.69 | 96.17 | 96.23 | 95.92 | 95.49 | 95.9 | 2025-03-21
Zhuhai Ruixu Electronic Technology Co., Ltd | RX-12K {208V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter | 9.8807 | 208 | 96.5 | Intertek | [10/18/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 24.1 |  |  | 190 | 380 | 510 | 0.98807 | 1.9761 | 2.9642 | 4.9403 | 7.4105 | 9.8807 | 91.2599 | 94.3745 | 95.5505 | 96.3072 | 96.3427 | 95.9977 | 95.9212 | 92.7067 | 95.4866 | 96.9869 | 97.2662 | 97.3087 | 97.1489 | 96.978 | 90.94 | 94.226 | 96.3799 | 97.1281 | 97.2907 | 97.2045 | 96.7357 | 2025-09-02
Zhuhai Ruixu Electronic Technology Co., Ltd | RX-12K {240V} | Y | Y | N | N | N | N | N |  | 11.4 kW, 240 Vac Grid Support Utility Interactive Inverter | 11.2981 | 240 | 96.5 | Intertek | [10/18/2024] | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted | No Information Submitted |  |  | N | N | 24 |  |  | 190 | 380 | 510 | 1.1298 | 2.2596 | 3.3894 | 5.649 | 8.4736 | 11.2981 | 92.0154 | 94.7699 | 95.7195 | 96.3851 | 96.3008 | 96.1752 | 95.9945 | 93.0107 | 95.727 | 96.7399 | 97.4337 | 97.3657 | 97.355 | 97.0482 | 91.9487 | 95.0137 | 96.5928 | 97.2894 | 97.1867 | 97.2073 | 96.8199 | 2025-09-02

## Data_Key
CEC Grid Support Inverters List Data Key
Updated | 2026-10-01
Column | Field Name | Explanation of Field | Field Format* | Require / Optional
A | Manufacturer Name | Equipment manufacturer name confirmed by a combination of documents (e.g., request form, certificate of compliance, manufacturer naming letter explaining relationship of multiple corporate entities under a single parent corporate entity). | Free form text entry | Required
B | Model Number | Equipment model number confirmed by the certificate of compliance. | Free form text entry | Required
C | Hybrid Inverter | Identifies if an inverter can accept DC input from both PV modules and batteries. Confirmed by the certificate of compliance or test report. | Y/N | Required
D | UL 1741 Supplement SB Certification | Identifies if the inverter was certified to UL 1741 Supplement B (SB). Confirmed by the certificate of compliance. | Y/N | Required if not submitting UL 1741 SA certification
E | UL 1741 Supplement SA Testing (SA8-13) | Identifies if the inverter was certified to UL 1741 Supplement A (SA) sections SA8-SA13. Confirmed by the certificate of compliance and test report. | Y/N | Required if not submitting UL 1741 SB certification
F | UL 1741 SA13 Volt-Var (RPP) | Identifies if the inverter had RPP enabled during testing for UL 1741 SA section SA13. Confirmed by the certificate of compliance and test report. | Y/N | Required if submitting UL 1741 SA certification
G | UL 1741 SA Freq-Watt Volt-Watt (SA14-15) | Identifies if the inverter was certified to UL 1741 SA sections SA14-SA15. Confirmed by the certificate of compliance and test report. | Y/N | Required if submitting UL 1741 SA certification
H | UL 1741 SA Disable Permit Service Limit Active Power (SA17-SA18) | Identifies if the inverter was certified to UL 1741 SA sections SA17-SA18. Confirmed by the certificate of compliance and test report. | Y/N | Optional, only if submitting UL 1741 SA certification
I | Common Smart Inverter Profile Conformance (CSIP) | Identifies if the manufactured supplied CSIP conformance documentation (test report or certificate). | Y/Y*/N | Optional, may be required by some utilities
J | Monitor Key Data Scheduling (Attestation) | Identifies if the manufactured provided the California IOU Monitor Key Data Scheduling Attestation Form. No longer collected. | - | -
K | Description | General description provided by the manufacturer. CEC staff may confirm and format. | Free form text entry | Required
L | Maximum Continuous Output Power at Unity Power Factor: kW | Measured inverter output power in AC kilowatts confirmed by test report. This measured value is not the inverter’s nominal AC output power rating. Test procedure at https://www.energy.ca.gov/sites/default/files/2020-06/2004-11-22_Sandia_Test_Protocol_ada.pdf. | Numerical decimal | Required
M | Nominal Voltage: Vac | Rated AC output voltage confirmed by the certificate of compliance or test report. | Numerical positive whole number | Required
N | Weighted Efficiency: % | Measured CEC-weighted conversion efficiency. Confirmed by test report. Test procedure at https://www.energy.ca.gov/sites/default/files/2020-06/2004-11-22_Sandia_Test_Protocol_ada.pdf. | Numerical decimal | Required
O | UL 1741 (3rd Ed.) Supplement SB Certification: Certifying Entity | Name of the Nationally Recognized Testing Laboratory (NRTL) that issued the certificate of compliance. | Text from drop down list | Required if submitting UL 1741 SB certification
P | UL 1741 (3rd Ed.) Supplement SB Certification: Certificate Date | Issue date of the certificate of compliance. | mm/dd/yyyy | Required if submitting UL 1741 SB certification
Q | UL 1741 Supplement SA Certification (SA8-SA13): Certifying Entity | Name of the Nationally Recognized Testing Laboratory (NRTL) that issued the certificate of compliance. | Text from drop down list | Required if submitting UL 1741 SA certification
R | UL 1741 Supplement SA Certification (SA8-SA13): Certificate Date | Issue date of the certificate of compliance. | mm/dd/yyyy | Required if submitting UL 1741 SA certification
S | UL 1741 Supplement SA Certification (SA8-SA13): Firmware Version(s) Tested | Firmware version for UL 1741 sections SA8-SA13. Confirmed by the certificate of compliance or test report. | Free form text entry | Required if submitting UL 1741 SA certification
T | UL 1741 SA13 Volt-Var: Listing Date | Date the product information was updated to include information for UL 1741 SA section SA13. | mm/dd/yyyy | Required if submitting UL 1741 SA certification
U | UL 1741 SA Freq-Watt Volt-Watt: Certificate Date | Issue date of the certificate of compliance that included UL 1741 SA sections SA14-SA15. | mm/dd/yyyy | Required if submitting UL 1741 SA certification
V | UL 1741 SA Disable Permit Service Limit Active Power: Listing Date | Date the product information was updated to include information for UL 1741 SA sections SA17-SA18. | mm/dd/yyyy | Required if submitting UL 1741 SA certification
W | Inverter CSIP Conformance: Issuing Entity | Name of entity that issued the CSIP conformance documentation. | Free form text entry | Optional, may be required by some utilities
X | Inverter CSIP Conformance: Issuing Document Date | Issue date of the CSIP conformance documentation. | mm/dd/yyyy | Optional, may be required by some utilities
Y | Monitor Key Data Scheduling Attestation: Listing Date | Date when information was updated to include the California IOU Monitor Key Data Scheduling Attestation. No longer collected. | - | -
Z | Notes | Additional information confirmed by CEC staff. | Free form text entry | Optional
AA | Built-In Meter | Identifies if the inverter includes a built-in meter. | Y/N | Required
AB | Microinverter | Identifies if the product is a microinverter. | Y/N | Required
AC | Night Tare Loss: W | Measured inverter standby power confirmed by test report. Test procedure at https://www.energy.ca.gov/sites/default/files/2020-06/2004-11-22_Sandia_Test_Protocol_ada.pdf. | Numerical decimal | Required
AD | Power Rating, Continuous, 40 deg C: kW | Field not used. | - | -
AE | Night Tare Loss, 40 deg C: W | Field not used. | - | -
AF-AH | Voltage (minimum, nominal, maximum): Vdc | Manufacturer specified DC input voltage to inverter during efficiency testing. Confirmed by test report. | Numerical decimal | Required
AI-AN | Power Level (10%, 20%, 30%, 50%, 75%, 100%): kW | Manufacturer specified nominal inverter output power in AC kilowatts at multiple power levels. Confirmed by test report. | Numerical decimal | Required
AO-AU | Efficiency at Vmin (10%, 20%, 30%, 50%, 75%, 100%): % | Measured conversion efficiency at multiple power levels with manufacturer specified Vmin DC input voltage. Confirmed by test report. Test procedure at https://www.energy.ca.gov/sites/default/files/2020-06/2004-11-22_Sandia_Test_Protocol_ada.pdf. | Numerical decimal | Required
AV-BB | Efficiency at Vnom (10%, 20%, 30%, 50%, 75%, 100%): % | Measured conversion efficiency at multiple power levels with manufacturer specified Vnom DC input voltage. Confirmed by test report. Test procedure at https://www.energy.ca.gov/sites/default/files/2020-06/2004-11-22_Sandia_Test_Protocol_ada.pdf. | Numerical decimal | Required
BC-BI | Efficiency at Vmax (10%, 20%, 30%, 50%, 75%, 100%): % | Measured conversion efficiency at multiple power levels with manufacturer specified Vmax DC input voltage. Confirmed by test report. Test procedure at https://www.energy.ca.gov/sites/default/files/2020-06/2004-11-22_Sandia_Test_Protocol_ada.pdf. | Numerical decimal | Required
BJ | Grid Support Listing Date | Date the product was initially included in the equipment list. | mm/dd/yyyy | Required
BK | Last Update | Date of the most recent revision to the product's information. | mm/dd/yyyy | Required when applicable
BL-BS | Anti-Islanding Group | Islanding detection method group provided by the manufacturer. See https://www.osti.gov/biblio/1463446. | Y/N/No Information Submitted | Required, at least one group must be a Yes.
* Numerous fields allow blanks, Not Applicable, and No Information Submitted in addition to the described field format.