## Power Control Systems
Power Control System (PCS) List
Data has not changed since October 12, 2026
Notes
(1) PCS model number must be identical to the model number on the UL 3141 certificate of compliance from the NRTL. Any text in curly brackets at the end of the model number is not part of the manufacturer's model number. The text in curly brackets indicates a distinguishing characteristic for model numbers with multiple configurations.
(2) NEM Integrity Mode per UL 3141 section 8.8.5. Zero set point means a zero export system with a point of reference behind the point of common coupling.
(3) NEM Integrity Mode per UL 3141 section 8.8.5. Dynamic set point means a system like the one described in UL 3141 section 8.8.5.1 note 3.
[11 empty] | PCS Functionality Operational Parameters |  | Electrical Ratings
Manufacturer | Model Number1 | End-product in which PCS is Integrated | UL 3141 Certificate of Compliance |  |  | PCS Functionality2,3 | Description of PCS Functionality | Scheduling Conformance per UL 3141 Annex A | Additional devices required for PCS functionality | Current Measurement Reference Points | Maximum Response Time | Time to Reach Steady State | Single Phase (L-N or L-L) or Three Phase (L-L-L) | Rated Operating Voltage(s) | Maximum Continuous Operating Current Rating (Controlled) | Maximum Continuous Operating Power Rating (Controlled) | Notes | Date Added to CEC List | Last Update to CEC List
|  |  | NRTL Issuing Certificate of Compliance | Edition of UL 3141 | Certificate Date (mm/dd/yyyy) |  |  | (yes/no) |  |  | (seconds) | (seconds) |  | (volts) | (Amps) | (kW) |  | (mm/dd/yyyy) | (mm/dd/yyyy)
Anker Innovations Limited | A17E1 | Inverter | SGS | OOI Issue 2 : 2024 | 2026-08-19 | ESS Export Only Mode | The ESS may export active power to the Area EPS during discharging but shall not import active power from the Area EPS for ESS charging purposes. | No | Electric Meter (CT-200_S) Optional Equipment: AS211, AX170-COMBINER, AX170-ATS | Point Of Common Coupling (PCC) | 0.5 | 0.8 | L-L | 240 | 32 | 7.68 |  | 2026-09-01
Anker Innovations Limited | A17E1 | Inverter | SGS | OOI Issue 2 : 2024 | 2026-08-19 | ESS Export Only Mode | The ESS may export active power to the Area EPS during discharging but shall not import active power from the Area EPS for ESS charging purposes. | No | Electric Meter (A17X7; CT model: CT-200, CT-50) Optional Equipment: AS211, AX170-COMBINER, AX170-ATS | Point Of Common Coupling (PCC) | 2 | 2.2 | L-L | 240 | 32 | 7.68 |  | 2026-09-01
Anker Innovations Limited | A17E1 | Inverter | SGS | OOI Issue 2 : 2024 | 2026-08-19 | ESS Import Only Mode | The ESS may import active power from the Area EPS for charging purposes but shall not export active power from the ESS to the Area EPS. | No | Electric Meter (CT-200_S) Optional Equipment: AS211, AX170-COMBINER, AX170-ATS | Point Of Common Coupling (PCC) | 0.5 | 0.8 | L-L | 240 | 32 | 7.68 |  | 2026-09-01
Anker Innovations Limited | A17E1 | Inverter | SGS | OOI Issue 2 : 2024 | 2026-08-19 | ESS Import Only Mode | The ESS may import active power from the Area EPS for charging purposes but shall not export active power from the ESS to the Area EPS. | No | Electric Meter (A17X7; CT model: CT-200, CT-50) Optional Equipment: AS211, AX170-COMBINER, AX170-ATS | Point Of Common Coupling (PCC) | 1.5 | 1.6 | L-L | 240 | 32 | 7.68 |  | 2026-09-01
Anker Innovations Limited | A17E1 | Inverter | SGS | OOI Issue 2 : 2024 | 2026-08-19 | ESS No Exchange Mode | The ESS shall not exchange active power with the Area EPS for charging or discharging purposes. | No | Electric Meter (CT-200_S) Optional Equipment: AS211, AX170-COMBINER, AX170-ATS | Point Of Common Coupling (PCC) | 0.4 | 0.6 | L-L | 240 | 32 | 7.68 |  | 2026-09-01
Anker Innovations Limited | A17E1 | Inverter | SGS | OOI Issue 2 : 2024 | 2026-08-19 | ESS No Exchange Mode | The ESS shall not exchange active power with the Area EPS for charging or discharging purposes. | No | Electric Meter (A17X7; CT model: CT-200, CT-50) Optional Equipment: AS211, AX170-COMBINER, AX170-ATS | Point Of Common Coupling (PCC) | 1.4 | 1.5 | L-L | 240 | 32 | 7.68 |  | 2026-09-01
Anker Innovations Limited | A17E1 | Inverter | SGS | OOI Issue 2 : 2024 | 2026-08-19 | ESS Unrestricted Mode | The ESS may import active power from Area EPS while charging and may export active power to the Area EPS while discharging. | No | Electric Meter (CT-200_S) Optional Equipment: AS211, AX170-COMBINER, AX170-ATS | Point Of Common Coupling (PCC) | 0.5 | 0.8 | L-L | 240 | 32 | 7.68 |  | 2026-09-01
Anker Innovations Limited | A17E1 | Inverter | SGS | OOI Issue 2 : 2024 | 2026-08-19 | ESS Unrestricted Mode | The ESS may import active power from Area EPS while charging and may export active power to the Area EPS while discharging. | No | Electric Meter (A17X7; CT model: CT-200, CT-50) Optional Equipment: AS211, AX170-COMBINER, AX170-ATS | Point Of Common Coupling (PCC) | 0.7 | 0.8 | L-L | 240 | 32 | 7.68 |  | 2026-09-01
Chint Power Systems America | CPS Energy Manager | Gateway | CSA Group | OOI Issue 2 : 2024 | 2026-02-12 | Export Limiting from all Sources (PEL) | Export limiting from all sources | No | Gateway (EHX2) and System Edge Box (SE-A3 or SE-A4) with integrated Gateway (EHX2) and Shanghai CHINT Power Systems Co., Ltd. Inverter (CPS SCA25KTL-DO/US-208) | Point Of Common Coupling (PCC) | 0.03 | 18.16 | L-N/L-L-L | 208 | 72 | 60 |  | 2026-08-21
Chint Power Systems America | CPS Energy Manager | Gateway | CSA Group | OOI Issue 2 : 2024 | 2026-02-12 | Export Limiting from all Sources (PEL) | Export limiting from all sources | No | Gateway (EHX2) and System Edge Box (SE-A3 or SE-A4) with integrated Gateway (EHX2) and Shanghai CHINT Power Systems Co., Ltd. Inverters (CPS SCAyKTL-DO/US-480) where y = 36, 50, or 60 | Point Of Common Coupling (PCC) | 0.03 | 18.16 | L-N/L-L-L | 480 | 72 | 60 |  | 2026-08-21
Chint Power Systems America | CPS Energy Manager-4G | Gateway | CSA Group | OOI Issue 2 : 2024 | 2026-02-12 | Export Limiting from all Sources (PEL) | Export limiting from all sources | No | Gateway (EHX2) and System Edge Box (SE-A3 or SE-A4) with integrated Gateway (EHX2) and Shanghai CHINT Power Systems Co., Ltd. Inverter (CPS SCA25KTL-DO/US-208) | Point Of Common Coupling (PCC) | 0.03 | 18.16 | L-N/L-L-L | 208 | 72 | 60 |  | 2026-08-21
Chint Power Systems America | CPS Energy Manager-4G | Gateway | CSA Group | OOI Issue 2 : 2024 | 2026-02-12 | Export Limiting from all Sources (PEL) | Export limiting from all sources | No | Gateway (EHX2) and System Edge Box (SE-A3 or SE-A4) with integrated Gateway (EHX2) and Shanghai CHINT Power Systems Co., Ltd. Inverters (CPS SCAyKTL-DO/US-480) where y = 36, 50, or 60 | Point Of Common Coupling (PCC) | 0.03 | 18.16 | L-N/L-L-L | 480 | 72 | 60 |  | 2026-08-21
Delta Electronics | PCS125HV | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-04-26 | ESS Export Only Mode | The ESS may export active power to the Area EPS during discharging but shall not import active power from the Area EPS for ESS charging purposes. | No | Inverter with integrated CRD Function Box (CRD-B-O) and CT (ALH-0.66 or CT of equivalent rating) | Point Of Common Coupling (PCC) | 0.244 | 0.244 | L-L-L | 480 | 151 | 125 |  | 2026-08-11
Delta Electronics | PCS125HV | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-04-26 | ESS Import Only Mode | The ESS may import active power from the Area EPS for charging purposes but shall not export active power from the ESS to the Area EPS. | No | Inverter with integrated CRD Function Box (CRD-B-O) and CT (ALH-0.66 or CT of equivalent rating) | Point Of Common Coupling (PCC) | 0.046 | 0.046 | L-L-L | 480 | 151 | 125 |  | 2026-08-11
Dyness Digital Energy Technology Co., LTD. | TXyK-HM | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-04-20 | ESS Export Only Mode | The ESS may export active power to the Area EPS during discharging but shall not import active power from the Area EPS for ESS charging purposes. | No | Microgrid Interconnection Device (ATS-US-200) with integrated CT (XH-SCT-T24) | Point of Connection (POC) | 1.991 | 9.314 | L-N/L-L | 240 | 47.5 | 11.4 | where y = 5, 6, 7.6, 9.6, or 11.4 | 2026-08-11
Dyness Digital Energy Technology Co., LTD. | TXyK-HM | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-04-20 | ESS Import Only Mode | The ESS may import active power from the Area EPS for charging purposes, but shall not export active power from the ESS to the Area EPS. | No | Microgrid Interconnection Device (ATS-US-200) with integrated CT (XH-SCT-T24) | Point of Connection (POC) | 1.991 | 8.647 | L-N/L-L | 240 | 47.5 | 11.4 | where y = 5, 6, 7.6, 9.6, or 11.4 | 2026-08-11
EcoFlow Inc. | EF-GW-001 | Gateway | Intertek/ETL | OOI Issue 2 : 2024 | 2026-03-17 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charging purposes. This is the same as "No Grid Charge". | No | Inverter (EF-PCS-24), Integrated Current Sensors (CT2404L-5k-200, Rating: 200A/40mA) | Point of Connection (POC) | 1.5 | 1.5 | L-N/L-L | 120/208/240 | 100 | 24 |  | 2026-05-11
EcoFlow Inc. | EF-GW-001 | Gateway | Intertek/ETL | OOI Issue 2 : 2024 | 2026-03-17 | ESS Import Only Mode | The PCS allows the import of active power from the Area EPS for BESS charging purposes but shall not allow the export of active power from the BESS to the Area EPS. This is the same as "No Storage Export". | No | Inverter (EF-PCS-24), Integrated Current Sensors (CT2404L-5k-200, Rating: 200A/40mA) | Point of Connection (POC) | 1.5 | 1.5 | L-N/L-L | 120/208/240 | 100 | 24 |  | 2026-05-11
EcoFlow Inc. | EF-GW-001 | Gateway | Intertek/ETL | OOI Issue 2 : 2024 | 2026-03-17 | ESS No Exchange Mode | The PCS does not allow the import of active power from the Area EPS for BESS charging purposes and does not allow the export of active power from the BESS to the Area EPS. | No | Inverter (EF-PCS-24), Integrated Current Sensors (CT2404L-5k-200, Rating: 200A/40mA) | Point Of Common Coupling (PCC) | 1.5 | 1.5 | L-N/L-L | 120/208/240 | 100 | 24 |  | 2026-05-11
EcoFlow Inc. | EF-GW-001 | Gateway | Intertek/ETL | OOI Issue 2 : 2024 | 2026-03-17 | ESS Unrestricted Mode | The PCS allows the import of active power from the Area EPS for BESS charging purposes and allows the export of active power from the BESS to the Area EPS. | No | Inverter (EF-PCS-24), Integrated Current Sensors (CT2404L-5k-200, Rating: 200A/40mA) | Point of Connection (POC) | 1.5 | 1.5 | L-N/L-L | 120/208/240 | 100 | 24 |  | 2026-05-11
EcoFlow Inc. | EF-GW-001 | Gateway | Intertek/ETL | OOI Issue 2 : 2024 | 2026-03-17 | Export Limiting from all Sources (PEL) | The PCS monitors power at the PCC and limits export to the Area EPS to a set value. | No | Inverter (EF-PCS-24), Integrated Current Sensors (CT2404L-5k-200, Rating: 200A/40mA) | Point Of Common Coupling (PCC) | 1.5 | 1.5 | L-N/L-L | 120/208/240 | 100 | 24 |  | 2026-05-11
EcoFlow Inc. | EF-GW-001 | Gateway | Intertek/ETL | OOI Issue 2 : 2024 | 2026-03-17 | Power Import Limiting at the PCC (PIL) | The PCS monitors power at the PCC and limits import from the Area EPS to a set value. | No | Inverter (EF-PCS-24), Integrated Current Sensors (CT2404L-5k-200, Rating: 200A/40mA) | Point Of Common Coupling (PCC) | 1.5 | 1.5 | L-N/L-L | 120/208/240 | 100 | 24 |  | 2026-05-11
EcoFlow Inc. | EF-OCEANP-01 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charging purposes. This is the same as "No Grid Charge". | No | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X) | Point Of Common Coupling (PCC) | 1.2 | 1.4 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-OCEANP-01 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | ESS Import Only Mode | The PCS allows the import of active power from the Area EPS for BESS charging purposes but shall not allow the export of active power from the BESS to the Area EPS. This is the same as "No Storage Export". | No | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X) | Point Of Common Coupling (PCC) | 1.2 | 1.4 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-OCEANP-01 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | ESS No Exchange Mode | The PCS does not allow the import of active power from the Area EPS for BESS charging purposes and does not allow the export of active power from the BESS to the Area EPS. | No | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X) | Point Of Common Coupling (PCC) | 1.6 | 1.7 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-OCEANP-01 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | ESS Unrestricted Mode | The PCS allows the import of active power from the Area EPS for BESS charging purposes and allows the export of active power from the BESS to the Area EPS. | No | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X) | Point Of Common Coupling (PCC) | 1.6 | 1.7 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-OCEANP-01 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | Export Limiting from all Sources (PEL) | The PCS monitors power at the PCC and limits export to the Area EPS to a set value. | Yes | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X) | Point Of Common Coupling (PCC) | 1 | 1.2 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-OCEANP-01 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | Power Import Limiting at the PCC (PIL) | The PCS monitors power at the PCC and limits import from the Area EPS to a set value. | Yes | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X) | Point Of Common Coupling (PCC) | 1.2 | 1.4 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-OCEANP-21 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charging purposes. This is the same as "No Grid Charge". | No | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X), Junction Box (EF-BL-001) | Point Of Common Coupling (PCC) | 1.2 | 1.4 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-OCEANP-21 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | ESS Import Only Mode | The PCS allows the import of active power from the Area EPS for BESS charging purposes but shall not allow the export of active power from the BESS to the Area EPS. This is the same as "No Storage Export". | No | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X), Junction Box (EF-BL-001) | Point Of Common Coupling (PCC) | 1.2 | 1.4 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-OCEANP-21 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | ESS No Exchange Mode | The PCS does not allow the import of active power from the Area EPS for BESS charging purposes and does not allow the export of active power from the BESS to the Area EPS. | No | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X), Junction Box (EF-BL-001) | Point Of Common Coupling (PCC) | 1.6 | 1.7 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-OCEANP-21 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | ESS Unrestricted Mode | The PCS allows the import of active power from the Area EPS for BESS charging purposes and allows the export of active power from the BESS to the Area EPS. | No | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X), Junction Box (EF-BL-001) | Point Of Common Coupling (PCC) | 1.6 | 1.7 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-OCEANP-21 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | Export Limiting from all Sources (PEL) | The PCS monitors power at the PCC and limits export to the Area EPS to a set value. | Yes | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X), Junction Box (EF-BL-001) | Point Of Common Coupling (PCC) | 1 | 1.2 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-OCEANP-21 | Energy Storage System | Intertek/ETL | OOI Issue 2 : 2024 | 2026-05-26 | Power Import Limiting at the PCC (PIL) | The PCS monitors power at the PCC and limits import from the Area EPS to a set value. | Yes | Inverter (EF-PCS-24), Communication Board (EF-MBS-002), Meter Socket Adapter (V-1-A-6/V-1-A-X), Junction Box (EF-BL-001) | Point Of Common Coupling (PCC) | 1.2 | 1.4 | L-N/L-L | 208/240 | 100 | 24 | ESS and Inverter can be rated at 24 kW or 11.5 kW | 2026-07-01
EcoFlow Inc. | EF-PCS-24 | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-04-14 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charging purposes. This is the same as "No Grid Charge". | No | CT (CT2404L-5k-200, Rating: 200A/40mA), Smart Electrical Panel (EF-SHP-x) | Point of Connection (POC) | 1.9 | 1.9 | L-N/L-L | 240 | 100 | 24 | where x = 8-NS, 16(OCEAN)-NS, 24(OCEAN)-NS, 32(OCEAN)-NS, 40-NS | 2026-06-01
EcoFlow Inc. | EF-PCS-24 | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-04-14 | ESS Import Only Mode | The PCS allows the import of active power from the Area EPS for BESS charging purposes but shall not allow the export of active power from the BESS to the Area EPS. This is the same as "No Storage Export". | No | CT (CT2404L-5k-200, Rating: 200A/40mA), Smart Electrical Panel (EF-SHP-x) | Point of Connection (POC) | 1.84 | 1.84 | L-N/L-L | 240 | 100 | 24 | where x = 8-NS, 16(OCEAN)-NS, 24(OCEAN)-NS, 32(OCEAN)-NS, 40-NS | 2026-06-01
EcoFlow Inc. | EF-PCS-24 | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-04-14 | ESS No Exchange Mode | The PCS does not allow the import of active power from the Area EPS for BESS charging purposes and does not allow the export of active power from the BESS to the Area EPS. | No | CT (CT2404L-5k-200, Rating: 200A/40mA), Smart Electrical Panel (EF-SHP-x) | Point Of Common Coupling (PCC) | 1.84 | 1.84 | L-N/L-L | 240 | 100 | 24 | where x = 8-NS, 16(OCEAN)-NS, 24(OCEAN)-NS, 32(OCEAN)-NS, 40-NS | 2026-06-01
EcoFlow Inc. | EF-PCS-24 | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-04-14 | ESS Unrestricted Mode | The PCS allows the import of active power from the Area EPS for BESS charging purposes and allows the export of active power from the BESS to the Area EPS. | No | CT (CT2404L-5k-200, Rating: 200A/40mA), Smart Electrical Panel (EF-SHP-x) | Point of Connection (POC) | 1.76 | 1.76 | L-N/L-L | 240 | 100 | 24 | where x = 8-NS, 16(OCEAN)-NS, 24(OCEAN)-NS, 32(OCEAN)-NS, 40-NS | 2026-06-01
EcoFlow Inc. | EF-PCS-24 | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-04-14 | Export Limiting from all Sources (PEL) | The PCS monitors power at the PCC and limits import from the Area EPS to a set value. | No | CT (CT2404L-5k-200, Rating: 200A/40mA), Smart Electrical Panel (EF-SHP-x) | Point Of Common Coupling (PCC) | 1.84 | 1.84 | L-N/L-L | 240 | 100 | 24 | where x = 8-NS, 16(OCEAN)-NS, 24(OCEAN)-NS, 32(OCEAN)-NS, 40-NS | 2026-06-01
EcoFlow Inc. | EF-PCS-24 | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-04-14 | Power Import Limiting at the PCC (PIL) | The PCS monitors power at the PCC and limits export to the Area EPS to a set value. | No | CT (CT2404L-5k-200, Rating: 200A/40mA), Smart Electrical Panel (EF-SHP-x) | Point Of Common Coupling (PCC) | 1.6 | 1.6 | L-N/L-L | 240 | 100 | 24 | where x = 8-NS, 16(OCEAN)-NS, 24(OCEAN)-NS, 32(OCEAN)-NS, 40-NS | 2026-06-01
FOMware | Flex Energy Manager | Gateway | CSA Group | OOI Issue 2 : 2024 | 2026-02-05 | Export Limiting from all Sources (PEL) | Export limiting from all sources | No | Gateway (EHX2) and System Edge Box (SE-A3 or SE-A4) with integrated Gateway (EHX2) and Shanghai CHINT Power Systems Co., Ltd. Inverters (CPS SCAyKTL-DO/US-480) where y = 36, 50, or 60. | Point Of Common Coupling (PCC) | 0.03 | 18.16 | L-N/L-L-L | 480 | 120 | 100 |  | 2026-08-11
FOMware | Flex Energy Manager | Gateway | CSA Group | OOI Issue 2 : 2024 | 2026-02-05 | Export Limiting from all Sources (PEL) | Export limiting from all sources | No | Gateway (EHX2) and System Edge Box (SE-A3 or SE-A4) with integrated Gateway (EHX2) and Shanghai CHINT Power Systems Co., Ltd. Inverter (CPS SCA25KTL-DO/US-208) | Point Of Common Coupling (PCC) | 0.03 | 18.16 | L-N/L-L-L | 208 | 120 | 100 |  | 2026-08-11
FOMware | Power Control System with Gateway {EHX2} | Gateway | CSA Group | OOI Issue 2 : 2024 | 2026-02-05 | Export Limiting from all Sources (PEL) | Export limiting from all sources | No | Gateway (EHX2) and Ginlong Technologies Co., Ltd. Inverters (S5-GCxK-US) or Shanghai CHINT Power Systems Co., Ltd. Inverters (CPS SCAyKTL-DO/US-480) where x = 75, 80, 90, or 100 where y = 36, 50, or 60. | Point Of Common Coupling (PCC) | 0.03 | 18.16 | L-N/L-L-L | 480 | 120 | 100 |  | 2026-08-11
FOMware | Power Control System with Gateway {EHX2} | Gateway | CSA Group | OOI Issue 2 : 2024 | 2026-02-05 | Export Limiting from all Sources (PEL) | Export limiting from all sources | No | Gateway (EHX2) and Shanghai CHINT Power Systems Co., Ltd. Inverter (CPS SCA25KTL-DO/US-208) | Point Of Common Coupling (PCC) | 0.03 | 18.16 | L-N/L-L-L | 208 | 120 | 100 |  | 2026-08-11
FOMware | Power Control System with System Edge Box | Gateway | CSA Group | OOI Issue 2 : 2024 | 2026-02-05 | Export Limiting from all Sources (PEL) | Export limiting from all sources | No | System Edge Box (SE-A3 or SE-A4) and Ginlong Technologies Co., Ltd. Inverters (S5-GCxK-US) or Shanghai CHINT Power Systems Co., Ltd. Inverters (CPS SCAyKTL-DO/US-480) where x = 75, 80, 90, or 100 where y = 36, 50, or 60. | Point Of Common Coupling (PCC) | 0.03 | 18.16 | L-N/L-L-L | 480 | 120 | 100 |  | 2026-08-11
FOMware | Power Control System with System Edge Box | Gateway | CSA Group | OOI Issue 2 : 2024 | 2026-02-05 | Export Limiting from all Sources (PEL) | Export limiting from all sources | No | System Edge Box (SE-A3 or SE-A4) and Shanghai CHINT Power Systems Co., Ltd. Inverters (CPS SCA25KTL-DO/US-208) | Point Of Common Coupling (PCC) | 0.03 | 18.16 | L-N/L-L-L | 208 | 120 | 100 |  | 2026-08-11
FOXESS CO., LTD. | H3-100-Plus-US-H | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charing porposes. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.945 | 4.644 | L-N/L-L-L | 480 | 120.3 | 100 |  | 2026-08-11
FOXESS CO., LTD. | H3-100-Plus-US-H | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Import Only Mode | The PCS allows the import of active power from the area EPS for BESS charging porposes but shall not allow the export of active power from the BESS to the Area EPS. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.955 | 3.833 | L-N/L-L-L | 480 | 120.3 | 100 |  | 2026-08-11
FOXESS CO., LTD. | H3-125-Plus-US-H | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charing porposes. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.945 | 4.644 | L-N/L-L-L | 480 | 150.4 | 125 |  | 2026-08-11
FOXESS CO., LTD. | H3-125-Plus-US-H | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Import Only Mode | The PCS allows the import of active power from the area EPS for BESS charging porposes but shall not allow the export of active power from the BESS to the Area EPS. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.955 | 3.833 | L-N/L-L-L | 480 | 150.4 | 125 |  | 2026-08-11
FOXESS CO., LTD. | H3-150-Plus-US-H | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charing porposes. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.945 | 4.644 | L-N/L-L-L | 480 | 180.4 | 150 |  | 2026-08-11
FOXESS CO., LTD. | H3-150-Plus-US-H | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Import Only Mode | The PCS allows the import of active power from the area EPS for BESS charging porposes but shall not allow the export of active power from the BESS to the Area EPS. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.955 | 3.833 | L-N/L-L-L | 480 | 180.4 | 150 |  | 2026-08-11
FOXESS CO., LTD. | H3-37.5-Plus-US-L | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charing porposes. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.945 | 4.644 | L-N/L-L-L | 208 | 104.1 | 37.5 |  | 2026-08-11
FOXESS CO., LTD. | H3-37.5-Plus-US-L | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Import Only Mode | The PCS allows the import of active power from the area EPS for BESS charging porposes but shall not allow the export of active power from the BESS to the Area EPS. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.955 | 3.833 | L-N/L-L-L | 208 | 104.1 | 37.5 |  | 2026-08-11
FOXESS CO., LTD. | H3-50-Plus-US-L | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charing porposes. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.945 | 4.644 | L-N/L-L-L | 208 | 138.8 | 50 |  | 2026-08-11
FOXESS CO., LTD. | H3-50-Plus-US-L | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Import Only Mode | The PCS allows the import of active power from the area EPS for BESS charging porposes but shall not allow the export of active power from the BESS to the Area EPS. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.955 | 3.833 | L-N/L-L-L | 208 | 138.8 | 50 |  | 2026-08-11
FOXESS CO., LTD. | H3-60-Plus-US-L | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charing porposes. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.945 | 4.644 | L-N/L-L-L | 208 | 166.6 | 60 |  | 2026-08-11
FOXESS CO., LTD. | H3-60-Plus-US-L | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Import Only Mode | The PCS allows the import of active power from the area EPS for BESS charging porposes but shall not allow the export of active power from the BESS to the Area EPS. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.955 | 3.833 | L-N/L-L-L | 208 | 166.6 | 60 |  | 2026-08-11
FOXESS CO., LTD. | H3-70-Plus-US-L | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charing porposes. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.945 | 4.644 | L-N/L-L-L | 208 | 194.3 | 70 |  | 2026-08-11
FOXESS CO., LTD. | H3-70-Plus-US-L | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Import Only Mode | The PCS allows the import of active power from the area EPS for BESS charging porposes but shall not allow the export of active power from the BESS to the Area EPS. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.955 | 3.833 | L-N/L-L-L | 208 | 194.3 | 70 |  | 2026-08-11
FOXESS CO., LTD. | H3-80-Plus-US-H | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Export Only Mode | The PCS allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charing porposes. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.945 | 4.644 | L-N/L-L-L | 480 | 96.2 | 80 |  | 2026-08-11
FOXESS CO., LTD. | H3-80-Plus-US-H | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-06-16 | ESS Import Only Mode | The PCS allows the import of active power from the area EPS for BESS charging porposes but shall not allow the export of active power from the BESS to the Area EPS. | No | Meter Model (DTSU666) | Point Of Common Coupling (PCC) | 1.955 | 3.833 | L-N/L-L-L | 480 | 96.2 | 80 |  | 2026-08-11
GoodWe Technologies Co., Ltd. | GW22KLV-SMT-US | Inverter | CSA Group | OOI Issue 2 : 2024 | 2025-05-16 | Export Limiting from all Sources (PEL) | PCS functions designed to provide control of power or energy exchange with the area EPS at an external Reference Point of Applicability (RPA) such as the PCC | No | Meter (GM330) | Point Of Common Coupling (PCC) | 1.28 | 2.74 | L-L-L | 208/240 | 61 | 25 |  | 2026-06-11
GoodWe Technologies Co., Ltd. | GW28KLV-SMT-US | Inverter | CSA Group | OOI Issue 2 : 2024 | 2025-05-16 | Export Limiting from all Sources (PEL) | PCS functions designed to provide control of power or energy exchange with the area EPS at an external Reference Point of Applicability (RPA) such as the PCC | No | Meter (GM330) | Point Of Common Coupling (PCC) | 1.28 | 2.74 | L-L-L | 208/240 | 77.7 | 32 |  | 2026-06-11
GoodWe Technologies Co., Ltd. | GW50K-SMT-US | Inverter | CSA Group | OOI Issue 2 : 2024 | 2025-05-16 | Export Limiting from all Sources (PEL) | PCS functions designed to provide control of power or energy exchange with the area EPS at an external Reference Point of Applicability (RPA) such as the PCC | No | Meter (GM330) | Point Of Common Coupling (PCC) | 1.28 | 2.74 | L-L-L | 480 | 60.1 | 50 |  | 2026-06-11
GoodWe Technologies Co., Ltd. | GW60K-SMT-US | Inverter | CSA Group | OOI Issue 2 : 2024 | 2025-05-16 | Export Limiting from all Sources (PEL) | PCS functions designed to provide control of power or energy exchange with the area EPS at an external Reference Point of Applicability (RPA) such as the PCC | No | Meter (GM330) | Point Of Common Coupling (PCC) | 1.28 | 2.74 | L-L-L | 480 | 72.2 | 60 |  | 2026-06-11
Hangzhou Boco Electronics Co., Ltd. | P115SJ240-2001FT-00 | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-08-20 | ESS Import Only Mode | The ESS may import active power from the Area EPS for charging purposes but shall not export active power from the ESS to the Area EPS. | No | Controller (BPM-0005-00) and CT (ECS2520-L40) | Point Of Common Coupling (PCC) | 1.6 | 1.7 | L-L | 240 | 9.2 | 2.2 |  | 2026-10-12
Shenzhen Growatt New Energy Co., Ltd. | MIN 10000TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Control the output power of the PCS AC port according to the set requirements. | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 1.6 | 1.85 | L-L | 240 | 42 | 10 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 10000TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Power Import Limiting at the PCC (PIL) | Control the input power of the PCS AC port according to the set requirements | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 0.8 | 1 | L-L | 240 | 42 | 10 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 11400TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Control the output power of the PCS AC port according to the set requirements. | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 1.6 | 1.85 | L-L | 240 | 48 | 11.4 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 11400TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Power Import Limiting at the PCC (PIL) | Control the input power of the PCS AC port according to the set requirements | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 0.8 | 1 | L-L | 240 | 48 | 11.4 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 3000TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Control the output power of the PCS AC port according to the set requirements. | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 1.6 | 1.85 | L-L | 240 | 12.5 | 3 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 3000TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Power Import Limiting at the PCC (PIL) | Control the input power of the PCS AC port according to the set requirements | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 0.8 | 1 | L-L | 240 | 12.5 | 3 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 3800TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Control the output power of the PCS AC port according to the set requirements. | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 1.6 | 1.85 | L-L | 240 | 16 | 3.8 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 3800TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Power Import Limiting at the PCC (PIL) | Control the input power of the PCS AC port according to the set requirements | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 0.8 | 1 | L-L | 240 | 16 | 3.8 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 5000TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Control the output power of the PCS AC port according to the set requirements. | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 1.6 | 1.85 | L-L | 240 | 21 | 5 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 5000TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Power Import Limiting at the PCC (PIL) | Control the input power of the PCS AC port according to the set requirements | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 0.8 | 1 | L-L | 240 | 21 | 5 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 5700TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Control the output power of the PCS AC port according to the set requirements. | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 1.6 | 1.85 | L-L | 240 | 24 | 5.7 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 5700TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Power Import Limiting at the PCC (PIL) | Control the input power of the PCS AC port according to the set requirements | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 0.8 | 1 | L-L | 240 | 24 | 5.7 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 6000TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Control the output power of the PCS AC port according to the set requirements. | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 1.6 | 1.85 | L-L | 240 | 25 | 6 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 6000TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Power Import Limiting at the PCC (PIL) | Control the input power of the PCS AC port according to the set requirements | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 0.8 | 1 | L-L | 240 | 25 | 6 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 7600TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Control the output power of the PCS AC port according to the set requirements. | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 1.6 | 1.85 | L-L | 240 | 32 | 7.6 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 7600TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Power Import Limiting at the PCC (PIL) | Control the input power of the PCS AC port according to the set requirements | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 0.8 | 1 | L-L | 240 | 32 | 7.6 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 8200TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Control the output power of the PCS AC port according to the set requirements. | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 1.6 | 1.85 | L-L | 240 | 35 | 8.2 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 8200TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Power Import Limiting at the PCC (PIL) | Control the input power of the PCS AC port according to the set requirements | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 0.8 | 1 | L-L | 240 | 35 | 8.2 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 9000TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Control the output power of the PCS AC port according to the set requirements. | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 1.6 | 1.85 | L-L | 240 | 38 | 9 |  | 2026-09-11
Shenzhen Growatt New Energy Co., Ltd. | MIN 9000TL-XH2 US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Power Import Limiting at the PCC (PIL) | Control the input power of the PCS AC port according to the set requirements | No | AKH-0.66 K-φ24 ,200A/40mA, and Smarter AC Interface (SYN 200-XH-US-yA or SYN 200U-z US) where y = 11 or 13 and z = 20, 21, 22, or 23 | Point Of Common Coupling (PCC) | 0.8 | 1 | L-L | 240 | 38 | 9 |  | 2026-09-11
Sigenergy Technology Co., Ltd. | SigenStor EC x SP US | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-04-16 | ESS Export Only Mode | The PCS controller in the BESS system allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charging purposes. This is the same as "No Grid Charge". | No | Energy Storage System (SigenStor-A-B), Sigen Backup Switch | Point Of Common Coupling (PCC) | 0.131 | 0.73 | L-N/L-L | 240 | 48 | 11.5 | The letter x in the PCS model number and the inverter model number represents the nominal AC output power (kW) of the inverter, where x = blank, 11.4, 9.6, 7.6, 5.7, 4.8, and 3.8 The letter A in the ESS model number represents the power capacity (kW), where A = 11.5, 11.4, 9.6, 7.6, 5.7, 4.8, and 3.8. The letter B in the ESS model number represents the energy capacity (kWh), where B = 6.02, 9.04, 12.04, 15.06, 18.08, 21.08, 24.10, 27.12, 30.12, 33.14, 36.16, 39.16, 42.18, 45.20, 48.20, 51.22, and 54.24. | 2026-05-21
Sigenergy Technology Co., Ltd. | SigenStor EC x SP US | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-08-18 | ESS Export Only Mode | The PCS controller in the BESS system allows the export of active power from the BESS to the Area EPS but shall not allow the import of active power from the Area EPS for BESS charging purposes. This is the same as "No Grid Charge". | No | Energy Storage System (SigenStor-A-B) with Sigen LoadHub | Point Of Common Coupling (PCC) | 0.411 | 0.735 | L-N/L-L | 208/240 | 48 | 11.5 | The letter x in the PCS model number and the inverter model number represents the nominal AC output power (kW) of the inverter, where x = blank, 11.4, 9.6, 7.6, 5.7, 4.8, and 3.8 The letter A in the ESS model number represents the power capacity (kW), where A = 11.5, 11.4, 9.6, 7.6, 5.7, 4.8, and 3.8. The letter B in the ESS model number represents the energy capacity (kWh), where B = 6.02, 9.04, 12.04, 15.06, 18.08, 21.08, 24.10, 27.12, 30.12, 33.14, 36.16, 39.16, 42.18, 45.20, 48.20, 51.22, and 54.24. | 2026-10-12
Sigenergy Technology Co., Ltd. | SigenStor EC x SP US | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-04-16 | ESS Import Only Mode | The PCS controller in the BESS system allows the import of active power from the Area EPS for BESS charging purposes but shall not allow the export of active power from the BESS to the Area EPS. This is the same as "No Storage Export". | No | Energy Storage System (SigenStor-A-B), Sigen Backup Switch | Point Of Common Coupling (PCC) | 0.337 | 0.496 | L-N/L-L | 240 | 48 | 11.5 | The letter x in the PCS model number and the inverter model number represents the nominal AC output power (kW) of the inverter, where x = blank, 11.4, 9.6, 7.6, 5.7, 4.8, and 3.8 The letter A in the ESS model number represents the power capacity (kW), where A = 11.5, 11.4, 9.6, 7.6, 5.7, 4.8, and 3.8. The letter B in the ESS model number represents the energy capacity (kWh), where B = 6.02, 9.04, 12.04, 15.06, 18.08, 21.08, 24.10, 27.12, 30.12, 33.14, 36.16, 39.16, 42.18, 45.20, 48.20, 51.22, and 54.24. | 2026-05-21
Sigenergy Technology Co., Ltd. | SigenStor EC x SP US | Inverter | CSA Group | OOI Issue 2 : 2024 | 2026-08-18 | ESS Import Only Mode | The PCS controller in the BESS system allows the import of active power from the Area EPS for BESS charging purposes but shall not allow the export of active power from the BESS to the Area EPS. This is the same as "No Storage Export". | No | Energy Storage System (SigenStor-A-B) with Sigen LoadHub | Point Of Common Coupling (PCC) | 0.337 | 0.574 | L-N/L-L | 208/240 | 48 | 11.5 | The letter x in the PCS model number and the inverter model number represents the nominal AC output power (kW) of the inverter, where x = blank, 11.4, 9.6, 7.6, 5.7, 4.8, and 3.8 The letter A in the ESS model number represents the power capacity (kW), where A = 11.5, 11.4, 9.6, 7.6, 5.7, 4.8, and 3.8. The letter B in the ESS model number represents the energy capacity (kWh), where B = 6.02, 9.04, 12.04, 15.06, 18.08, 21.08, 24.10, 27.12, 30.12, 33.14, 36.16, 39.16, 42.18, 45.20, 48.20, 51.22, and 54.24. | 2026-10-12
SolarEdge Technologies Ltd. | NXx00T-US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | ESS Export Only Mode | ESS charge through PV only; 0% import from grid to charge ESS | No | Inverter (NXx00T-US), Battery (NX-BLCK-5K, NX-BLCK-5K-SR, or NX-BLCK-5K-NB), DC Link (NX-LNK), Power Meter (SE-RGMTR-1D-240C-C), CT (SECT-S1) | Multiple | 0.3 | 9.1 | L-N/L-L | 240 | 54 | 13 | where x = 38, 50, 57, 60, 76, 96, 100, 115, 130 | 2026-08-05
SolarEdge Technologies Ltd. | NXx00T-US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | ESS Export Only Mode | ESS charge through PV only; 0% import from grid to charge ESS | No | Inverter (NXx00T-US), Battery (NX-BLCK-5K, NX-BLCK-5K-SR, or NX-BLCK-5K-NB), DC Link (NX-LNK), Meter Collar (V1-D-SE) | Multiple | 0.05 | 6.45 | L-N/L-L | 208/240 | 54 | 13 | where x = 38, 50, 57, 60, 76, 96, 100, 115, 130 | 2026-08-05
SolarEdge Technologies Ltd. | NXx00T-US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | ESS Import Only Mode | ESS discharge 0% to grid; only PV discharge to grid | No | Inverter (NXx00T-US), Battery (NX-BLCK-5K, NX-BLCK-5K-SR, or NX-BLCK-5K-NB), DC Link (NX-LNK), Power Meter (SE-RGMTR-1D-240C-C), CT (SECT-S1) | Point Of Common Coupling (PCC) | 1 | 9.1 | L-N/L-L | 240 | 54 | 13 | where x = 38, 50, 57, 60, 76, 96, 100, 115, 130 | 2026-08-05
SolarEdge Technologies Ltd. | NXx00T-US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | ESS Import Only Mode | ESS discharge 0% to grid; only PV discharge to grid | No | Inverter (NXx00T-US), Battery (NX-BLCK-5K, NX-BLCK-5K-SR, or NX-BLCK-5K-NB), DC Link (NX-LNK), Meter Collar (V1-D-SE) | Point Of Common Coupling (PCC) | 0.05 | 6.45 | L-N/L-L | 208/240 | 54 | 13 | where x = 38, 50, 57, 60, 76, 96, 100, 115, 130 | 2026-08-05
SolarEdge Technologies Ltd. | NXx00T-US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Limits inverter export to grid using internal control logic (PEL functionality is for PV only). | No | Inverter (NXx00T-US), Power Meter (SE-RGMTR-1D-240C-C), CT (SECT-S1) | Point Of Common Coupling (PCC) | 1 | 1 | L-N/L-L | 240 | 54 | 13 | where x = 38, 50, 57, 60, 76, 96, 100, 115, 130 | 2026-08-05
SolarEdge Technologies Ltd. | NXx00T-US | Inverter | Intertek/ETL | OOI Issue 2 : 2024 | 2026-07-17 | Export Limiting from all Sources (PEL) | Limits inverter export to grid using internal control logic (PEL functionality is for PV only). | No | Inverter (NXx00T-US), Meter Collar (V1-D-SE) | Point Of Common Coupling (PCC) | 0.1 | 4.05 | L-N/L-L | 208/240 | 54 | 13 | where x = 38, 50, 57, 60, 76, 96, 100, 115, 130 | 2026-08-05

## Data_Key
CEC Power Control System Equipment List Data Key
Updated | 2026-10-01
Column | Field Name | Explanation of Field | Field Format* | Require / Optional
A | Manufacturer | Equipment manufacturer name confirmed by a combination of documents (e.g., request form, certificate of compliance, manufacturer naming letter explaining relationship of multiple corporate entities under a single parent corporate entity). | Free form text entry | Required
B | Model Number | Equipment model number confirmed by the certificate of compliance. | Free form text entry | Required
C | End-product in which PCS is Integrated | End-product or component in which the PCS is implemented. Typically where the software/firmware resides and where processing occurs. Confirmed by a combination of documents (e.g., request form, certificate of compliance, test report). | Free form text entry | Required
D | UL 3141 Certificate of Compliance: NRTL Issuing Certificate of Compliance | Name of the Nationally Recognized Testing Laboratory (NRTL) that issued the certificate of compliance. | Text from drop down list | Required
E | UL 3141 Certificate of Compliance: Edition of UL 3141 | Issue date of the certificate of compliance. | Text from drop down list | Required
F | UL 3141 Certificate of Compliance: Certificate Date | Edition number of UL 3141 and year that edition was published. | mm/dd/yyyy | Required
G | PCS Functionality | Name of PCS functionality. Confirmed by the certificate of compliance or UL 3141 test report. See instructions tab for definitions at https://www.energy.ca.gov/media/12563. | Text from drop down list | Required
H | Description of PCS Functionality | Description of the PCS functionality evaluated by the NRTL. Confirmed by a combination of the request form, certificate of compliance, and UL 3141 test report. | Free form text entry | Required
I | Scheduling Conformance per UL 3141 Annex A: yes/no | Indicates if schedules for Power Import Limiting (PIL) and Power Export Limiting (PEL) per UL 3141 Annex A were evaluated by the NRTL. Confirmed by certificate of compliance or UL 3141 test report. | Y/N | Required
J | Additional devices required for PCS functionality | Additional components, identified by model number, that are required to achieve PCS functionality. Confirmed by certificate of compliance or UL 3141 test report. | Free form text entry | Required
K | Current Measurement Reference Points | Location of current measurement for the PCS functionality evaluated by the NRTL. Confirmed by a combination of the request form, certificate of compliance, and UL 3141 test report. | Text from drop down list | Required
L | Maximum Response Time: seconds | Measured longest response time for the PCS functionality evaluated by the NRTL. Confirmed by certificate of compliance or UL 3141 test report. | Numerical decimal | Required
M | Time to Reach Steady State: seconds | Measured longest time to steady state for the PCS functionality evaluated by the NRTL. Confirmed by certificate of compliance or UL 3141 test report. | Numerical decimal | Required
N | Single Phase (L-N or L-L) or Three Phase (L-L-L) | Identifies the power phases for which the PCS is rated. Confirmed by a combination of the request form, certificate of compliance, and UL 3141 test report. | Text from drop down list | Required
O | Rated Operating Voltage(s): volts | Identifies the operating voltage(s) for which the PCS is rated. Confirmed by a combination of the request form, certificate of compliance, and UL 3141 test report. | Numerical positive whole number. Multiple values may be separated by /. | Required
P | Maximum Continuous Operating Current Rating (Controlled): Amps | The highest value of continuous controlled current for which the PCS is rated. Confirmed by a combination of the request form, certificate of compliance, and UL 3141 test report. | Numerical decimal | Required
Q | Maximum Continuous Operating Power Rating (Controlled): kW | The highest value of continuous controlled power for which the PCS is rated. Confirmed by a combination of the request form, certificate of compliance, and UL 3141 test report. | Numerical decimal | Required
R | Notes | Additional information confirmed by CEC staff. Wildcards in model number are defined here. | Free form text entry | Optional
S | Date Added to CEC List | Date the product was initially included in the equipment list. | mm/dd/yyyy | Required
T | Last Update to CEC List | Date of the most recent revision to the product's information. | mm/dd/yyyy | Required when applicable
* Numerous fields allow blanks, Not Applicable, and No Information Submitted in addition to the described field format.